## Metadata
Data Dictionary
Column Heading | Description
Associated GSP Group | Name of the upstream Grid Supply Point (GSP) group which supplies the substation. Note that multiple GSPs can run in parallel so are therefore reported as groups.
Bulk Supply Point | Name of the upstream Bulk Supply Point (BSP) which supplies the substation.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Latitude | Latitude and longitude of the location of the substation.
Longitude
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) or WPD Best View scenario the headroom figures refer to
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below)
Limiting constraint | For generation headroom worksheet only. Identifier for the limiting factor (either thermal or fault level) that triggers the constraint when the generation headroom falls below zero.
0 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the calendar year
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2040
2045
2050

## Demand headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | 0 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Consumer Transformation | Thermal headroom (MW) | 49.18 | 48.4691 | 46.7292 | 44.7986 | 42.3155 | 37.9623 | 31.8197 | 26.1268 | 20.2985 | 12.8936 | 0.10802 | -13.0492 | -26.3324 | -39.2544 | -51.8916 | -102.6075 | -136.2256 | -154.928
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Leading the Way | Thermal headroom (MW) | 49.18 | 46.7533 | 43.3806 | 39.8883 | 35.2817 | 29.2757 | 21.0744 | 12.2463 | 2.3997 | -8.7305 | -20.5462 | -32.9577 | -45.6976 | -57.997 | -69.4051 | -99.2557 | -109.2103 | -109.7733
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Steady Progression | Thermal headroom (MW) | 49.18 | 50.1913 | 50.4397 | 50.6746 | 50.8152 | 49.9427 | 48.1155 | 46.1588 | 44.1205 | 41.0179 | 37.1653 | 33.8941 | 30.3372 | 26.4784 | 22.3501 | -5.1346 | -28.7751 | -38.1844
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | System Transformation | Thermal headroom (MW) | 49.18 | 49.6146 | 49.2259 | 48.7729 | 47.9213 | 46.7921 | 44.1775 | 41.5323 | 38.5895 | 34.9412 | 30.0972 | 24.9508 | 19.5441 | 13.9363 | 8.4778 | -20.3581 | -31.9909 | -32.6875
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | WPD Best View | Thermal headroom (MW) | 49.18 | 48.46 | 46.7106 | 44.7706 | 42.2772 | 37.9154 | 31.7589 | 26.0525 | 20.2131 | 12.7934 | -0.09481 | -13.259 | -26.5462 | -39.4733 | -52.1169 | -102.6824 | -136.1642 | -154.7999
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Consumer Transformation | Thermal headroom (MW) | 0.68 | 0.65 | 0.52 | 0.39 | 0.22 | -0.05 | -0.35 | -0.65 | -0.85 | -1.17 | -1.63 | -2.08 | -2.56 | -3 | -3.43 | -4.9 | -5.62 | -5.9
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Leading the Way | Thermal headroom (MW) | 0.68 | 0.57 | 0.4 | 0.22 | -0.02 | -0.3 | -0.65 | -1.05 | -1.36 | -1.73 | -2.19 | -2.65 | -3.09 | -3.54 | -3.93 | -4.77 | -4.89 | -4.65
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Steady Progression | Thermal headroom (MW) | 0.68 | 0.74 | 0.75 | 0.77 | 0.78 | 0.75 | 0.68 | 0.6 | 0.55 | 0.5 | 0.39 | 0.3 | 0.16 | 0.03 | -0.11 | -1.17 | -1.95 | -2.16
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | System Transformation | Thermal headroom (MW) | 0.68 | 0.72 | 0.7 | 0.69 | 0.65 | 0.57 | 0.48 | 0.38 | 0.27 | 0.17 | 0.01 | -0.2 | -0.42 | -0.68 | -0.91 | -2.01 | -2.25 | -2.09
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | WPD Best View | Thermal headroom (MW) | 0.68 | 0.65 | 0.52 | 0.39 | 0.22 | -0.05 | -0.35 | -0.65 | -0.85 | -1.17 | -1.63 | -2.08 | -2.56 | -3 | -3.43 | -4.9 | -5.62 | -5.9
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Consumer Transformation | Thermal headroom (MW) | 10.4 | 10.41 | 10.34 | 10.21 | 10.06 | 9.87 | 8.55 | 7.6 | 6.59 | 5.34 | 4.4 | 3.44 | 2.48 | 1.55 | 0.73 | -2.27 | -2.29 | -1.82
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Leading the Way | Thermal headroom (MW) | 10.4 | 10.35 | 10.21 | 10.02 | 9.81 | 9.54 | 7.78 | 6.4 | 4.96 | 3.26 | 2.31 | 1.35 | 0.37 | -0.5 | -1.26 | -2.48 | -1.46 | -0.11
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Steady Progression | Thermal headroom (MW) | 10.4 | 10.53 | 10.57 | 10.58 | 10.62 | 10.62 | 10.05 | 9.64 | 9.14 | 8.55 | 8.12 | 7.62 | 7.08 | 6.57 | 6.05 | 3.33 | 2.67 | 3.21
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | System Transformation | Thermal headroom (MW) | 10.4 | 10.51 | 10.52 | 10.5 | 10.49 | 10.51 | 9.48 | 8.82 | 8.07 | 7.12 | 6.55 | 5.95 | 5.31 | 4.66 | 3.99 | 1.21 | 1.59 | 2.57
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | WPD Best View | Thermal headroom (MW) | 10.4 | 10.41 | 10.34 | 10.21 | 10.06 | 9.87 | 8.55 | 7.6 | 6.59 | 5.34 | 4.4 | 3.44 | 2.48 | 1.55 | 0.73 | -2.27 | -2.29 | -1.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Consumer Transformation | Thermal headroom (MW) | 8.47 | 8.27 | 7.94 | 7.56 | 7.15 | 5.97 | 4.89 | 3.84 | 2.77 | 1.26 | -2.51 | -6.35 | -10.22 | -14.08 | -17.95 | -32.39 | -45.57 | -53.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Leading the Way | Thermal headroom (MW) | 8.47 | 7.82 | 7 | 6.14 | 5.02 | 3.34 | 1.77 | -0.16 | -2.88 | -5.85 | -8.79 | -12.05 | -15.49 | -18.9 | -22.16 | -30.69 | -34.8 | -36.36
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Steady Progression | Thermal headroom (MW) | 8.47 | 8.61 | 8.64 | 8.66 | 8.69 | 8.38 | 8.06 | 7.71 | 7.31 | 6.42 | 5.21 | 4.52 | 3.78 | 2.88 | 1.76 | -4.2 | -10.42 | -13.41
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | System Transformation | Thermal headroom (MW) | 8.47 | 8.48 | 8.37 | 8.24 | 8.1 | 7.82 | 7.54 | 7.12 | 6.63 | 6.07 | 4.82 | 3.5 | 2.17 | 0.88 | -0.36 | -6.76 | -10.29 | -11.49
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | WPD Best View | Thermal headroom (MW) | 8.47 | 8.27 | 7.94 | 7.56 | 7.15 | 5.97 | 4.89 | 3.84 | 2.77 | 1.26 | -2.51 | -6.35 | -10.22 | -14.08 | -17.95 | -32.39 | -45.57 | -53.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Consumer Transformation | Thermal headroom (MW) | 4.21 | 4.17 | 4.08 | 3.97 | 3.79 | 3.58 | 3.32 | 3.01 | 2.69 | 2.27 | 1.59 | 0.88 | 0.16 | -0.54 | -1.23 | -4.29 | -6.03 | -6.87
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Leading the Way | Thermal headroom (MW) | 4.21 | 4.07 | 3.87 | 3.66 | 3.32 | 2.97 | 2.61 | 2.15 | 1.69 | 1.16 | 0.5 | -0.23 | -0.99 | -1.69 | -2.32 | -4.12 | -4.67 | -4.5
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Steady Progression | Thermal headroom (MW) | 4.21 | 4.31 | 4.36 | 4.41 | 4.44 | 4.37 | 4.32 | 4.19 | 4.08 | 3.98 | 3.86 | 3.66 | 3.45 | 3.2 | 2.96 | 1.03 | -0.62 | -1.33
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | System Transformation | Thermal headroom (MW) | 4.21 | 4.27 | 4.28 | 4.29 | 4.2 | 4.08 | 3.98 | 3.85 | 3.74 | 3.55 | 3.3 | 3.02 | 2.71 | 2.33 | 1.94 | -0.08 | -0.89 | -0.89
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | WPD Best View | Thermal headroom (MW) | 4.21 | 4.17 | 4.08 | 3.97 | 3.79 | 3.58 | 3.32 | 3.01 | 2.69 | 2.27 | 1.59 | 0.88 | 0.16 | -0.54 | -1.23 | -4.29 | -6.03 | -6.87
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Consumer Transformation | Thermal headroom (MW) | 14.31 | 14.33 | 14.28 | 14.24 | 14.17 | 14.02 | 13.77 | 13.6 | 13.4 | 13.15 | 12.75 | 12.31 | 11.88 | 11.49 | 11.11 | 9.4 | 8.45 | 8.11
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Leading the Way | Thermal headroom (MW) | 14.31 | 14.23 | 14.11 | 14 | 13.83 | 13.61 | 13.3 | 13.01 | 12.72 | 12.42 | 12.02 | 11.62 | 11.19 | 10.77 | 10.39 | 9.31 | 9.03 | 9.25
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Steady Progression | Thermal headroom (MW) | 14.31 | 14.41 | 14.46 | 14.51 | 14.55 | 14.57 | 14.56 | 14.51 | 14.47 | 14.38 | 14.25 | 14.14 | 14.03 | 13.92 | 13.74 | 12.29 | 11.12 | 10.88
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | System Transformation | Thermal headroom (MW) | 14.31 | 14.39 | 14.4 | 14.44 | 14.44 | 14.46 | 14.39 | 14.3 | 14.22 | 14.12 | 13.97 | 13.83 | 13.66 | 13.46 | 13.21 | 11.73 | 11.03 | 11.12
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | WPD Best View | Thermal headroom (MW) | 14.31 | 14.33 | 14.28 | 14.24 | 14.17 | 14.02 | 13.77 | 13.6 | 13.4 | 13.15 | 12.75 | 12.31 | 11.88 | 11.49 | 11.11 | 9.4 | 8.45 | 8.11
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Consumer Transformation | Thermal headroom (MW) | 5.93 | 5.55 | 5.15 | 4.6 | 3.91 | 2.91 | 1.78 | 0.55 | -0.54 | -1.73 | -5.07 | -8.83 | -12.66 | -16.4 | -20.15 | -34.22 | -47.1 | -55.33
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Leading the Way | Thermal headroom (MW) | 5.93 | 5.21 | 4.44 | 3.61 | 2.56 | 1.05 | -0.49 | -2.37 | -4.6 | -7.18 | -10.26 | -13.65 | -17.22 | -20.63 | -23.94 | -33.41 | -38.44 | -41.37
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Steady Progression | Thermal headroom (MW) | 5.93 | 5.92 | 5.89 | 5.81 | 5.71 | 5.42 | 5.09 | 4.7 | 4.37 | 3.55 | 2.43 | 1.72 | 0.95 | 0.03 | -0.77 | -6.27 | -12.33 | -15.4
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | System Transformation | Thermal headroom (MW) | 5.93 | 5.77 | 5.6 | 5.36 | 5.05 | 4.73 | 4.35 | 3.8 | 3.21 | 2.51 | 1.16 | -0.29 | -1.75 | -3.17 | -4.46 | -11.02 | -14.84 | -16.02
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | WPD Best View | Thermal headroom (MW) | 5.93 | 5.54 | 5.12 | 4.56 | 3.85 | 2.84 | 1.69 | 0.44 | -0.67 | -1.88 | -5.37 | -9.14 | -12.97 | -16.72 | -20.48 | -34.33 | -47.01 | -55.14
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Consumer Transformation | Thermal headroom (MW) | 8.41 | 8.22 | 7.73 | 7.24 | 6.69 | 5.66 | 4.49 | 3.39 | 1.94 | 0.21 | -2.6 | -5.27 | -7.95 | -10.54 | -13.07 | -24.79 | -30.71 | -33.99
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Leading the Way | Thermal headroom (MW) | 8.41 | 7.82 | 6.89 | 6.02 | 4.98 | 3.61 | 2.09 | 0.33 | -1.66 | -3.9 | -6.69 | -9.42 | -12.09 | -14.7 | -17.08 | -23.69 | -25.82 | -26.04
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Steady Progression | Thermal headroom (MW) | 8.41 | 8.58 | 8.54 | 8.53 | 8.52 | 8.25 | 7.89 | 7.52 | 7.06 | 6.49 | 5.72 | 4.99 | 4.21 | 3.41 | 2.63 | -3.18 | -8.84 | -11.78
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | System Transformation | Thermal headroom (MW) | 8.41 | 8.43 | 8.2 | 7.99 | 7.75 | 7.48 | 7.13 | 6.68 | 6.06 | 5.32 | 4.36 | 3.4 | 2.45 | 1.54 | 0.72 | -4.87 | -7.55 | -8.14
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | WPD Best View | Thermal headroom (MW) | 8.41 | 8.22 | 7.73 | 7.24 | 6.69 | 5.66 | 4.49 | 3.39 | 1.94 | 0.21 | -2.6 | -5.27 | -7.95 | -10.54 | -13.07 | -24.79 | -30.71 | -33.99
Berkswell 132kV | Coventry South | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Consumer Transformation | Thermal headroom (MW) | 7.34 | 7.16 | 6.76 | 6.27 | 5.66 | 4.4 | 2.92 | 1.79 | 0.62 | -0.63 | -2.24 | -4.46 | -6.82 | -9.16 | -11.43 | -24.01 | -32.58 | -37.91
Berkswell 132kV | Coventry South | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Leading the Way | Thermal headroom (MW) | 7.34 | 6.9 | 6.18 | 5.39 | 4.49 | 2.34 | -0.04 | -1.8 | -3.53 | -5.72 | -8.21 | -10.81 | -13.47 | -16.06 | -18.46 | -27.52 | -32.41 | -36.03
Berkswell 132kV | Coventry South | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Steady Progression | Thermal headroom (MW) | 7.34 | 7.49 | 7.44 | 7.35 | 7.31 | 6.78 | 6.13 | 5.56 | 4.92 | 4.2 | 3.31 | 2.39 | 1.41 | 0.4 | -0.62 | -6.3 | -10.22 | -12.39
Berkswell 132kV | Coventry South | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | System Transformation | Thermal headroom (MW) | 7.34 | 7.4 | 7.23 | 7 | 6.8 | 6.23 | 5.32 | 4.65 | 3.83 | 2.97 | 1.94 | 0.86 | -0.27 | -1.35 | -2.43 | -8.48 | -12.22 | -13.89
Berkswell 132kV | Coventry South | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | WPD Best View | Thermal headroom (MW) | 7.34 | 7.16 | 6.76 | 6.27 | 5.66 | 4.4 | 2.92 | 1.79 | 0.62 | -0.63 | -2.24 | -4.46 | -6.82 | -9.16 | -11.43 | -24.01 | -32.58 | -37.91
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Consumer Transformation | Thermal headroom (MW) | 10.93 | 10.9 | 10.73 | 10.47 | 10.01 | 9.22 | 8.4 | 7.54 | 6.66 | 5.7 | 4.27 | 2.95 | 1.28 | -0.51 | -2.21 | -10.01 | -14.78 | -17.25
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Leading the Way | Thermal headroom (MW) | 10.93 | 10.68 | 10.26 | 9.78 | 9.07 | 8.13 | 7.14 | 6.05 | 4.94 | 3.64 | 1.82 | -0.1 | -2.06 | -3.92 | -5.61 | -11.07 | -13.02 | -13.68
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Steady Progression | Thermal headroom (MW) | 10.93 | 11.13 | 11.2 | 11.23 | 11.22 | 11.04 | 10.75 | 10.39 | 9.97 | 9.47 | 8.85 | 8.19 | 7.48 | 6.73 | 5.99 | 1.32 | -1.34 | -3.43
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | System Transformation | Thermal headroom (MW) | 10.93 | 11.06 | 11.05 | 10.98 | 10.86 | 10.61 | 10.25 | 9.8 | 9.24 | 8.59 | 7.77 | 6.9 | 6 | 5.04 | 4.1 | 0.33 | -2.1 | -2.11
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | WPD Best View | Thermal headroom (MW) | 10.93 | 10.9 | 10.73 | 10.47 | 10.01 | 9.22 | 8.4 | 7.54 | 6.66 | 5.7 | 4.27 | 2.95 | 1.28 | -0.51 | -2.21 | -10.01 | -14.78 | -17.25
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Consumer Transformation | Thermal headroom (MW) | 13.58 | 13.33 | 12.95 | 12.71 | 12.15 | 11.47 | 10.89 | 10.5 | 9.75 | 8.81 | 7.38 | 5.63 | 3.93 | 2.66 | 1.46 | -3.04 | -4.86 | -5.61
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Leading the Way | Thermal headroom (MW) | 13.58 | 13.16 | 12.6 | 12.22 | 11.48 | 10.73 | 10.05 | 9.22 | 8.09 | 6.91 | 5.51 | 4.08 | 2.72 | 1.46 | 0.38 | -1.81 | -1.82 | -0.61
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Steady Progression | Thermal headroom (MW) | 13.58 | 13.58 | 13.52 | 13.55 | 13.46 | 13.3 | 13.15 | 13.06 | 12.92 | 12.78 | 12.52 | 12.28 | 12 | 11.54 | 11.01 | 6.9 | 4.04 | 3.53
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | System Transformation | Thermal headroom (MW) | 13.58 | 13.48 | 13.32 | 13.27 | 13.04 | 12.9 | 12.73 | 12.63 | 12.46 | 12.33 | 12.02 | 11.56 | 10.87 | 9.73 | 8.6 | 4.44 | 3.34 | 3.75
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | WPD Best View | Thermal headroom (MW) | 13.58 | 13.33 | 12.95 | 12.71 | 12.15 | 11.47 | 10.89 | 10.5 | 9.75 | 8.81 | 7.38 | 5.63 | 3.93 | 2.66 | 1.46 | -3.04 | -4.86 | -5.61
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Consumer Transformation | Thermal headroom (MW) | 18.73 | 18.65 | 18.32 | 17.72 | 16.91 | 15.85 | 14.57 | 13.38 | 11.88 | 10.33 | 8.39 | 6.42 | 4.64 | 2.93 | 1.33 | -6.67 | -10.93 | -12.84
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Leading the Way | Thermal headroom (MW) | 18.73 | 18.33 | 17.66 | 16.72 | 15.64 | 14.16 | 12.43 | 10.61 | 8.4 | 6.16 | 4.03 | 1.77 | -0.07 | -1.8 | -3.32 | -8.16 | -9.78 | -10.32
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Steady Progression | Thermal headroom (MW) | 18.73 | 18.94 | 18.94 | 18.81 | 18.72 | 18.47 | 18.11 | 17.8 | 17.27 | 16.79 | 16.16 | 15.57 | 14.91 | 14.11 | 13.37 | 8.94 | 6.2 | 5.13
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | System Transformation | Thermal headroom (MW) | 18.73 | 18.87 | 18.79 | 18.55 | 18.31 | 18.03 | 17.48 | 16.99 | 16.25 | 15.55 | 14.77 | 13.91 | 13.11 | 12.22 | 11.32 | 6.22 | 4.53 | 4.37
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | WPD Best View | Thermal headroom (MW) | 18.73 | 18.65 | 18.32 | 17.72 | 16.91 | 15.85 | 14.57 | 13.38 | 11.88 | 10.33 | 8.39 | 6.42 | 4.64 | 2.93 | 1.33 | -6.67 | -10.93 | -12.84
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Consumer Transformation | Thermal headroom (MW) | 83.98 | 83.2238 | 82.3872 | 80.6307 | 78.2482 | 74.5592 | 70.2091 | 65.7535 | 61.1367 | 56.4989 | 49.6749 | 44.0935 | 38.0127 | 32.0642 | 25.6934 | -2.8299 | -21.7199 | -33.2556
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Leading the Way | Thermal headroom (MW) | 83.98 | 82.5726 | 81.0354 | 78.593 | 75.3131 | 70.3668 | 64.4864 | 58.0015 | 50.5656 | 43.1001 | 36.5659 | 31.0001 | 25.0489 | 18.9333 | 13.2719 | -4.15 | -11.0645 | -14.2264
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Steady Progression | Thermal headroom (MW) | 83.98 | 83.98 | 83.9151 | 83.4971 | 82.9302 | 81.4404 | 79.6378 | 77.7007 | 75.577 | 72.8781 | 69.6478 | 67.4415 | 65.0956 | 62.5033 | 60.2008 | 46.9986 | 39.4453 | 36.0748
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | System Transformation | Thermal headroom (MW) | 83.98 | 83.606 | 83.237 | 82.3624 | 81.2037 | 79.3959 | 76.7802 | 74.1063 | 71.1544 | 68.3893 | 64.8734 | 62.4739 | 59.4419 | 56.7345 | 53.802 | 40.3481 | 34.1101 | 32.2686
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | WPD Best View | Thermal headroom (MW) | 83.98 | 83.2238 | 82.3872 | 80.6307 | 78.2482 | 74.5592 | 70.2091 | 65.7535 | 61.1367 | 56.4989 | 49.6749 | 44.0935 | 38.0127 | 32.0642 | 25.6934 | -2.8299 | -21.7199 | -33.2556
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Consumer Transformation | Thermal headroom (MW) | 11.92 | 11.81 | 11.54 | 11.03 | 10.38 | 9.65 | 9 | 8.41 | 7.71 | 6.95 | 6.09 | 5.34 | 4.26 | 3.03 | 1.77 | -5.18 | -9.66 | -11.98
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Leading the Way | Thermal headroom (MW) | 11.92 | 11.66 | 11.19 | 10.49 | 9.63 | 8.63 | 7.67 | 6.72 | 5.65 | 4.51 | 3.45 | 2.07 | 0.67 | -0.69 | -1.96 | -6.27 | -8.32 | -9.39
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Steady Progression | Thermal headroom (MW) | 11.92 | 12.02 | 12 | 11.88 | 11.73 | 11.47 | 11.24 | 10.96 | 10.6 | 10.2 | 9.71 | 9.22 | 8.68 | 8.12 | 7.58 | 4.56 | 3.09 | 2.12
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | System Transformation | Thermal headroom (MW) | 11.92 | 11.96 | 11.85 | 11.63 | 11.36 | 11.11 | 10.86 | 10.54 | 10.1 | 9.58 | 9.06 | 8.5 | 7.93 | 7.38 | 6.92 | 4.61 | 2.97 | 2.46
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | WPD Best View | Thermal headroom (MW) | 11.92 | 11.81 | 11.54 | 11.03 | 10.38 | 9.65 | 9 | 8.41 | 7.71 | 6.95 | 6.09 | 5.34 | 4.26 | 3.03 | 1.77 | -5.18 | -9.66 | -11.98
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Consumer Transformation | Thermal headroom (MW) | 12.42 | 12.42 | 12.39 | 12.24 | 12.02 | 11.69 | 11.31 | 10.84 | 10.36 | 9.83 | 9.27 | 8.96 | 8.68 | 8.41 | 8.07 | 6.01 | 5.35 | 4.97
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Leading the Way | Thermal headroom (MW) | 12.42 | 12.39 | 12.33 | 12.14 | 11.88 | 11.5 | 11.07 | 10.5 | 9.93 | 9.3 | 8.7 | 8.4 | 8.08 | 7.71 | 7.39 | 5.94 | 5.57 | 5.5
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Steady Progression | Thermal headroom (MW) | 12.42 | 12.45 | 12.46 | 12.4 | 12.34 | 12.22 | 12.07 | 11.89 | 11.69 | 11.48 | 11.24 | 11.04 | 10.83 | 10.62 | 10.41 | 9.32 | 8.65 | 8.39
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | System Transformation | Thermal headroom (MW) | 12.42 | 12.44 | 12.43 | 12.36 | 12.26 | 12.1 | 11.88 | 11.64 | 11.36 | 11.06 | 10.76 | 10.54 | 10.32 | 10.11 | 9.91 | 9.01 | 8.85 | 8.89
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | WPD Best View | Thermal headroom (MW) | 12.42 | 12.42 | 12.39 | 12.24 | 12.02 | 11.69 | 11.31 | 10.84 | 10.36 | 9.83 | 9.27 | 8.96 | 8.68 | 8.41 | 8.07 | 6.01 | 5.35 | 4.97
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Consumer Transformation | Thermal headroom (MW) | 10.94 | 10.7 | 10.4 | 10.02 | 9.49 | 8.32 | 6.66 | 5.14 | 3.62 | 2.44 | -0.28 | -2.69 | -5.24 | -7.79 | -10.49 | -17.29 | -25.02 | -30.8
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Leading the Way | Thermal headroom (MW) | 10.94 | 10.59 | 10.18 | 9.69 | 8.84 | 7.2 | 4.8 | 2.39 | -1.06 | -4.09 | -5.87 | -7.6 | -9.67 | -11.77 | -13.76 | -16.88 | -18.23 | -19.38
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Steady Progression | Thermal headroom (MW) | 10.94 | 10.88 | 10.79 | 10.68 | 10.55 | 9.94 | 9.17 | 8.44 | 7.66 | 6.36 | 4.82 | 4.26 | 3.65 | 2.83 | 2.29 | -0.65 | -1.7 | -1.91
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | System Transformation | Thermal headroom (MW) | 10.94 | 10.67 | 10.44 | 10.15 | 9.77 | 8.94 | 7.59 | 6.36 | 5.08 | 4.29 | 2.68 | 2.09 | 0.88 | 0.22 | -0.91 | -5.59 | -8.28 | -9.42
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | WPD Best View | Thermal headroom (MW) | 10.94 | 10.7 | 10.4 | 10.02 | 9.49 | 8.32 | 6.66 | 5.14 | 3.62 | 2.44 | -0.28 | -2.69 | -5.24 | -7.79 | -10.49 | -17.29 | -25.02 | -30.8
Berkswell 132kV | Coventry West | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Consumer Transformation | Thermal headroom (MW) | -1.03 | -2.48 | -3.11 | -3.96 | -5.22 | -6.92 | -8.97 | -10.84 | -12.57 | -14.24 | -16.88 | -19.75 | -23.64 | -27.43 | -31.2 | -47.47 | -60.18 | -67.75
Berkswell 132kV | Coventry West | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Leading the Way | Thermal headroom (MW) | -1.03 | -2.92 | -3.89 | -5.06 | -6.66 | -8.8 | -11.75 | -14.55 | -17.38 | -20.32 | -23.69 | -27.37 | -31.16 | -34.77 | -38.12 | -48.25 | -53.28 | -56.15
Berkswell 132kV | Coventry West | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Steady Progression | Thermal headroom (MW) | -1.03 | -1.85 | -1.94 | -2.09 | -2.38 | -2.97 | -3.84 | -4.64 | -5.51 | -6.71 | -8.14 | -9.24 | -10.44 | -11.78 | -13.02 | -19.52 | -22.99 | -24.84
Berkswell 132kV | Coventry West | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | System Transformation | Thermal headroom (MW) | -1.03 | -2.11 | -2.35 | -2.7 | -3.26 | -3.87 | -4.91 | -5.88 | -6.93 | -8.02 | -9.11 | -10.28 | -11.82 | -13.31 | -14.66 | -21.53 | -25.42 | -26.81
Berkswell 132kV | Coventry West | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | WPD Best View | Thermal headroom (MW) | -1.03 | -2.48 | -3.11 | -3.96 | -5.22 | -6.92 | -8.97 | -10.84 | -12.57 | -14.24 | -16.88 | -19.75 | -23.64 | -27.43 | -31.2 | -47.47 | -60.18 | -67.75
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Consumer Transformation | Thermal headroom (MW) | 5.168 | 4.998 | 4.648 | 4.188 | 3.638 | 2.738 | 1.938 | 1.188 | 0.368 | -0.572 | -2.672 | -5.102 | -7.602 | -9.692 | -11.782 | -23.682 | -31.892 | -35.802
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Leading the Way | Thermal headroom (MW) | 5.168 | 4.458 | 3.538 | 2.548 | 1.438 | -0.252 | -1.782 | -3.402 | -4.982 | -6.722 | -8.822 | -11.062 | -13.302 | -15.532 | -17.692 | -24.782 | -28.292 | -29.382
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Steady Progression | Thermal headroom (MW) | 5.168 | 5.378 | 5.428 | 5.458 | 5.468 | 5.138 | 4.828 | 4.458 | 4.088 | 3.698 | 3.158 | 2.568 | 1.978 | 1.328 | 0.668 | -4.812 | -9.192 | -11.382
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | System Transformation | Thermal headroom (MW) | 5.168 | 5.258 | 5.168 | 5.048 | 4.828 | 4.508 | 4.218 | 3.908 | 3.578 | 3.148 | 2.598 | 1.918 | 1.178 | 0.038 | -1.162 | -6.782 | -9.802 | -10.732
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | WPD Best View | Thermal headroom (MW) | 5.168 | 4.998 | 4.648 | 4.188 | 3.638 | 2.738 | 1.938 | 1.188 | 0.368 | -0.572 | -2.672 | -5.102 | -7.602 | -9.692 | -11.782 | -23.682 | -31.892 | -35.802
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Consumer Transformation | Thermal headroom (MW) | 102.24 | 101.6938 | 101.1683 | 100.7214 | 99.9351 | 99.1984 | 98.481 | 97.7691 | 97.0454 | 96.2519 | 94.7404 | 92.7145 | 90.5551 | 88.5673 | 86.5798 | 77.1172 | 70.2989 | 66.5955
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Leading the Way | Thermal headroom (MW) | 102.24 | 101.4059 | 100.6013 | 99.9342 | 98.8425 | 97.8002 | 96.6811 | 95.4433 | 93.9655 | 92.3269 | 90.7286 | 88.9821 | 87.0769 | 85.2095 | 83.4106 | 77.2209 | 74.6073 | 73.6336
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Steady Progression | Thermal headroom (MW) | 102.24 | 101.9587 | 101.6741 | 101.5021 | 101.1028 | 100.7292 | 100.3332 | 99.9303 | 99.5222 | 98.9674 | 98.1951 | 97.5765 | 96.9096 | 96.195 | 95.5272 | 90.2969 | 86.9232 | 85.4873
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | System Transformation | Thermal headroom (MW) | 102.24 | 101.8264 | 101.4317 | 101.1574 | 100.5813 | 100.3014 | 100.0181 | 99.6911 | 99.3266 | 98.9018 | 98.3826 | 97.8431 | 97.1087 | 96.2058 | 95.3504 | 89.1479 | 85.334 | 84.4519
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | WPD Best View | Thermal headroom (MW) | 102.24 | 101.9525 | 101.6633 | 101.4867 | 101.0806 | 100.6858 | 100.2681 | 99.8415 | 99.4085 | 98.826 | 98.043 | 97.4131 | 96.734 | 96.008 | 95.3282 | 89.9203 | 86.4928 | 85.0014
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Consumer Transformation | Thermal headroom (MW) | 11.92 | 11.09 | 10.72 | 10.4 | 9.52 | 9.07 | 8.67 | 8.3 | 7.91 | 7.47 | 6.08 | 4.74 | 3.41 | 1.94 | 0.36 | -3.3 | -8.14 | -11.45
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Leading the Way | Thermal headroom (MW) | 11.92 | 10.88 | 10.38 | 9.99 | 8.9 | 8.48 | 7.96 | 7.39 | 6.53 | 5.64 | 4.97 | 4.17 | 3.08 | 1.97 | 0.88 | -1.52 | -2.71 | -3.29
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Steady Progression | Thermal headroom (MW) | 11.92 | 11.26 | 10.98 | 10.75 | 10.06 | 9.75 | 9.45 | 9.18 | 8.94 | 8.43 | 7.73 | 7.38 | 7 | 6.57 | 6.24 | 3.61 | 2.5 | 2.27
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | System Transformation | Thermal headroom (MW) | 11.92 | 11.13 | 10.79 | 10.51 | 9.68 | 9.54 | 9.45 | 9.34 | 9.22 | 9.09 | 8.89 | 8.71 | 8.16 | 7.59 | 7.01 | 3.87 | 1.77 | 1.4
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | WPD Best View | Thermal headroom (MW) | 11.92 | 11.26 | 10.97 | 10.75 | 10.06 | 9.74 | 9.44 | 9.17 | 8.92 | 8.41 | 7.72 | 7.36 | 6.99 | 6.56 | 6.23 | 3.62 | 2.53 | 2.29
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Consumer Transformation | Thermal headroom (MW) | 13.9 | 13.76 | 13.35 | 13.1 | 12.8 | 12.38 | 11.95 | 11.52 | 11.1 | 10.65 | 10.18 | 9.37 | 8.38 | 7.44 | 6.54 | 0.86 | -2.14 | -3.63
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Leading the Way | Thermal headroom (MW) | 13.9 | 13.62 | 13.05 | 12.66 | 12.21 | 11.63 | 10.97 | 10.23 | 9.51 | 8.66 | 7.75 | 6.78 | 5.81 | 4.88 | 3.97 | 0.15 | -1.22 | -1.78
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Steady Progression | Thermal headroom (MW) | 13.9 | 13.9 | 13.66 | 13.58 | 13.5 | 13.3 | 13.09 | 12.85 | 12.6 | 12.36 | 12.03 | 11.68 | 11.3 | 10.92 | 10.53 | 7.6 | 5.65 | 4.65
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | System Transformation | Thermal headroom (MW) | 13.9 | 13.84 | 13.52 | 13.39 | 13.23 | 13.04 | 12.84 | 12.62 | 12.38 | 12.11 | 11.79 | 11.46 | 11.12 | 10.79 | 10.5 | 7.09 | 4.89 | 4.36
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | WPD Best View | Thermal headroom (MW) | 13.9 | 13.89 | 13.64 | 13.56 | 13.47 | 13.24 | 13 | 12.73 | 12.45 | 12.17 | 11.82 | 11.46 | 11.06 | 10.65 | 10.25 | 7.1 | 5.06 | 4.02
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Consumer Transformation | Thermal headroom (MW) | 4.36 | 4.25 | 4.04 | 3.75 | 3.38 | 2.83 | 2.28 | 1.72 | 1.14 | 0.5 | -0.64 | -2.48 | -4.38 | -5.84 | -7.24 | -16.06 | -21.55 | -24.04
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Leading the Way | Thermal headroom (MW) | 4.36 | 4.03 | 3.58 | 3.08 | 2.46 | 1.46 | 0.49 | -0.58 | -1.87 | -3.3 | -4.8 | -6.39 | -8.03 | -9.62 | -11.12 | -16.74 | -19.23 | -19.97
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Steady Progression | Thermal headroom (MW) | 4.36 | 4.45 | 4.44 | 4.41 | 4.37 | 4.16 | 3.91 | 3.64 | 3.35 | 3.01 | 2.53 | 2.04 | 1.51 | 0.95 | 0.38 | -4.15 | -7.57 | -9.06
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | System Transformation | Thermal headroom (MW) | 4.36 | 4.37 | 4.29 | 4.17 | 4.01 | 3.81 | 3.57 | 3.28 | 2.94 | 2.53 | 2.05 | 1.53 | 1 | 0.11 | -0.72 | -6.13 | -9.18 | -9.96
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | WPD Best View | Thermal headroom (MW) | 4.36 | 4.45 | 4.44 | 4.41 | 4.37 | 4.15 | 3.9 | 3.62 | 3.32 | 2.98 | 2.49 | 1.99 | 1.46 | 0.9 | 0.33 | -4.31 | -7.76 | -9.29
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Consumer Transformation | Thermal headroom (MW) | 13.8 | 12.29 | 11 | 9.48 | 7.71 | 4.9 | 1.7 | -1.72 | -5.37 | -9.07 | -15.93 | -22.87 | -29.87 | -36.6 | -43.33 | -69.84 | -92.15 | -105.61
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Leading the Way | Thermal headroom (MW) | 13.8 | 11.44 | 8.59 | 5.99 | 3.03 | -1 | -5.6 | -10.77 | -16.8 | -22.66 | -28.49 | -34.9 | -41.46 | -47.86 | -53.82 | -69.82 | -76.16 | -79
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Steady Progression | Thermal headroom (MW) | 13.8 | 13.82 | 13.74 | 13.58 | 13.35 | 12.32 | 11.23 | 9.95 | 8.57 | 6.69 | 4.16 | 2.35 | -0.06 | -2.79 | -5.4 | -21.76 | -32.97 | -37.06
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | System Transformation | Thermal headroom (MW) | 13.8 | 13.47 | 13.03 | 12.44 | 11.74 | 10.71 | 9.46 | 7.95 | 6.21 | 4.68 | 2.42 | -0.14 | -2.99 | -6.02 | -9.56 | -26.28 | -32.49 | -33.76
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | WPD Best View | Thermal headroom (MW) | 13.8 | 12.29 | 11 | 9.48 | 7.71 | 4.91 | 1.71 | -1.7 | -5.33 | -9.02 | -15.88 | -22.82 | -29.81 | -36.54 | -43.26 | -69.63 | -91.93 | -105.34
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Consumer Transformation | Thermal headroom (MW) | 80.36 | 78.9687 | 76.4137 | 73.8969 | 70.3343 | 65.3672 | 60.8401 | 56.2652 | 51.5224 | 46.4997 | 38.5762 | 29.2383 | 18.7515 | 9.2458 | 0.03569 | -48.658 | -78.9617 | -93.7439
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Leading the Way | Thermal headroom (MW) | 80.36 | 77.589 | 73.3603 | 69.4087 | 64.1962 | 57.0244 | 50.0616 | 42.681 | 34.8015 | 26.1217 | 16.8521 | 6.7631 | -3.2106 | -12.8573 | -21.7741 | -54.1058 | -67.2072 | -72.251
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Steady Progression | Thermal headroom (MW) | 80.36 | 80.5345 | 79.6816 | 79.19 | 78.2901 | 76.3672 | 74.4457 | 72.4012 | 70.1141 | 67.4605 | 63.8174 | 60.347 | 56.6297 | 52.5472 | 48.4389 | 20.7647 | 2.9285 | -5.4766
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | System Transformation | Thermal headroom (MW) | 80.36 | 80.0643 | 78.6378 | 77.5323 | 75.798 | 73.963 | 72.2359 | 70.1675 | 67.5648 | 64.6861 | 61.2771 | 57.638 | 53.6087 | 48.804 | 43.8913 | 14.8187 | -1.7681 | -5.917
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | WPD Best View | Thermal headroom (MW) | 80.36 | 79.3014 | 77.0388 | 74.998 | 72.0185 | 67.8374 | 64.0213 | 60.1202 | 56.0294 | 51.7221 | 45.2645 | 38.0857 | 29.9405 | 21.9176 | 14.1359 | -31.5882 | -60.3964 | -74.4743
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Consumer Transformation | Thermal headroom (MW) | 6.12 | 5.47 | 4.62 | 3.39 | 2.3 | 0.87 | -0.27 | -1.37 | -2.51 | -3.51 | -4.74 | -6.22 | -8.04 | -9.91 | -11.71 | -22.59 | -29.46 | -32.75
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Leading the Way | Thermal headroom (MW) | 6.12 | 5.15 | 3.95 | 2.36 | 0.99 | -1.04 | -2.74 | -4.45 | -6.12 | -7.78 | -9.72 | -11.75 | -13.75 | -15.7 | -17.46 | -24.18 | -27.08 | -28.69
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Steady Progression | Thermal headroom (MW) | 6.12 | 5.89 | 5.57 | 5.01 | 4.7 | 4.05 | 3.44 | 2.81 | 2.17 | 1.52 | 0.7 | -0.11 | -0.94 | -1.8 | -2.62 | -7.19 | -10.09 | -11.44
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | System Transformation | Thermal headroom (MW) | 6.12 | 5.75 | 5.28 | 4.52 | 4.01 | 3.38 | 2.82 | 2.21 | 1.52 | 0.88 | 0.14 | -0.64 | -1.39 | -2.12 | -2.75 | -6.91 | -10.47 | -11.94
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | WPD Best View | Thermal headroom (MW) | 6.12 | 5.63 | 4.98 | 4.02 | 3.2 | 2.07 | 1.19 | 0.3 | -0.65 | -1.43 | -2.41 | -3.45 | -4.55 | -5.64 | -6.68 | -15.42 | -20.6 | -22.89
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Consumer Transformation | Thermal headroom (MW) | 5.09 | 4.91 | 4.14 | 3.78 | 3.32 | 2.55 | 1.8 | 1.03 | 0.22 | -0.66 | -1.87 | -3.65 | -5.49 | -7.3 | -9.06 | -19.21 | -25.9 | -29.36
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Leading the Way | Thermal headroom (MW) | 5.09 | 4.64 | 3.5 | 2.8 | 1.9 | 0.64 | -0.59 | -1.89 | -3.22 | -4.9 | -6.82 | -8.81 | -10.84 | -12.79 | -14.62 | -21.44 | -24.4 | -26.1
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Steady Progression | Thermal headroom (MW) | 5.09 | 5.21 | 4.8 | 4.79 | 4.74 | 4.48 | 4.19 | 3.82 | 3.36 | 2.87 | 2.19 | 1.5 | 0.77 | 0 | -0.77 | -5.25 | -8.78 | -10.68
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | System Transformation | Thermal headroom (MW) | 5.09 | 5.11 | 4.55 | 4.41 | 4.23 | 3.98 | 3.69 | 3.28 | 2.76 | 2.14 | 1.45 | 0.7 | -0.09 | -0.84 | -1.56 | -6.24 | -8.98 | -9.98
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | WPD Best View | Thermal headroom (MW) | 5.09 | 4.91 | 4.14 | 3.78 | 3.32 | 2.55 | 1.8 | 1.03 | 0.22 | -0.66 | -1.87 | -3.65 | -5.49 | -7.3 | -9.06 | -19.22 | -25.92 | -29.38
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Consumer Transformation | Thermal headroom (MW) | 0.64 | 0.62 | 0.46 | 0.16 | -0.2 | -0.85 | -1.51 | -2.21 | -2.93 | -3.74 | -5.63 | -7.56 | -9.51 | -11.32 | -13.12 | -21.2 | -25.33 | -27.36
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Leading the Way | Thermal headroom (MW) | 0.64 | 0.5 | 0.2 | -0.22 | -0.75 | -1.7 | -2.8 | -4.14 | -5.87 | -7.75 | -9.35 | -11.07 | -12.77 | -14.4 | -15.89 | -21.66 | -23.41 | -23.88
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Steady Progression | Thermal headroom (MW) | 0.64 | 0.78 | 0.79 | 0.74 | 0.69 | 0.35 | -0.01 | -0.42 | -0.9 | -1.41 | -2.06 | -2.73 | -3.47 | -4.49 | -5.57 | -13.12 | -16.99 | -18.66
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | System Transformation | Thermal headroom (MW) | 0.64 | 0.73 | 0.67 | 0.53 | 0.35 | 0.16 | -0.07 | -0.38 | -0.77 | -1.24 | -1.86 | -2.52 | -3.2 | -3.86 | -4.86 | -12.32 | -16.74 | -17.57
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | WPD Best View | Thermal headroom (MW) | 0.64 | 0.74 | 0.69 | 0.56 | 0.41 | -0.01 | -0.45 | -0.93 | -1.46 | -2.03 | -2.73 | -3.79 | -4.96 | -6.15 | -7.36 | -14.26 | -17.87 | -19.72
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Consumer Transformation | Thermal headroom (MW) | 14.53 | 14.56 | 14.02 | 13.87 | 13.09 | 12.44 | 12.07 | 11.64 | 11.18 | 10.61 | 9.76 | 8.94 | 8.15 | 7.37 | 6.65 | 3.21 | 1.22 | 0.39
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Leading the Way | Thermal headroom (MW) | 14.53 | 14.39 | 13.67 | 13.39 | 12.33 | 11.38 | 10.83 | 10.27 | 9.62 | 8.84 | 8 | 7.06 | 6.27 | 5.55 | 4.81 | 2.6 | 1.78 | 1.77
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Steady Progression | Thermal headroom (MW) | 14.53 | 14.67 | 14.35 | 14.37 | 13.93 | 13.62 | 13.45 | 13.28 | 13.06 | 12.85 | 12.6 | 12.36 | 12.09 | 11.82 | 11.55 | 9.6 | 8.31 | 7.86
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | System Transformation | Thermal headroom (MW) | 14.53 | 14.65 | 14.24 | 14.22 | 13.66 | 13.19 | 12.98 | 12.79 | 12.59 | 12.35 | 12.02 | 11.7 | 11.33 | 10.97 | 10.59 | 8.56 | 7.83 | 7.77
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | WPD Best View | Thermal headroom (MW) | 14.53 | 14.56 | 14.02 | 13.87 | 13.09 | 12.44 | 12.07 | 11.64 | 11.18 | 10.61 | 9.76 | 8.94 | 8.15 | 7.37 | 6.65 | 3.21 | 1.22 | 0.39
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Consumer Transformation | Thermal headroom (MW) | 9.29 | 9.29 | 9.27 | 9.21 | 9.1 | 8.83 | 8.57 | 8.31 | 8.05 | 7.74 | 7.28 | 6.46 | 5.64 | 5.2 | 4.78 | 2.06 | 0.51 | -0.06
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Leading the Way | Thermal headroom (MW) | 9.29 | 9.26 | 9.14 | 9.01 | 8.83 | 8.46 | 8.05 | 7.62 | 7.18 | 6.67 | 6.27 | 5.81 | 5.35 | 4.9 | 4.48 | 2.55 | 1.57 | 1.41
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Steady Progression | Thermal headroom (MW) | 9.29 | 9.35 | 9.37 | 9.38 | 9.38 | 9.31 | 9.25 | 9.18 | 9.11 | 9.01 | 8.77 | 8.55 | 8.33 | 8.11 | 7.89 | 5.59 | 4.07 | 3.47
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | System Transformation | Thermal headroom (MW) | 9.29 | 9.33 | 9.33 | 9.32 | 9.29 | 9.26 | 9.23 | 9.15 | 9.02 | 8.86 | 8.67 | 8.47 | 8.23 | 7.58 | 6.94 | 4.21 | 2.69 | 2.57
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | WPD Best View | Thermal headroom (MW) | 9.29 | 9.34 | 9.35 | 9.35 | 9.34 | 9.24 | 9.15 | 9.06 | 8.96 | 8.83 | 8.56 | 8.3 | 8.05 | 7.8 | 7.55 | 4.99 | 3.29 | 2.59
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Consumer Transformation | Thermal headroom (MW) | 17.02 | 17.05 | 17.02 | 16.97 | 16.88 | 16.76 | 16.62 | 16.45 | 16.27 | 16.06 | 15.82 | 15.61 | 15.15 | 14.69 | 14.28 | 11.64 | 10.23 | 9.62
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Leading the Way | Thermal headroom (MW) | 17.02 | 17 | 16.9 | 16.81 | 16.68 | 16.49 | 16.27 | 16 | 15.71 | 15.4 | 15.01 | 14.5 | 13.97 | 13.46 | 13.01 | 11.09 | 10.51 | 10.4
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Steady Progression | Thermal headroom (MW) | 17.02 | 17.11 | 17.14 | 17.16 | 17.17 | 17.14 | 17.09 | 17.05 | 16.99 | 16.88 | 16.74 | 16.6 | 16.45 | 16.28 | 16.1 | 14.86 | 13.91 | 13.18
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | System Transformation | Thermal headroom (MW) | 17.02 | 17.1 | 17.11 | 17.11 | 17.1 | 17.1 | 17.08 | 17.06 | 16.95 | 16.83 | 16.7 | 16.56 | 16.39 | 16.24 | 16.1 | 14.5 | 13.62 | 13.52
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | WPD Best View | Thermal headroom (MW) | 17.02 | 17.05 | 17.02 | 16.97 | 16.88 | 16.76 | 16.62 | 16.45 | 16.27 | 16.06 | 15.82 | 15.61 | 15.15 | 14.69 | 14.28 | 11.64 | 10.23 | 9.62
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Consumer Transformation | Thermal headroom (MW) | 3.94 | 3.57 | 3.07 | 2.5 | 1.78 | 0.6 | -0.49 | -1.6 | -2.81 | -4.21 | -6.76 | -9.31 | -11.92 | -14.44 | -16.88 | -28.66 | -36.18 | -39.78
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Leading the Way | Thermal headroom (MW) | 3.94 | 2.92 | 1.75 | 0.59 | -0.79 | -2.54 | -4.23 | -6.08 | -8.09 | -10.26 | -12.85 | -15.58 | -18.31 | -20.97 | -23.47 | -31.09 | -33.68 | -34.44
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Steady Progression | Thermal headroom (MW) | 3.94 | 4.08 | 4.11 | 4.14 | 4.08 | 3.74 | 3.35 | 2.9 | 2.43 | 1.88 | 1.06 | 0.25 | -0.66 | -1.61 | -2.64 | -9.56 | -14.39 | -16.35
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | System Transformation | Thermal headroom (MW) | 3.94 | 3.97 | 3.86 | 3.69 | 3.39 | 3.04 | 2.71 | 2.28 | 1.74 | 1.13 | 0.28 | -0.68 | -1.74 | -2.89 | -4.11 | -11.01 | -13.78 | -14.82
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | WPD Best View | Thermal headroom (MW) | 3.94 | 3.57 | 3.07 | 2.5 | 1.78 | 0.6 | -0.49 | -1.6 | -2.81 | -4.21 | -6.76 | -9.31 | -11.92 | -14.44 | -16.88 | -28.66 | -36.18 | -39.78
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Consumer Transformation | Thermal headroom (MW) | 41.2 | 41.3685 | 41.1701 | 40.8803 | 40.3545 | 38.1307 | 35.8472 | 33.5947 | 31.2898 | 28.8365 | 25.4602 | 21.9288 | 18.2046 | 14.3821 | 10.5368 | -6.2623 | -18.7874 | -27.9838
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Leading the Way | Thermal headroom (MW) | 41.2 | 40.9579 | 40.3419 | 39.6365 | 38.2386 | 34.3712 | 30.4674 | 25.7731 | 18.2732 | 10.2173 | 6.9317 | 2.1623 | -3.8469 | -10.1673 | -16.0808 | -37.1319 | -54.9104 | -72.5664
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Steady Progression | Thermal headroom (MW) | 41.2 | 41.3939 | 41.2866 | 41.1693 | 41.0034 | 40.008 | 39.0077 | 37.9877 | 36.9156 | 34.3193 | 30.8948 | 29.439 | 27.7907 | 25.6107 | 23.8853 | 11.4801 | 6.4353 | 4.553
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | System Transformation | Thermal headroom (MW) | 41.2 | 41.2065 | 40.9714 | 40.6435 | 40.152 | 39.4806 | 38.6603 | 37.65 | 36.4013 | 35.4031 | 32.6669 | 31.2396 | 28.6062 | 26.796 | 24.2898 | 9.9594 | -5.4676 | -12.6523
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | WPD Best View | Thermal headroom (MW) | 41.2 | 41.3473 | 41.1225 | 40.8176 | 40.2998 | 38.487 | 36.6242 | 34.8145 | 33.0065 | 30.9836 | 27.9248 | 24.8858 | 21.7411 | 18.3136 | 14.8686 | -0.58518 | -11.331 | -17.6365
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Consumer Transformation | Thermal headroom (MW) | 5.31 | 5.39 | 5.41 | 5.41 | 5.38 | 4.42 | 3.44 | 2.47 | 1.51 | 0.49 | -0.66 | -1.8 | -2.99 | -4.13 | -5.26 | -10.79 | -14.44 | -17.7
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Leading the Way | Thermal headroom (MW) | 5.31 | 5.28 | 5.19 | 5.09 | 4.9 | 3.34 | 1.81 | 0.18 | -1.77 | -3.86 | -4.85 | -6.01 | -7.31 | -8.67 | -9.95 | -15.91 | -20.21 | -24.58
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Steady Progression | Thermal headroom (MW) | 5.31 | 5.31 | 5.24 | 5.16 | 5.07 | 4.6 | 4.16 | 3.71 | 3.26 | 2.66 | 1.84 | 1.27 | 0.64 | -0.04 | -0.72 | -5.7 | -7.6 | -8.14
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | System Transformation | Thermal headroom (MW) | 5.31 | 5.28 | 5.2 | 5.09 | 4.94 | 4.71 | 4.46 | 4.12 | 3.68 | 3.38 | 2.52 | 2.01 | 1.13 | 0.44 | -0.42 | -5.81 | -11.82 | -14.77
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | WPD Best View | Thermal headroom (MW) | 5.31 | 5.36 | 5.35 | 5.33 | 5.28 | 4.62 | 3.95 | 3.32 | 2.7 | 1.99 | 1.1 | 0.33 | -0.51 | -1.34 | -2.19 | -6.31 | -8.35 | -9.19
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Consumer Transformation | Thermal headroom (MW) | 6.84 | 6.9 | 6.88 | 6.87 | 6.84 | 6.64 | 6.45 | 6.26 | 6.09 | 5.94 | 5.8 | 5.63 | 5.45 | 5.28 | 5.11 | 4.41 | 4.16 | 4.06
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Leading the Way | Thermal headroom (MW) | 6.84 | 6.86 | 6.81 | 6.77 | 6.69 | 6.37 | 6.06 | 5.71 | 5.23 | 4.76 | 4.65 | 4.46 | 4.17 | 3.88 | 3.6 | 2.71 | 2.13 | 1.56
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Steady Progression | Thermal headroom (MW) | 6.84 | 6.9 | 6.9 | 6.91 | 6.92 | 6.86 | 6.79 | 6.73 | 6.66 | 6.53 | 6.34 | 6.26 | 6.17 | 6.06 | 5.98 | 5.26 | 5.15 | 5.18
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | System Transformation | Thermal headroom (MW) | 6.84 | 6.87 | 6.85 | 6.84 | 6.81 | 6.76 | 6.69 | 6.62 | 6.53 | 6.48 | 6.25 | 6.19 | 6 | 5.92 | 5.71 | 4.72 | 3.7 | 3.24
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | WPD Best View | Thermal headroom (MW) | 6.84 | 6.9 | 6.88 | 6.87 | 6.84 | 6.64 | 6.45 | 6.26 | 6.09 | 5.94 | 5.8 | 5.63 | 5.45 | 5.28 | 5.11 | 4.41 | 4.16 | 4.06
Bicker Fen 132kV | Grantham | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Consumer Transformation | Thermal headroom (MW) | 1.85 | 1.94 | 1.91 | 1.83 | 1.69 | 1.23 | 0.81 | 0.4 | -0.02 | -0.46 | -1.05 | -1.71 | -2.57 | -3.42 | -4.28 | -7.29 | -8.8 | -9.61
Bicker Fen 132kV | Grantham | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Leading the Way | Thermal headroom (MW) | 1.85 | 1.86 | 1.73 | 1.57 | 1.29 | 0.69 | 0.1 | -0.76 | -1.91 | -3.09 | -3.67 | -4.45 | -5.36 | -6.29 | -7.1 | -10.45 | -12.31 | -13.9
Bicker Fen 132kV | Grantham | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Steady Progression | Thermal headroom (MW) | 1.85 | 1.98 | 2.01 | 2.02 | 2.03 | 1.8 | 1.56 | 1.31 | 0.99 | 0.5 | -0.2 | -0.68 | -1.19 | -1.76 | -2.29 | -7.09 | -8.86 | -9.29
Bicker Fen 132kV | Grantham | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | System Transformation | Thermal headroom (MW) | 1.85 | 1.9 | 1.86 | 1.79 | 1.67 | 1.58 | 1.47 | 1.32 | 1.12 | 0.92 | 0.26 | -0.09 | -0.7 | -1.09 | -1.63 | -5.88 | -10.68 | -12.23
Bicker Fen 132kV | Grantham | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | WPD Best View | Thermal headroom (MW) | 1.85 | 1.96 | 1.94 | 1.9 | 1.8 | 1.45 | 1.1 | 0.76 | 0.4 | -0.06 | -0.75 | -1.3 | -1.87 | -2.68 | -3.45 | -7.41 | -9.15 | -9.85
Bicker Fen 132kV | Grantham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Consumer Transformation | Thermal headroom (MW) | 1.29 | 1.34 | 1.32 | 1.29 | 1.25 | 0.97 | 0.69 | 0.43 | 0.12 | -0.23 | -0.71 | -1.18 | -1.67 | -2.1 | -2.52 | -5.17 | -6.55 | -7.23
Bicker Fen 132kV | Grantham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Leading the Way | Thermal headroom (MW) | 1.29 | 1.23 | 1.11 | 0.99 | 0.82 | 0.35 | -0.13 | -0.64 | -1.13 | -1.72 | -2.17 | -2.63 | -3.07 | -3.51 | -3.91 | -5.75 | -6.38 | -6.65
Bicker Fen 132kV | Grantham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Steady Progression | Thermal headroom (MW) | 1.29 | 1.36 | 1.38 | 1.39 | 1.39 | 1.29 | 1.19 | 1.09 | 0.99 | 0.89 | 0.72 | 0.57 | 0.41 | 0.19 | -0.03 | -1.98 | -3.07 | -3.31
Bicker Fen 132kV | Grantham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | System Transformation | Thermal headroom (MW) | 1.29 | 1.36 | 1.37 | 1.37 | 1.36 | 1.3 | 1.21 | 1.14 | 1.06 | 0.98 | 0.82 | 0.6 | 0.4 | 0.14 | -0.12 | -2.1 | -3.44 | -3.67
Bicker Fen 132kV | Grantham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | WPD Best View | Thermal headroom (MW) | 1.29 | 1.34 | 1.33 | 1.3 | 1.26 | 1.05 | 0.82 | 0.61 | 0.41 | 0.17 | -0.2 | -0.61 | -1.02 | -1.4 | -1.77 | -4.25 | -5.58 | -6.15
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Consumer Transformation | Thermal headroom (MW) | 6.65 | 6.54 | 6.05 | 5.35 | 4.26 | 2.69 | 0.91 | -0.9 | -2.8 | -4.94 | -9.95 | -15.24 | -20.61 | -26.49 | -32.61 | -52.6 | -76.92 | -94.41
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Leading the Way | Thermal headroom (MW) | 6.65 | 6.04 | 5.05 | 3.77 | 0.66 | -3.52 | -7.93 | -14.1 | -29.82 | -46.87 | -52.44 | -62.49 | -76.52 | -91.52 | -105.87 | -144.93 | -190.63 | -237.87
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Steady Progression | Thermal headroom (MW) | 6.65 | 6.74 | 6.59 | 6.4 | 6.15 | 5.5 | 4.75 | 3.96 | 3.07 | -3.03 | -10.56 | -11.72 | -13.22 | -16.36 | -17.68 | -22.96 | -25.15 | -26.94
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | System Transformation | Thermal headroom (MW) | 6.65 | 6.43 | 6.06 | 5.5 | 4.66 | 3.68 | 2.4 | 0.89 | -0.92 | -2.46 | -6.9 | -8.43 | -12.36 | -14.37 | -17.86 | -28.97 | -43.84 | -53.72
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | WPD Best View | Thermal headroom (MW) | 6.65 | 6.54 | 6.05 | 5.35 | 4.26 | 2.69 | 0.91 | -0.9 | -2.8 | -4.94 | -9.95 | -15.24 | -20.61 | -26.49 | -32.61 | -52.6 | -76.92 | -94.41
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Consumer Transformation | Thermal headroom (MW) | 7.66 | 7.65 | 7.57 | 7.48 | 7.35 | 7.08 | 6.81 | 6.53 | 6.25 | 5.96 | 5.7 | 5.37 | 5.03 | 4.58 | 4.17 | 1.54 | 0.43 | -0.17
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Leading the Way | Thermal headroom (MW) | 7.66 | 7.6 | 7.48 | 7.35 | 7.16 | 6.81 | 6.44 | 5.96 | 5.48 | 4.96 | 4.7 | 4.32 | 3.9 | 3.49 | 3.16 | 1.05 | 0.42 | 0.03
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Steady Progression | Thermal headroom (MW) | 7.66 | 7.69 | 7.68 | 7.66 | 7.64 | 7.54 | 7.43 | 7.31 | 7.18 | 7.04 | 6.84 | 6.63 | 6.41 | 6.18 | 5.93 | 3.98 | 3 | 2.38
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | System Transformation | Thermal headroom (MW) | 7.66 | 7.67 | 7.63 | 7.6 | 7.54 | 7.46 | 7.37 | 7.26 | 7.13 | 6.98 | 6.8 | 6.61 | 6.42 | 6.23 | 6.06 | 4.04 | 2.37 | 1.96
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | WPD Best View | Thermal headroom (MW) | 7.66 | 7.65 | 7.57 | 7.48 | 7.35 | 7.08 | 6.81 | 6.53 | 6.25 | 5.96 | 5.7 | 5.37 | 5.03 | 4.58 | 4.17 | 1.54 | 0.43 | -0.17
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Consumer Transformation | Thermal headroom (MW) | 29.304 | 29.289 | 28.854 | 28.1176 | 26.7624 | 23.2842 | 19.8386 | 16.4915 | 12.0553 | 6.4552 | -4.0441 | -15.3575 | -26.9929 | -37.8033 | -48.5759 | -94.4359 | -127.6133 | -146.7085
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Leading the Way | Thermal headroom (MW) | 29.304 | 28.6791 | 27.2512 | 25.6294 | 23.1216 | 17.3083 | 10.4623 | 2.226 | -7.4656 | -18.2897 | -26.7351 | -36.364 | -46.3389 | -56.1193 | -65.1831 | -96.8791 | -111.3978 | -119.0512
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Steady Progression | Thermal headroom (MW) | 29.304 | 30.1714 | 30.4753 | 30.6928 | 30.736 | 29.3695 | 27.8203 | 26.0025 | 24.0199 | 20.9833 | 16.207 | 12.1716 | 8.0299 | 3.2457 | -1.48 | -34.3819 | -49.7823 | -55.7463
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | System Transformation | Thermal headroom (MW) | 29.304 | 29.8658 | 29.8375 | 29.6599 | 29.1133 | 28.3857 | 27.3001 | 25.993 | 24.3941 | 22.5299 | 19.0854 | 15.6179 | 10.7966 | 5.2179 | -0.90135 | -35.685 | -58.1082 | -65.0027
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | WPD Best View | Thermal headroom (MW) | 29.304 | 29.8952 | 29.8893 | 29.7411 | 29.2454 | 28.4455 | 27.3023 | 25.9457 | 24.3182 | 22.3566 | 18.8927 | 15.3439 | 10.5458 | 4.8708 | -1.2768 | -36.4952 | -57.5284 | -63.9233
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Consumer Transformation | Thermal headroom (MW) | 1.18 | 1.16 | 1.11 | 1.01 | 0.84 | 0.41 | -0.04 | -0.47 | -1.26 | -2.09 | -4.26 | -6.45 | -8.6 | -10.74 | -12.93 | -20.34 | -27.27 | -31.73
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Leading the Way | Thermal headroom (MW) | 1.18 | 1.09 | 0.95 | 0.78 | 0.49 | -0.38 | -1.38 | -2.59 | -4.17 | -5.84 | -7.32 | -8.99 | -10.75 | -12.54 | -14.21 | -18.87 | -21.34 | -22.54
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Steady Progression | Thermal headroom (MW) | 1.18 | 1.23 | 1.24 | 1.24 | 1.23 | 1.02 | 0.78 | 0.49 | 0.17 | -0.44 | -1.38 | -1.99 | -2.6 | -3.32 | -3.98 | -8.74 | -11.15 | -12.19
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | System Transformation | Thermal headroom (MW) | 1.18 | 1.21 | 1.21 | 1.18 | 1.11 | 0.99 | 0.83 | 0.64 | 0.38 | 0.11 | -0.31 | -0.83 | -1.83 | -2.84 | -3.93 | -9.32 | -12.24 | -13.26
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | WPD Best View | Thermal headroom (MW) | 1.18 | 1.21 | 1.21 | 1.18 | 1.11 | 0.99 | 0.83 | 0.64 | 0.38 | 0.11 | -0.31 | -0.83 | -1.83 | -2.84 | -3.93 | -9.32 | -12.24 | -13.26
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Consumer Transformation | Thermal headroom (MW) | 3.67 | 3.69 | 3.63 | 3.53 | 3.42 | 2.93 | 2.48 | 2.06 | 1.63 | 1.09 | 0.21 | -0.65 | -1.53 | -2.39 | -3.21 | -6.3 | -8.02 | -8.98
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Leading the Way | Thermal headroom (MW) | 3.67 | 3.58 | 3.39 | 3.18 | 2.94 | 2.35 | 1.6 | 0.77 | -0.42 | -1.66 | -2.31 | -3.06 | -3.88 | -4.63 | -5.35 | -8.25 | -9.42 | -10.45
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Steady Progression | Thermal headroom (MW) | 3.67 | 3.78 | 3.8 | 3.83 | 3.85 | 3.65 | 3.44 | 3.15 | 2.85 | 2.48 | 1.79 | 1.2 | 0.6 | -0.04 | -0.65 | -4.86 | -6.09 | -6.32
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | System Transformation | Thermal headroom (MW) | 3.67 | 3.7 | 3.66 | 3.6 | 3.53 | 3.48 | 3.42 | 3.32 | 3.18 | 3.05 | 2.58 | 2.24 | 1.78 | 1.43 | 0.94 | -3.09 | -6.78 | -8.02
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | WPD Best View | Thermal headroom (MW) | 3.67 | 3.7 | 3.66 | 3.6 | 3.53 | 3.48 | 3.42 | 3.32 | 3.18 | 3.05 | 2.58 | 2.24 | 1.78 | 1.43 | 0.94 | -3.09 | -6.78 | -8.02
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Consumer Transformation | Thermal headroom (MW) | 0.27 | 0.28 | 0.19 | 0.07 | -0.19 | -0.81 | -1.69 | -2.34 | -3 | -3.73 | -5.9 | -8.46 | -11.07 | -13.61 | -16.21 | -25.63 | -33.37 | -38.21
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Leading the Way | Thermal headroom (MW) | 0.27 | 0.15 | -0.06 | -0.31 | -0.74 | -1.67 | -3.13 | -4.46 | -6.08 | -8.27 | -10.14 | -12.25 | -14.47 | -16.63 | -18.68 | -24.63 | -27.31 | -28.54
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Steady Progression | Thermal headroom (MW) | 0.27 | 0.45 | 0.52 | 0.57 | 0.61 | 0.42 | 0.06 | -0.22 | -0.53 | -1.15 | -2 | -2.49 | -3.01 | -3.7 | -4.41 | -10.43 | -13.35 | -14.39
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | System Transformation | Thermal headroom (MW) | 0.27 | 0.41 | 0.42 | 0.42 | 0.35 | 0.23 | -0.22 | -0.49 | -0.81 | -1.17 | -1.68 | -2.25 | -3.19 | -4.1 | -4.97 | -11.64 | -15.13 | -16.03
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | WPD Best View | Thermal headroom (MW) | 0.27 | 0.41 | 0.42 | 0.42 | 0.35 | 0.23 | -0.22 | -0.49 | -0.81 | -1.17 | -1.68 | -2.25 | -3.19 | -4.1 | -4.97 | -11.64 | -15.13 | -16.03
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Consumer Transformation | Thermal headroom (MW) | 11.23 | 11.35 | 11.36 | 11.34 | 11.3 | 11.14 | 11 | 10.88 | 10.74 | 10.57 | 10.25 | 9.97 | 9.51 | 8.98 | 8.49 | 5.53 | 3.78 | 3.03
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Leading the Way | Thermal headroom (MW) | 11.23 | 11.25 | 11.15 | 11.04 | 10.89 | 10.66 | 10.45 | 10.19 | 9.87 | 9.52 | 9.01 | 8.35 | 7.68 | 7.02 | 6.46 | 4.69 | 4.17 | 3.95
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Steady Progression | Thermal headroom (MW) | 11.23 | 11.43 | 11.52 | 11.61 | 11.69 | 11.69 | 11.69 | 11.69 | 11.67 | 11.65 | 11.54 | 11.44 | 11.33 | 11.18 | 11.03 | 9.64 | 8.64 | 8.64
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | System Transformation | Thermal headroom (MW) | 11.23 | 11.41 | 11.47 | 11.53 | 11.56 | 11.59 | 11.6 | 11.61 | 11.59 | 11.57 | 11.41 | 11.23 | 11.04 | 10.84 | 10.65 | 8.99 | 7.81 | 7.74
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | WPD Best View | Thermal headroom (MW) | 11.23 | 11.41 | 11.47 | 11.53 | 11.56 | 11.59 | 11.6 | 11.61 | 11.59 | 11.57 | 11.41 | 11.23 | 11.04 | 10.84 | 10.65 | 8.99 | 7.81 | 7.74
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Consumer Transformation | Thermal headroom (MW) | 4.22 | 4.22 | 4.16 | 4.04 | 3.84 | 3.22 | 2.58 | 1.89 | 1.19 | 0.02 | -1.28 | -2.92 | -4.59 | -5.86 | -7.12 | -13.22 | -16.25 | -17.59
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Leading the Way | Thermal headroom (MW) | 4.22 | 4.15 | 3.99 | 3.79 | 3.49 | 2.55 | 1.41 | -0.1 | -1.59 | -3.49 | -4.51 | -5.64 | -6.73 | -7.81 | -8.8 | -13.32 | -15.07 | -15.65
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Steady Progression | Thermal headroom (MW) | 4.22 | 4.28 | 4.28 | 4.27 | 4.24 | 3.95 | 3.63 | 3.21 | 2.81 | 2.3 | 1.65 | 0.91 | 0.18 | -0.6 | -1.42 | -7.01 | -9.52 | -10.63
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | System Transformation | Thermal headroom (MW) | 4.22 | 4.25 | 4.22 | 4.17 | 4.06 | 3.85 | 3.6 | 3.24 | 2.9 | 2.4 | 1.91 | 1.39 | 0.86 | -0.08 | -1.2 | -6.96 | -10.69 | -11.56
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | WPD Best View | Thermal headroom (MW) | 4.22 | 4.25 | 4.22 | 4.17 | 4.06 | 3.85 | 3.6 | 3.24 | 2.9 | 2.4 | 1.91 | 1.39 | 0.86 | -0.08 | -1.2 | -6.96 | -10.69 | -11.56
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Consumer Transformation | Thermal headroom (MW) | 5.58 | 5.54 | 5.4 | 5.2 | 4.87 | 4.39 | 3.96 | 3.5 | 2.8 | 1.89 | 0.23 | -1.74 | -3.76 | -5.35 | -6.87 | -17.03 | -23.11 | -25.9
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Leading the Way | Thermal headroom (MW) | 5.58 | 5.39 | 5.09 | 4.59 | 3.94 | 2.87 | 1.59 | 0.23 | -1.18 | -2.68 | -4.38 | -6.21 | -8.04 | -9.79 | -11.39 | -17.62 | -20.53 | -21.6
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Steady Progression | Thermal headroom (MW) | 5.58 | 5.72 | 5.78 | 5.82 | 5.82 | 5.66 | 5.49 | 5.29 | 5.07 | 4.8 | 4.31 | 3.67 | 3.03 | 2.34 | 1.59 | -3.45 | -6.44 | -7.71
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | System Transformation | Thermal headroom (MW) | 5.58 | 5.68 | 5.67 | 5.64 | 5.55 | 5.41 | 5.23 | 5 | 4.71 | 4.38 | 3.77 | 3.12 | 2.39 | 1.15 | -0.1 | -5.9 | -8.69 | -9.58
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | WPD Best View | Thermal headroom (MW) | 5.58 | 5.68 | 5.67 | 5.64 | 5.55 | 5.41 | 5.23 | 5 | 4.71 | 4.38 | 3.77 | 3.12 | 2.39 | 1.15 | -0.1 | -5.9 | -8.69 | -9.58
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Consumer Transformation | Thermal headroom (MW) | 15.28 | 14.79 | 14.53 | 14.22 | 13.68 | 12.52 | 11.44 | 10.4 | 8.53 | 6.16 | 1.65 | -2.9 | -7.51 | -12.01 | -16.54 | -34.48 | -51.42 | -62.56
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Leading the Way | Thermal headroom (MW) | 15.28 | 14.81 | 13.84 | 13.21 | 12.21 | 10.09 | 7.85 | 4.71 | 0.97 | -3.07 | -6.58 | -10.53 | -14.65 | -18.7 | -22.51 | -34.79 | -41.22 | -45.58
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Steady Progression | Thermal headroom (MW) | 15.28 | 15.52 | 15.63 | 15.73 | 15.77 | 15.44 | 15.09 | 14.69 | 14.26 | 13.31 | 11.72 | 10.48 | 9.14 | 7.24 | 5.47 | -4.67 | -10.73 | -13.53
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | System Transformation | Thermal headroom (MW) | 15.28 | 15.39 | 15.35 | 15.3 | 15.12 | 14.94 | 14.72 | 14.38 | 13.92 | 13.44 | 12.16 | 10.79 | 8.95 | 7 | 4.92 | -6.54 | -13.02 | -15.61
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | WPD Best View | Thermal headroom (MW) | 15.28 | 15.39 | 15.35 | 15.3 | 15.12 | 14.94 | 14.72 | 14.38 | 13.92 | 13.44 | 12.16 | 10.79 | 8.95 | 7 | 4.92 | -6.54 | -13.02 | -15.61
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Consumer Transformation | Thermal headroom (MW) | 1.04 | 1.2 | 1.26 | 1.29 | 1.17 | 0.76 | 0.41 | 0.07 | -0.27 | -0.63 | -1.24 | -1.8 | -2.5 | -3.25 | -4.04 | -6.64 | -7.7 | -8.19
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Leading the Way | Thermal headroom (MW) | 1.04 | 1.16 | 1.17 | 1.14 | 0.93 | 0.34 | -0.22 | -1.01 | -1.91 | -2.84 | -3.18 | -3.75 | -4.37 | -5.01 | -5.57 | -8.24 | -9.37 | -10.22
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Steady Progression | Thermal headroom (MW) | 1.04 | 1.2 | 1.27 | 1.3 | 1.27 | 1.05 | 0.84 | 0.62 | 0.33 | -0.05 | -0.61 | -1.04 | -1.49 | -1.96 | -2.43 | -6.05 | -6.78 | -7.07
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | System Transformation | Thermal headroom (MW) | 1.04 | 1.16 | 1.18 | 1.17 | 1.06 | 1 | 0.94 | 0.84 | 0.71 | 0.58 | 0.13 | -0.17 | -0.6 | -0.92 | -1.3 | -4.04 | -7.13 | -8.17
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | WPD Best View | Thermal headroom (MW) | 1.04 | 1.2 | 1.25 | 1.28 | 1.22 | 1.08 | 0.94 | 0.78 | 0.62 | 0.37 | -0.11 | -0.51 | -0.91 | -1.35 | -1.76 | -5.04 | -6.42 | -6.83
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Consumer Transformation | Thermal headroom (MW) | 45.2133 | 45.3141 | 44.8852 | 44.2002 | 43.1373 | 40.4134 | 37.7626 | 35.2305 | 32.6351 | 29.6852 | 24.6111 | 19.0992 | 13.1616 | 7.3974 | 1.6113 | -27.5304 | -45.2291 | -54.8648
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Leading the Way | Thermal headroom (MW) | 45.2133 | 44.6398 | 43.4799 | 42.1639 | 40.285 | 35.661 | 31.181 | 26.1754 | 20.5346 | 14.0899 | 9.1172 | 3.7055 | -1.9579 | -7.4915 | -12.6205 | -32.5903 | -40.8816 | -45.554
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Steady Progression | Thermal headroom (MW) | 45.2133 | 45.7914 | 45.8656 | 45.901 | 45.8328 | 44.6582 | 43.5305 | 42.3896 | 41.0994 | 39.4036 | 36.9578 | 35.0182 | 32.8955 | 30.5403 | 28.0811 | 10.2465 | 1.6302 | -1.9344
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | System Transformation | Thermal headroom (MW) | 45.2133 | 45.6344 | 45.534 | 45.3312 | 44.9121 | 44.0197 | 43.0459 | 41.9904 | 40.7509 | 39.3507 | 37.0532 | 34.8099 | 32.2893 | 29.9007 | 27.5071 | 9.0964 | -3.2856 | -7.0818
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | WPD Best View | Thermal headroom (MW) | 45.2133 | 45.733 | 45.7273 | 45.6543 | 45.4212 | 44.2882 | 43.1239 | 41.9748 | 40.6954 | 39.0904 | 36.7554 | 34.6862 | 32.401 | 29.8256 | 27.2208 | 9.5391 | 0.029712 | -3.6316
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Consumer Transformation | Thermal headroom (MW) | -1.341 | -1.261 | -1.241 | -1.231 | -1.221 | -1.261 | -1.301 | -1.331 | -1.371 | -1.411 | -1.521 | -1.621 | -1.741 | -1.851 | -1.961 | -3.171 | -3.831 | -4.071
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Leading the Way | Thermal headroom (MW) | -1.341 | -1.331 | -1.371 | -1.411 | -1.471 | -1.611 | -1.751 | -1.881 | -2.021 | -2.171 | -2.291 | -2.421 | -2.561 | -2.701 | -2.831 | -3.511 | -3.751 | -3.841
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Steady Progression | Thermal headroom (MW) | -1.341 | -1.241 | -1.201 | -1.161 | -1.121 | -1.111 | -1.101 | -1.091 | -1.081 | -1.071 | -1.081 | -1.091 | -1.111 | -1.121 | -1.141 | -1.381 | -1.371 | -1.331
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | System Transformation | Thermal headroom (MW) | -1.341 | -1.251 | -1.211 | -1.171 | -1.141 | -1.141 | -1.131 | -1.131 | -1.131 | -1.131 | -1.131 | -1.141 | -1.151 | -1.161 | -1.171 | -1.421 | -1.491 | -1.511
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | WPD Best View | Thermal headroom (MW) | -1.341 | -1.241 | -1.201 | -1.161 | -1.121 | -1.131 | -1.131 | -1.151 | -1.161 | -1.181 | -1.201 | -1.211 | -1.231 | -1.251 | -1.271 | -1.631 | -1.631 | -1.601
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Consumer Transformation | Thermal headroom (MW) | -0.09 | -0.07 | -0.09 | -0.16 | -0.28 | -0.65 | -1.06 | -1.49 | -1.95 | -2.45 | -2.92 | -3.44 | -4.14 | -4.83 | -5.52 | -10.48 | -12.62 | -13.74
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Leading the Way | Thermal headroom (MW) | -0.09 | -0.12 | -0.21 | -0.33 | -0.52 | -1.2 | -1.97 | -2.82 | -3.69 | -4.8 | -5.41 | -6.1 | -6.84 | -7.54 | -8.23 | -11.81 | -13.02 | -13.63
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Steady Progression | Thermal headroom (MW) | -0.09 | 0 | 0.03 | 0.05 | 0.05 | -0.07 | -0.21 | -0.35 | -0.51 | -0.69 | -0.94 | -1.2 | -1.5 | -1.81 | -2.13 | -4.53 | -5.86 | -6.66
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | System Transformation | Thermal headroom (MW) | -0.09 | -0.02 | -0.01 | -0.02 | -0.06 | -0.23 | -0.43 | -0.67 | -0.94 | -1.27 | -1.56 | -1.88 | -2.2 | -2.51 | -2.79 | -5.39 | -7.17 | -7.73
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | WPD Best View | Thermal headroom (MW) | -0.09 | 0 | 0.03 | 0.05 | 0.05 | -0.07 | -0.21 | -0.35 | -0.51 | -0.69 | -0.94 | -1.2 | -1.5 | -1.81 | -2.13 | -4.53 | -5.86 | -6.66
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Consumer Transformation | Thermal headroom (MW) | 10.98 | 10.98 | 10.91 | 10.78 | 10.59 | 10.11 | 9.65 | 9.17 | 8.65 | 8.09 | 7.16 | 6.29 | 5.4 | 4.54 | 3.68 | -2.43 | -5.62 | -7.17
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Leading the Way | Thermal headroom (MW) | 10.98 | 10.73 | 10.39 | 10.03 | 9.58 | 8.67 | 7.79 | 6.84 | 5.87 | 4.82 | 3.83 | 2.88 | 1.94 | 1.06 | 0.2 | -3.87 | -5.52 | -6.5
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Steady Progression | Thermal headroom (MW) | 10.98 | 11.09 | 11.11 | 11.12 | 11.11 | 10.91 | 10.71 | 10.51 | 10.26 | 10.01 | 9.64 | 9.33 | 8.98 | 8.56 | 8.15 | 5.34 | 4.02 | 3.27
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | System Transformation | Thermal headroom (MW) | 10.98 | 11.07 | 11.06 | 11.03 | 10.97 | 10.87 | 10.75 | 10.58 | 10.39 | 10.18 | 9.8 | 9.4 | 9 | 8.6 | 8.16 | 4.79 | 2.93 | 2.3
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | WPD Best View | Thermal headroom (MW) | 10.98 | 11.09 | 11.11 | 11.12 | 11.11 | 10.91 | 10.71 | 10.51 | 10.26 | 10.01 | 9.64 | 9.33 | 8.98 | 8.56 | 8.15 | 5.34 | 4.02 | 3.27
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Consumer Transformation | Thermal headroom (MW) | 8.81 | 8.63 | 8.21 | 7.65 | 6.78 | 5.13 | 3.78 | 2.42 | 1.05 | -0.87 | -5.12 | -9.39 | -13.76 | -18.04 | -22.41 | -39.6 | -53.45 | -61.96
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Leading the Way | Thermal headroom (MW) | 8.81 | 8.38 | 7.69 | 6.88 | 5.54 | 2.71 | 0.62 | -2.13 | -5.7 | -9.63 | -13.15 | -17.04 | -21.09 | -25.02 | -28.81 | -39.7 | -44.7 | -47.5
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Steady Progression | Thermal headroom (MW) | 8.81 | 8.93 | 8.86 | 8.78 | 8.6 | 7.79 | 7.2 | 6.57 | 5.9 | 4.75 | 3.26 | 2.26 | 1.17 | -0.1 | -1.6 | -10.08 | -15.37 | -17.76
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | System Transformation | Thermal headroom (MW) | 8.81 | 8.86 | 8.7 | 8.49 | 8.11 | 7.22 | 6.59 | 5.88 | 5.09 | 4.18 | 2.65 | 1.03 | -0.61 | -2.25 | -3.79 | -13.57 | -18.08 | -19.75
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | WPD Best View | Thermal headroom (MW) | 8.81 | 8.93 | 8.86 | 8.78 | 8.6 | 7.79 | 7.2 | 6.57 | 5.9 | 4.75 | 3.26 | 2.26 | 1.17 | -0.1 | -1.6 | -10.08 | -15.37 | -17.76
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Consumer Transformation | Thermal headroom (MW) | 4.57 | 4.54 | 4.36 | 4.15 | 3.92 | 2.85 | 1.78 | 0.77 | -0.23 | -1.27 | -2.7 | -4.11 | -5.57 | -6.93 | -8.24 | -14.22 | -17.15 | -18.56
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Leading the Way | Thermal headroom (MW) | 4.57 | 4.34 | 3.93 | 3.52 | 3.12 | 1.48 | -0.05 | -1.66 | -3.22 | -4.84 | -5.93 | -7.05 | -8.17 | -9.24 | -10.16 | -14.71 | -16.14 | -16.91
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Steady Progression | Thermal headroom (MW) | 4.57 | 4.59 | 4.48 | 4.38 | 4.28 | 3.69 | 3.15 | 2.63 | 2.05 | 1.5 | 0.63 | -0.16 | -1.02 | -1.92 | -2.85 | -9.01 | -11.34 | -12.35
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | System Transformation | Thermal headroom (MW) | 4.57 | 4.59 | 4.45 | 4.32 | 4.18 | 3.97 | 3.73 | 3.49 | 3.21 | 2.89 | 2.18 | 1.47 | 0.79 | 0.06 | -0.68 | -6.68 | -10.99 | -12.06
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | WPD Best View | Thermal headroom (MW) | 4.57 | 4.57 | 4.44 | 4.3 | 4.16 | 3.77 | 3.4 | 3.03 | 2.65 | 2.24 | 1.42 | 0.64 | -0.12 | -0.95 | -1.76 | -8.04 | -11.38 | -12.24
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Consumer Transformation | Thermal headroom (MW) | 0.344 | 0.304 | 0.204 | 0.054 | -0.156 | -0.526 | -0.846 | -1.146 | -1.446 | -1.756 | -2.206 | -2.896 | -3.606 | -4.276 | -4.946 | -8.706 | -10.796 | -11.826
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Leading the Way | Thermal headroom (MW) | 0.344 | 0.234 | 0.064 | -0.146 | -0.436 | -1.016 | -1.586 | -2.146 | -2.756 | -3.466 | -4.136 | -4.826 | -5.526 | -6.236 | -6.826 | -9.196 | -10.216 | -10.736
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Steady Progression | Thermal headroom (MW) | 0.344 | 0.384 | 0.384 | 0.364 | 0.324 | 0.164 | 0.004 | -0.156 | -0.336 | -0.516 | -0.786 | -1.046 | -1.336 | -1.616 | -1.916 | -4.186 | -5.496 | -5.926
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | System Transformation | Thermal headroom (MW) | 0.344 | 0.364 | 0.334 | 0.284 | 0.184 | 0.064 | -0.076 | -0.236 | -0.416 | -0.606 | -0.896 | -1.206 | -1.516 | -1.826 | -2.116 | -4.156 | -5.756 | -6.236
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | WPD Best View | Thermal headroom (MW) | 0.344 | 0.364 | 0.334 | 0.284 | 0.204 | 0.074 | -0.076 | -0.226 | -0.406 | -0.596 | -0.886 | -1.196 | -1.516 | -1.836 | -2.116 | -4.256 | -5.776 | -6.216
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Consumer Transformation | Thermal headroom (MW) | 15.9687 | 15.985 | 15.3713 | 14.5766 | 13.4479 | 9.7939 | 5.6672 | 1.7923 | -1.2764 | -5.0276 | -13.6618 | -21.9066 | -30.4867 | -38.6996 | -47.1004 | -82.537 | -112.3983 | -131.8982
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Leading the Way | Thermal headroom (MW) | 15.9687 | 15.1498 | 13.6572 | 12.0665 | 9.5216 | 3.0364 | -3.6812 | -10.9241 | -18.3157 | -26.6389 | -33.9306 | -41.3781 | -49.3823 | -57.368 | -64.8841 | -87.3573 | -99.2415 | -107.1642
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Steady Progression | Thermal headroom (MW) | 15.9687 | 16.6608 | 16.7878 | 16.8985 | 16.926 | 15.2072 | 13.5279 | 11.8305 | 10.4242 | 7.5329 | 3.7481 | 1.6312 | -0.71182 | -3.58 | -6.019 | -23.1614 | -32.639 | -35.1528
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | System Transformation | Thermal headroom (MW) | 15.9687 | 16.2748 | 16.0878 | 15.7491 | 15.1338 | 13.1101 | 10.6948 | 8.2554 | 6.3606 | 4.3284 | 0.05645 | -2.5667 | -6.5318 | -9.9061 | -14.1356 | -34.4078 | -47.7437 | -52.7504
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | WPD Best View | Thermal headroom (MW) | 15.9687 | 15.985 | 15.3713 | 14.5766 | 13.4479 | 9.7939 | 5.6672 | 1.7923 | -1.2764 | -5.0276 | -13.6618 | -21.9066 | -30.4867 | -38.6996 | -47.1004 | -82.537 | -112.3983 | -131.8982
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Consumer Transformation | Thermal headroom (MW) | 13.898 | 13.968 | 13.968 | 13.958 | 13.938 | 13.408 | 12.918 | 12.398 | 12.148 | 11.888 | 11.208 | 10.768 | 10.288 | 9.818 | 9.358 | 6.828 | 5.688 | 5.248
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Leading the Way | Thermal headroom (MW) | 13.898 | 13.878 | 13.778 | 13.688 | 13.568 | 12.658 | 11.878 | 11.018 | 10.618 | 10.198 | 9.428 | 8.988 | 8.578 | 8.138 | 7.718 | 6.328 | 5.898 | 5.668
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Steady Progression | Thermal headroom (MW) | 13.898 | 14.008 | 14.048 | 14.088 | 14.128 | 13.768 | 13.508 | 13.198 | 13.038 | 12.868 | 12.618 | 12.398 | 12.138 | 11.878 | 11.618 | 10.148 | 9.768 | 9.768
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | System Transformation | Thermal headroom (MW) | 13.898 | 13.998 | 14.018 | 14.038 | 14.038 | 13.628 | 13.278 | 12.888 | 12.768 | 12.638 | 12.278 | 12.008 | 11.728 | 11.448 | 11.158 | 9.678 | 9.328 | 9.418
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | WPD Best View | Thermal headroom (MW) | 13.898 | 13.968 | 13.968 | 13.958 | 13.938 | 13.408 | 12.918 | 12.398 | 12.148 | 11.888 | 11.208 | 10.768 | 10.288 | 9.818 | 9.358 | 6.828 | 5.688 | 5.248
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Consumer Transformation | Thermal headroom (MW) | 7.808 | 7.818 | 7.688 | 7.508 | 7.258 | 6.378 | 5.398 | 4.328 | 3.488 | 2.438 | 0.758 | -1.332 | -3.482 | -5.212 | -6.882 | -17.012 | -22.892 | -25.352
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Leading the Way | Thermal headroom (MW) | 7.808 | 7.648 | 7.328 | 6.988 | 6.398 | 4.528 | 2.748 | 0.528 | -1.032 | -3.072 | -4.872 | -6.742 | -8.552 | -10.322 | -12.022 | -18.512 | -21.382 | -22.602
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Steady Progression | Thermal headroom (MW) | 7.808 | 7.998 | 8.058 | 8.098 | 8.108 | 7.598 | 7.148 | 6.658 | 6.278 | 5.678 | 5.008 | 4.348 | 3.658 | 2.958 | 2.238 | -3.162 | -6.052 | -7.272
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | System Transformation | Thermal headroom (MW) | 7.808 | 7.948 | 7.958 | 7.928 | 7.868 | 7.278 | 6.668 | 6.008 | 5.508 | 4.748 | 4.028 | 3.248 | 2.438 | 1.278 | 0.078 | -6.062 | -8.662 | -9.252
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | WPD Best View | Thermal headroom (MW) | 7.808 | 7.818 | 7.688 | 7.508 | 7.258 | 6.378 | 5.398 | 4.328 | 3.488 | 2.438 | 0.758 | -1.332 | -3.482 | -5.212 | -6.882 | -17.012 | -22.892 | -25.352
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Consumer Transformation | Thermal headroom (MW) | 8.17 | 8.04 | 7.85 | 7.56 | 7.24 | 6.27 | 5.15 | 4.26 | 3.5 | 2.58 | 0.93 | -0.65 | -2.11 | -3.45 | -4.74 | -10.95 | -14.02 | -15.17
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Leading the Way | Thermal headroom (MW) | 8.17 | 7.82 | 7.39 | 6.92 | 6.34 | 4.85 | 3.2 | 1.8 | 0.65 | -0.63 | -2.42 | -4.09 | -5.68 | -7.05 | -8.26 | -12.01 | -13.1 | -13.08
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Steady Progression | Thermal headroom (MW) | 8.17 | 8.29 | 8.28 | 8.27 | 8.25 | 7.78 | 7.3 | 6.86 | 6.46 | 6.07 | 5.57 | 5 | 4.43 | 3.84 | 3.22 | -1.14 | -3.75 | -4.15
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | System Transformation | Thermal headroom (MW) | 8.17 | 8.24 | 8.18 | 8.12 | 8.02 | 7.42 | 6.62 | 6.07 | 5.69 | 5.18 | 4.46 | 3.72 | 2.99 | 2.22 | 1.39 | -3.32 | -5.06 | -5.04
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | WPD Best View | Thermal headroom (MW) | 8.17 | 8.04 | 7.85 | 7.56 | 7.24 | 6.27 | 5.15 | 4.26 | 3.5 | 2.58 | 0.93 | -0.65 | -2.11 | -3.45 | -4.74 | -10.95 | -14.02 | -15.17
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Consumer Transformation | Thermal headroom (MW) | 7.72 | 7.73 | 7.65 | 7.58 | 7.47 | 7.04 | 6.55 | 6.17 | 5.78 | 5.27 | 3.35 | 1.43 | -0.49 | -2.37 | -4.44 | -9.12 | -17.44 | -24.66
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Leading the Way | Thermal headroom (MW) | 7.72 | 7.66 | 7.52 | 7.38 | 6.98 | 6.24 | 5.43 | 4.54 | 2.67 | 0.66 | -0.04 | -1.19 | -2.75 | -4.4 | -5.99 | -9.11 | -11.98 | -14.8
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Steady Progression | Thermal headroom (MW) | 7.72 | 7.75 | 7.73 | 7.71 | 7.7 | 7.59 | 7.46 | 7.37 | 7.27 | 6.46 | 5.43 | 5.31 | 5.14 | 4.72 | 4.55 | 3.1 | 2.28 | 2.23
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | System Transformation | Thermal headroom (MW) | 7.72 | 7.61 | 7.51 | 7.37 | 7.18 | 7.01 | 6.77 | 6.5 | 6.15 | 5.97 | 4.99 | 4.83 | 3.99 | 3.65 | 2.87 | 0.19 | -3.25 | -5.45
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | WPD Best View | Thermal headroom (MW) | 7.72 | 7.73 | 7.65 | 7.58 | 7.47 | 7.04 | 6.55 | 6.17 | 5.78 | 5.27 | 3.35 | 1.43 | -0.49 | -2.37 | -4.44 | -9.12 | -17.44 | -24.66
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Consumer Transformation | Thermal headroom (MW) | 7.13 | 7.16 | 7.06 | 6.94 | 6.69 | 6.3 | 5.97 | 5.56 | 5.14 | 4.57 | 3.18 | 2.13 | 1.14 | 0.12 | -0.84 | -6.66 | -10.11 | -11.75
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Leading the Way | Thermal headroom (MW) | 7.13 | 6.92 | 6.6 | 6.24 | 5.75 | 5.07 | 4.43 | 3.65 | 2.9 | 1.96 | 0.27 | -0.89 | -2.04 | -3.15 | -4.19 | -7.9 | -9.45 | -10.07
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Steady Progression | Thermal headroom (MW) | 7.13 | 7.3 | 7.38 | 7.46 | 7.52 | 7.43 | 7.36 | 7.26 | 7.12 | 6.94 | 6.64 | 6.36 | 6.04 | 5.72 | 5.4 | 2.99 | 1.32 | 0.76
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | System Transformation | Thermal headroom (MW) | 7.13 | 7.31 | 7.34 | 7.37 | 7.29 | 7.17 | 7.06 | 6.89 | 6.76 | 6.5 | 5.95 | 5.6 | 5.18 | 4.7 | 4.16 | 1.19 | 0.03 | -0.15
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | WPD Best View | Thermal headroom (MW) | 7.13 | 7.16 | 7.06 | 6.94 | 6.69 | 6.3 | 5.97 | 5.56 | 5.14 | 4.57 | 3.18 | 2.13 | 1.14 | 0.12 | -0.84 | -6.66 | -10.11 | -11.75
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Consumer Transformation | Thermal headroom (MW) | 0.26 | 0.24 | 0.15 | 0.03 | -0.13 | -0.37 | -0.78 | -1.14 | -1.42 | -1.74 | -2.14 | -2.52 | -3.09 | -3.71 | -4.33 | -8.14 | -10.41 | -11.55
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Leading the Way | Thermal headroom (MW) | 0.26 | 0.17 | 0 | -0.19 | -0.43 | -0.87 | -1.48 | -2.09 | -2.58 | -3.11 | -3.68 | -4.38 | -5.07 | -5.75 | -6.38 | -8.85 | -9.97 | -10.62
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Steady Progression | Thermal headroom (MW) | 0.26 | 0.32 | 0.33 | 0.33 | 0.32 | 0.21 | 0.04 | -0.13 | -0.3 | -0.48 | -0.74 | -0.99 | -1.26 | -1.55 | -1.84 | -3.67 | -4.84 | -5.27
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | System Transformation | Thermal headroom (MW) | 0.26 | 0.3 | 0.29 | 0.26 | 0.2 | 0.11 | -0.07 | -0.27 | -0.45 | -0.65 | -0.94 | -1.25 | -1.57 | -1.89 | -2.16 | -3.83 | -5.24 | -5.58
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | WPD Best View | Thermal headroom (MW) | 0.26 | 0.24 | 0.15 | 0.03 | -0.13 | -0.37 | -0.78 | -1.14 | -1.42 | -1.74 | -2.14 | -2.52 | -3.09 | -3.71 | -4.33 | -8.14 | -10.41 | -11.55
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Consumer Transformation | Thermal headroom (MW) | 25.921 | 25.4829 | 24.83 | 23.9884 | 22.835 | 21.2359 | 19.5975 | 17.9538 | 16.2286 | 14.3172 | 11.6076 | 8.3063 | 4.5096 | 0.9986 | -2.3924 | -23.2381 | -36.2368 | -42.7054
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Leading the Way | Thermal headroom (MW) | 25.921 | 24.9914 | 23.7856 | 22.4372 | 20.7516 | 18.0421 | 15.2208 | 12.2774 | 9.2474 | 5.8501 | 2.3568 | -1.4945 | -5.3938 | -9.2138 | -12.7206 | -26.8342 | -33.3873 | -36.8045
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Steady Progression | Thermal headroom (MW) | 25.921 | 26.0813 | 26.0552 | 26.0034 | 25.855 | 25.2292 | 24.5328 | 23.7453 | 22.8816 | 21.9037 | 20.6195 | 19.3313 | 17.913 | 16.4185 | 14.9213 | 4.8791 | -1.8881 | -5.1743
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | System Transformation | Thermal headroom (MW) | 25.921 | 25.927 | 25.741 | 25.4951 | 25.081 | 24.5083 | 23.7797 | 22.9468 | 21.9846 | 20.8042 | 19.357 | 17.7632 | 16.1072 | 14.1061 | 12.1967 | 1.3054 | -5.3539 | -7.011
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | WPD Best View | Thermal headroom (MW) | 25.921 | 25.4828 | 24.8301 | 23.9888 | 22.8358 | 21.2372 | 19.5987 | 17.956 | 16.2315 | 14.3208 | 11.612 | 8.3115 | 4.5147 | 1.0036 | -2.3874 | -23.2335 | -36.2325 | -42.7014
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Consumer Transformation | Thermal headroom (MW) | 2.14 | 2.07 | 1.84 | 1.59 | 1.21 | 0.75 | 0.24 | -0.29 | -0.81 | -1.36 | -2.07 | -3.11 | -4.57 | -5.65 | -6.71 | -14.29 | -18.74 | -20.79
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Leading the Way | Thermal headroom (MW) | 2.14 | 1.96 | 1.59 | 1.21 | 0.73 | -0.08 | -0.97 | -1.91 | -2.77 | -3.68 | -4.75 | -5.99 | -7.24 | -8.46 | -9.62 | -14.88 | -17.41 | -18.56
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Steady Progression | Thermal headroom (MW) | 2.14 | 2.24 | 2.22 | 2.21 | 2.15 | 1.96 | 1.74 | 1.49 | 1.22 | 0.9 | 0.47 | 0.03 | -0.45 | -0.94 | -1.43 | -4.87 | -7.41 | -8.91
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | System Transformation | Thermal headroom (MW) | 2.14 | 2.2 | 2.13 | 2.06 | 1.93 | 1.77 | 1.56 | 1.29 | 1 | 0.63 | 0.14 | -0.39 | -0.92 | -1.79 | -2.6 | -6.6 | -9.43 | -10.1
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | WPD Best View | Thermal headroom (MW) | 2.14 | 2.07 | 1.84 | 1.59 | 1.21 | 0.75 | 0.24 | -0.29 | -0.81 | -1.36 | -2.07 | -3.11 | -4.57 | -5.65 | -6.71 | -14.29 | -18.74 | -20.79
Chesterfield 132kV | Annesley (1 & 2) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Consumer Transformation | Thermal headroom (MW) | 5.1 | 4.82 | 4.53 | 4.19 | 3.76 | 3.26 | 2.76 | 2.26 | 1.7 | 1.13 | 0.35 | -0.47 | -1.4 | -2.5 | -3.58 | -10.19 | -14.92 | -17.66
Chesterfield 132kV | Annesley (1 & 2) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Leading the Way | Thermal headroom (MW) | 5.1 | 4.68 | 4.28 | 3.83 | 3.28 | 2.43 | 1.58 | 0.67 | -0.43 | -1.62 | -2.61 | -3.8 | -5.07 | -6.3 | -7.46 | -12.2 | -14.77 | -16.57
Chesterfield 132kV | Annesley (1 & 2) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Steady Progression | Thermal headroom (MW) | 5.1 | 5.03 | 4.95 | 4.88 | 4.78 | 4.56 | 4.33 | 4.07 | 3.79 | 3.48 | 3.09 | 2.7 | 2.29 | 1.86 | 1.45 | -0.83 | -2.23 | -3.25
Chesterfield 132kV | Annesley (1 & 2) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | System Transformation | Thermal headroom (MW) | 5.1 | 4.97 | 4.85 | 4.72 | 4.54 | 4.34 | 4.09 | 3.81 | 3.48 | 3.08 | 2.64 | 2.18 | 1.72 | 1.28 | 0.9 | -1.54 | -3.22 | -3.77
Chesterfield 132kV | Annesley (1 & 2) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | WPD Best View | Thermal headroom (MW) | 5.1 | 4.82 | 4.53 | 4.19 | 3.76 | 3.26 | 2.76 | 2.26 | 1.7 | 1.13 | 0.35 | -0.47 | -1.4 | -2.5 | -3.58 | -10.19 | -14.92 | -17.66
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Consumer Transformation | Thermal headroom (MW) | 18.33 | 18.34 | 18.28 | 18.2 | 18.07 | 17.89 | 17.7 | 17.5 | 17.29 | 17.04 | 16.74 | 16.28 | 15.73 | 15.25 | 14.78 | 11.69 | 10 | 9.17
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Leading the Way | Thermal headroom (MW) | 18.33 | 18.29 | 18.19 | 18.06 | 17.87 | 17.52 | 17.15 | 16.74 | 16.36 | 15.9 | 15.36 | 14.81 | 14.25 | 13.7 | 13.23 | 11.19 | 10.32 | 9.83
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Steady Progression | Thermal headroom (MW) | 18.33 | 18.41 | 18.43 | 18.44 | 18.43 | 18.33 | 18.23 | 18.1 | 17.96 | 17.8 | 17.59 | 17.39 | 17.18 | 16.95 | 16.71 | 15.05 | 13.98 | 13.65
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | System Transformation | Thermal headroom (MW) | 18.33 | 18.39 | 18.4 | 18.38 | 18.33 | 18.27 | 18.19 | 18.09 | 17.96 | 17.81 | 17.6 | 17.38 | 17.16 | 16.93 | 16.73 | 15.08 | 13.79 | 13.45
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | WPD Best View | Thermal headroom (MW) | 18.33 | 18.34 | 18.28 | 18.2 | 18.07 | 17.89 | 17.7 | 17.5 | 17.29 | 17.04 | 16.74 | 16.28 | 15.73 | 15.25 | 14.78 | 11.69 | 10 | 9.17
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Consumer Transformation | Thermal headroom (MW) | 17.46 | 16.6 | 15.76 | 14.68 | 13.37 | 11.24 | 9.05 | 7.1 | 5.06 | 2.69 | -1.05 | -5.22 | -9.42 | -13.19 | -16.86 | -36.8 | -49.73 | -55.99
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Leading the Way | Thermal headroom (MW) | 17.46 | 15.74 | 14 | 12.09 | 9.94 | 6.62 | 3.25 | -0.1 | -3.38 | -7.16 | -11.05 | -15.14 | -19.17 | -23.12 | -26.85 | -39.87 | -45.76 | -48.41
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Steady Progression | Thermal headroom (MW) | 17.46 | 17.24 | 17.06 | 16.84 | 16.6 | 15.76 | 14.87 | 13.86 | 12.82 | 11.67 | 10.31 | 8.93 | 7.43 | 5.8 | 4.13 | -7.41 | -15.57 | -19.43
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | System Transformation | Thermal headroom (MW) | 17.46 | 17.04 | 16.67 | 16.22 | 15.64 | 14.7 | 13.6 | 12.49 | 11.37 | 9.97 | 8.43 | 6.64 | 4.71 | 2.33 | -0.17 | -12.73 | -18.57 | -20.52
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | WPD Best View | Thermal headroom (MW) | 17.46 | 16.6 | 15.76 | 14.68 | 13.38 | 11.24 | 9.06 | 7.11 | 5.07 | 2.7 | -1.03 | -5.2 | -9.4 | -13.17 | -16.84 | -36.79 | -49.71 | -55.98
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Consumer Transformation | Thermal headroom (MW) | 14.07 | 14.2 | 14.29 | 14.38 | 14.42 | 14.47 | 14.52 | 14.52 | 14.53 | 14.53 | 14.5 | 14.47 | 14.45 | 14.39 | 14.38 | 14.47 | 14.76 | 15.08
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Leading the Way | Thermal headroom (MW) | 14.07 | 14.24 | 14.29 | 14.35 | 14.38 | 14.42 | 14.46 | 14.5 | 14.5 | 14.49 | 14.45 | 14.43 | 14.41 | 14.4 | 14.42 | 14.62 | 14.98 | 15.44
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Steady Progression | Thermal headroom (MW) | 14.07 | 14.24 | 14.33 | 14.42 | 14.5 | 14.59 | 14.68 | 14.76 | 14.85 | 14.93 | 14.97 | 15 | 15 | 15 | 15.01 | 14.95 | 15 | 15.26
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | System Transformation | Thermal headroom (MW) | 14.07 | 14.24 | 14.33 | 14.42 | 14.5 | 14.59 | 14.67 | 14.76 | 14.8 | 14.84 | 14.84 | 14.84 | 14.81 | 14.79 | 14.77 | 14.66 | 14.89 | 15.27
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | WPD Best View | Thermal headroom (MW) | 14.07 | 14.2 | 14.29 | 14.38 | 14.42 | 14.47 | 14.52 | 14.52 | 14.53 | 14.53 | 14.5 | 14.47 | 14.45 | 14.39 | 14.38 | 14.47 | 14.76 | 15.08
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Consumer Transformation | Thermal headroom (MW) | 43.2927 | 41.7737 | 40.2252 | 39.1656 | 37.845 | 35.8591 | 33.8513 | 32.0467 | 29.8016 | 27.3241 | 22.0244 | 16.6643 | 11.1287 | 5.4603 | -0.21873 | -26.5612 | -47.9618 | -60.327
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Leading the Way | Thermal headroom (MW) | 43.2927 | 41.2499 | 38.6858 | 37.0293 | 34.9508 | 31.6477 | 28.2072 | 24.4962 | 19.9702 | 15.0442 | 10.2375 | 4.8483 | -0.8 | -6.3542 | -11.5416 | -29.3015 | -38.0847 | -42.8397
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Steady Progression | Thermal headroom (MW) | 43.2927 | 42.7813 | 42.035 | 41.8601 | 41.6306 | 40.7804 | 39.8121 | 38.9646 | 38.0418 | 36.6779 | 34.8166 | 33.4586 | 31.9668 | 30.0311 | 28.2077 | 16.2551 | 7.7899 | 3.4157
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | System Transformation | Thermal headroom (MW) | 43.2927 | 42.5541 | 41.5482 | 41.1369 | 40.5129 | 39.7002 | 38.7255 | 37.9191 | 36.8928 | 35.6725 | 33.7995 | 31.7722 | 29.4694 | 27.1505 | 24.8844 | 10.9847 | 4.1206 | 2.0884
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | WPD Best View | Thermal headroom (MW) | 43.2927 | 41.7737 | 40.2252 | 39.1656 | 37.845 | 35.8591 | 33.8513 | 32.0467 | 29.8016 | 27.3241 | 22.0244 | 16.6643 | 11.1287 | 5.4603 | -0.21873 | -26.5612 | -47.9618 | -60.327
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Consumer Transformation | Thermal headroom (MW) | 9.958 | 9.968 | 9.768 | 9.438 | 8.918 | 8.088 | 6.968 | 6.038 | 5.068 | 3.948 | 0.168 | -3.672 | -7.542 | -11.382 | -15.212 | -33.032 | -46.932 | -54.942
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Leading the Way | Thermal headroom (MW) | 9.958 | 9.668 | 9.138 | 8.518 | 7.438 | 5.518 | 3.288 | 0.998 | -1.602 | -4.522 | -7.852 | -11.452 | -15.202 | -18.932 | -22.422 | -33.742 | -39.522 | -42.512
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Steady Progression | Thermal headroom (MW) | 9.958 | 10.298 | 10.418 | 10.498 | 10.528 | 10.218 | 9.768 | 9.428 | 9.028 | 8.258 | 7.098 | 6.268 | 5.368 | 4.338 | 3.368 | -4.832 | -10.722 | -13.402
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | System Transformation | Thermal headroom (MW) | 9.958 | 10.208 | 10.218 | 10.168 | 10.018 | 9.718 | 9.138 | 8.748 | 8.198 | 7.488 | 6.418 | 5.278 | 3.718 | 2.188 | 0.778 | -8.892 | -13.452 | -15.272
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | WPD Best View | Thermal headroom (MW) | 9.958 | 9.968 | 9.768 | 9.438 | 8.918 | 8.088 | 6.968 | 6.038 | 5.068 | 3.948 | 0.168 | -3.672 | -7.542 | -11.382 | -15.212 | -33.032 | -46.932 | -54.942
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Consumer Transformation | Thermal headroom (MW) | 9.22 | 7.21 | 5.4 | 4.6 | 3.76 | 2.38 | 1.01 | -0.15 | -1.83 | -3.67 | -7.64 | -11.61 | -15.62 | -19.57 | -23.58 | -38.38 | -52.96 | -61.86
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Leading the Way | Thermal headroom (MW) | 9.22 | 6.96 | 4.15 | 2.91 | 1.59 | -0.32 | -2.41 | -4.78 | -7.88 | -11.14 | -14.18 | -17.58 | -21.19 | -24.73 | -28.04 | -37.82 | -42.53 | -44.81
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Steady Progression | Thermal headroom (MW) | 9.22 | 8.13 | 6.89 | 6.61 | 6.34 | 5.7 | 4.93 | 4.32 | 3.67 | 2.61 | 1.22 | 0.45 | -0.44 | -1.9 | -3.21 | -11.05 | -16.93 | -19.75
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | System Transformation | Thermal headroom (MW) | 9.22 | 7.95 | 6.49 | 6.04 | 5.51 | 4.92 | 4.23 | 3.74 | 3.1 | 2.45 | 1.15 | -0.25 | -1.8 | -3.44 | -5.14 | -14.5 | -18.57 | -19.61
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | WPD Best View | Thermal headroom (MW) | 9.22 | 7.21 | 5.4 | 4.6 | 3.76 | 2.38 | 1.01 | -0.15 | -1.83 | -3.67 | -7.64 | -11.61 | -15.62 | -19.57 | -23.58 | -38.38 | -52.96 | -61.86
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Consumer Transformation | Thermal headroom (MW) | 10.746 | 10.826 | 10.746 | 10.616 | 10.346 | 9.716 | 9.276 | 8.876 | 8.356 | 7.696 | 6.386 | 5.086 | 3.736 | 2.456 | 1.166 | -6.084 | -10.344 | -12.084
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Leading the Way | Thermal headroom (MW) | 10.746 | 10.576 | 10.146 | 9.766 | 9.216 | 8.116 | 7.316 | 6.456 | 5.526 | 4.406 | 3.086 | 1.656 | 0.286 | -1.074 | -2.334 | -7.374 | -9.224 | -9.564
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Steady Progression | Thermal headroom (MW) | 10.746 | 11.046 | 11.176 | 11.306 | 11.406 | 11.166 | 11.056 | 10.926 | 10.796 | 10.646 | 10.366 | 10.046 | 9.726 | 9.316 | 8.876 | 5.366 | 2.826 | 1.686
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | System Transformation | Thermal headroom (MW) | 10.746 | 10.996 | 11.076 | 11.136 | 11.046 | 10.776 | 10.666 | 10.586 | 10.476 | 10.236 | 9.826 | 9.346 | 8.756 | 8.186 | 7.566 | 3.366 | 1.616 | 1.436
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | WPD Best View | Thermal headroom (MW) | 10.746 | 10.826 | 10.746 | 10.616 | 10.346 | 9.716 | 9.276 | 8.876 | 8.356 | 7.696 | 6.386 | 5.086 | 3.736 | 2.456 | 1.166 | -6.084 | -10.344 | -12.084
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Consumer Transformation | Thermal headroom (MW) | 2.22 | 2.22 | 2.18 | 2.12 | 1.89 | 1.55 | 1.15 | 0.84 | 0.44 | 0.05 | -0.57 | -1.18 | -1.84 | -2.46 | -3.06 | -6.02 | -7.66 | -8.4
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Leading the Way | Thermal headroom (MW) | 2.22 | 2.16 | 2.08 | 1.98 | 1.59 | 0.91 | 0.21 | -0.39 | -1.03 | -1.62 | -2.22 | -2.83 | -3.42 | -4.04 | -4.61 | -6.52 | -7.26 | -7.57
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Steady Progression | Thermal headroom (MW) | 2.22 | 2.27 | 2.28 | 2.29 | 2.16 | 1.96 | 1.78 | 1.62 | 1.43 | 1.26 | 1.03 | 0.82 | 0.57 | 0.31 | 0.03 | -2.15 | -3.42 | -3.79
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | System Transformation | Thermal headroom (MW) | 2.22 | 2.26 | 2.25 | 2.24 | 2.07 | 1.85 | 1.62 | 1.46 | 1.29 | 1.13 | 0.88 | 0.6 | 0.32 | 0.04 | -0.32 | -2.51 | -3.69 | -3.92
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | WPD Best View | Thermal headroom (MW) | 2.22 | 2.22 | 2.18 | 2.12 | 1.89 | 1.55 | 1.15 | 0.84 | 0.44 | 0.05 | -0.57 | -1.18 | -1.84 | -2.46 | -3.06 | -6.02 | -7.66 | -8.4
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Consumer Transformation | Thermal headroom (MW) | 11.42 | 11.16 | 10.86 | 10.48 | 9.91 | 9.16 | 8.24 | 7.42 | 6.45 | 5.43 | 3.51 | 1.42 | -0.61 | -2.51 | -4.33 | -15.03 | -21.95 | -26.23
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Leading the Way | Thermal headroom (MW) | 11.42 | 10.97 | 10.48 | 9.94 | 9.15 | 7.72 | 6.16 | 4.64 | 2.74 | 0.68 | -1.52 | -3.75 | -5.89 | -8.01 | -9.88 | -16.93 | -20.83 | -23.68
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Steady Progression | Thermal headroom (MW) | 11.42 | 11.37 | 11.32 | 11.24 | 11.13 | 10.86 | 10.51 | 10.2 | 9.84 | 9.46 | 8.87 | 8.27 | 7.66 | 7.04 | 6.41 | 1.3 | -2.64 | -3.98
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | System Transformation | Thermal headroom (MW) | 11.42 | 11.29 | 11.16 | 11.01 | 10.77 | 10.49 | 10.05 | 9.66 | 9.04 | 8.44 | 7.6 | 6.77 | 5.97 | 5.19 | 4.48 | -1.24 | -5.32 | -6.91
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | WPD Best View | Thermal headroom (MW) | 11.42 | 11.16 | 10.86 | 10.48 | 9.91 | 9.16 | 8.24 | 7.42 | 6.45 | 5.43 | 3.51 | 1.42 | -0.61 | -2.51 | -4.33 | -15.03 | -21.95 | -26.23
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Consumer Transformation | Thermal headroom (MW) | 3.31 | 3.22 | 3.09 | 2.88 | 2.61 | 2.23 | 1.63 | 1.07 | 0.45 | -0.27 | -1.43 | -2.62 | -3.82 | -4.95 | -6.07 | -12.58 | -15.67 | -17.09
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Leading the Way | Thermal headroom (MW) | 3.31 | 3.01 | 2.65 | 2.3 | 1.81 | 1.09 | 0.19 | -0.77 | -1.78 | -2.9 | -4.15 | -5.49 | -6.77 | -7.99 | -9.11 | -13.41 | -14.67 | -14.99
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Steady Progression | Thermal headroom (MW) | 3.31 | 3.34 | 3.33 | 3.26 | 3.17 | 2.99 | 2.76 | 2.55 | 2.34 | 2.08 | 1.77 | 1.36 | 0.94 | 0.45 | -0.06 | -3.45 | -5.57 | -6.57
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | System Transformation | Thermal headroom (MW) | 3.31 | 3.32 | 3.22 | 3.12 | 2.93 | 2.8 | 2.58 | 2.35 | 2.1 | 1.73 | 1.26 | 0.68 | 0.05 | -0.56 | -1.23 | -5.45 | -7.11 | -7.28
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | WPD Best View | Thermal headroom (MW) | 3.31 | 3.22 | 3.09 | 2.88 | 2.61 | 2.23 | 1.63 | 1.07 | 0.45 | -0.27 | -1.43 | -2.62 | -3.82 | -4.95 | -6.07 | -12.58 | -15.67 | -17.09
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Consumer Transformation | Thermal headroom (MW) | 4.45 | 4.32 | 4 | 3.57 | 2.74 | 1.49 | -0.35 | -2.07 | -3.77 | -6.04 | -10.39 | -14.96 | -19.63 | -24.3 | -29.07 | -52.97 | -72.23 | -84.66
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Leading the Way | Thermal headroom (MW) | 4.45 | 4 | 3.3 | 2.29 | 0.58 | -2.09 | -5.24 | -8.7 | -12.86 | -17.3 | -21.6 | -25.99 | -30.55 | -35.14 | -39.44 | -55.22 | -64.39 | -71.09
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Steady Progression | Thermal headroom (MW) | 4.45 | 4.67 | 4.7 | 4.69 | 4.45 | 3.97 | 3.28 | 2.63 | 1.85 | 0.6 | -1.1 | -2.27 | -3.53 | -4.96 | -6.59 | -15.51 | -21.92 | -24.93
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | System Transformation | Thermal headroom (MW) | 4.45 | 4.59 | 4.51 | 4.37 | 3.94 | 3.52 | 2.73 | 1.83 | 0.77 | -0.33 | -2.21 | -4.07 | -5.94 | -7.77 | -9.47 | -19.85 | -26.57 | -29.88
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | WPD Best View | Thermal headroom (MW) | 4.45 | 4.32 | 4 | 3.57 | 2.74 | 1.49 | -0.35 | -2.07 | -3.77 | -6.04 | -10.39 | -14.96 | -19.63 | -24.3 | -29.07 | -52.97 | -72.23 | -84.66
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Consumer Transformation | Thermal headroom (MW) | 10.756 | 9.656 | 9.236 | 8.706 | 7.926 | 6.876 | 5.816 | 4.526 | 3.066 | 0.916 | -2.834 | -6.674 | -10.424 | -14.054 | -17.744 | -30.604 | -41.304 | -47.964
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Leading the Way | Thermal headroom (MW) | 10.756 | 9.286 | 8.566 | 7.766 | 6.566 | 5.086 | 3.486 | 1.486 | -1.524 | -4.894 | -7.954 | -11.254 | -14.654 | -17.964 | -20.944 | -28.534 | -31.554 | -31.904
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Steady Progression | Thermal headroom (MW) | 10.756 | 10.156 | 10.046 | 9.926 | 9.746 | 9.386 | 8.856 | 8.326 | 7.846 | 6.846 | 5.516 | 4.726 | 3.756 | 2.586 | 1.116 | -7.304 | -13.334 | -15.444
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | System Transformation | Thermal headroom (MW) | 10.756 | 9.966 | 9.756 | 9.476 | 9.076 | 8.636 | 8.216 | 7.656 | 6.916 | 6.096 | 4.616 | 3.016 | 1.206 | -0.744 | -2.804 | -12.834 | -16.404 | -16.444
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | WPD Best View | Thermal headroom (MW) | 10.756 | 9.656 | 9.236 | 8.706 | 7.926 | 6.876 | 5.816 | 4.526 | 3.066 | 0.916 | -2.834 | -6.674 | -10.424 | -14.054 | -17.744 | -30.604 | -41.304 | -47.964
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Consumer Transformation | Thermal headroom (MW) | 38.3427 | 36.3787 | 33.9042 | 31.511 | 28.3141 | 23.9036 | 19.9067 | 14.279 | 9.6538 | 4.829 | -4.1252 | -13.483 | -23.0384 | -32.0735 | -41.0783 | -89.3926 | -120.8336 | -137.1065
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Leading the Way | Thermal headroom (MW) | 38.3427 | 34.4465 | 30.0911 | 26.0268 | 20.9677 | 13.6629 | 6.8145 | -3.3186 | -12.575 | -22.3586 | -31.6278 | -41.9333 | -52.2626 | -62.2521 | -71.704 | -105.2665 | -122.7617 | -133.8493
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Steady Progression | Thermal headroom (MW) | 38.3427 | 37.7141 | 36.7144 | 35.9952 | 35.008 | 33.1515 | 31.3468 | 28.5055 | 26.3422 | 23.662 | 20.0261 | 17.0904 | 13.8844 | 10.4724 | 7.2647 | -15.2819 | -28.3809 | -33.2134
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | System Transformation | Thermal headroom (MW) | 38.3427 | 37.1241 | 35.6155 | 34.3202 | 32.5387 | 30.9261 | 29.3532 | 25.8535 | 23.3351 | 20.9399 | 16.66 | 13.0514 | 8.307 | 3.5032 | -1.9213 | -29.9302 | -44.717 | -50.552
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | WPD Best View | Thermal headroom (MW) | 38.3427 | 36.3787 | 33.9042 | 31.511 | 28.3141 | 23.9036 | 19.9067 | 14.279 | 9.6538 | 4.829 | -4.1252 | -13.483 | -23.0384 | -32.0735 | -41.0783 | -89.3926 | -120.8336 | -137.1065
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Consumer Transformation | Thermal headroom (MW) | 9.41 | 9.48 | 9.46 | 9.36 | 9.19 | 8.9 | 8.64 | 8.41 | 8.23 | 8.04 | 7.68 | 7.32 | 6.96 | 6.59 | 6.24 | 4.41 | 3.58 | 3.35
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Leading the Way | Thermal headroom (MW) | 9.41 | 9.42 | 9.3 | 9.12 | 8.86 | 8.38 | 7.98 | 7.6 | 7.27 | 6.87 | 6.55 | 6.23 | 5.91 | 5.61 | 5.34 | 4.28 | 4 | 4.02
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Steady Progression | Thermal headroom (MW) | 9.41 | 9.52 | 9.53 | 9.52 | 9.51 | 9.42 | 9.34 | 9.28 | 9.23 | 9.18 | 9.03 | 8.9 | 8.73 | 8.56 | 8.4 | 7.36 | 7.12 | 7.15
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | System Transformation | Thermal headroom (MW) | 9.41 | 9.51 | 9.51 | 9.49 | 9.44 | 9.41 | 9.39 | 9.34 | 9.31 | 9.27 | 9.13 | 9 | 8.83 | 8.67 | 8.52 | 7.54 | 7.11 | 7.11
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | WPD Best View | Thermal headroom (MW) | 9.41 | 9.48 | 9.46 | 9.36 | 9.19 | 8.9 | 8.64 | 8.41 | 8.23 | 8.04 | 7.68 | 7.32 | 6.96 | 6.59 | 6.24 | 4.41 | 3.58 | 3.35
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Consumer Transformation | Thermal headroom (MW) | 3.738 | 3.758 | 3.768 | 3.778 | 3.768 | 3.738 | 3.718 | 3.688 | 3.648 | 3.608 | 3.518 | 3.448 | 3.318 | 3.188 | 3.068 | 2.438 | 2.078 | 1.898
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Leading the Way | Thermal headroom (MW) | 3.738 | 3.748 | 3.748 | 3.738 | 3.698 | 3.628 | 3.538 | 3.418 | 3.148 | 2.868 | 2.728 | 2.498 | 2.208 | 1.928 | 1.658 | 0.868 | 0.228 | -0.352
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Steady Progression | Thermal headroom (MW) | 3.738 | 3.768 | 3.788 | 3.798 | 3.818 | 3.808 | 3.798 | 3.788 | 3.778 | 3.678 | 3.558 | 3.528 | 3.488 | 3.428 | 3.388 | 3.028 | 2.728 | 2.638
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | System Transformation | Thermal headroom (MW) | 3.738 | 3.738 | 3.738 | 3.728 | 3.708 | 3.688 | 3.658 | 3.608 | 3.558 | 3.518 | 3.298 | 3.258 | 3.068 | 2.988 | 2.818 | 2.118 | 1.358 | 0.948
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | WPD Best View | Thermal headroom (MW) | 3.738 | 3.758 | 3.768 | 3.778 | 3.768 | 3.738 | 3.718 | 3.688 | 3.648 | 3.608 | 3.518 | 3.448 | 3.318 | 3.188 | 3.068 | 2.438 | 2.078 | 1.898
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Consumer Transformation | Thermal headroom (MW) | 16.45 | 16.34 | 16.18 | 16.03 | 15.77 | 15.42 | 15.12 | 14.84 | 14.5 | 14.04 | 13.3 | 12.56 | 11.85 | 11.14 | 10.46 | 6.62 | 4.3 | 3.26
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Leading the Way | Thermal headroom (MW) | 16.45 | 16.16 | 15.82 | 15.52 | 15.09 | 14.5 | 13.98 | 13.4 | 12.83 | 12.08 | 11.27 | 10.43 | 9.72 | 8.97 | 8.26 | 5.63 | 4.47 | 3.82
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Steady Progression | Thermal headroom (MW) | 16.45 | 16.45 | 16.41 | 16.39 | 16.29 | 16.12 | 15.97 | 15.82 | 15.66 | 15.49 | 15.23 | 14.99 | 14.73 | 14.47 | 14.21 | 12.47 | 11.53 | 11.12
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | System Transformation | Thermal headroom (MW) | 16.45 | 16.42 | 16.35 | 16.29 | 16.13 | 15.98 | 15.85 | 15.7 | 15.54 | 15.35 | 15.03 | 14.71 | 14.41 | 14.04 | 13.67 | 11.71 | 10.91 | 10.55
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | WPD Best View | Thermal headroom (MW) | 16.45 | 16.34 | 16.18 | 16.03 | 15.77 | 15.42 | 15.12 | 14.84 | 14.5 | 14.04 | 13.3 | 12.56 | 11.85 | 11.14 | 10.46 | 6.62 | 4.3 | 3.26
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Consumer Transformation | Thermal headroom (MW) | 9.29 | 9.15 | 8.87 | 8.5 | 8.05 | 7.28 | 6.49 | 5.74 | 5.01 | 4.06 | 2.45 | 0.45 | -1.52 | -3.09 | -4.64 | -14.51 | -20.99 | -23.97
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Leading the Way | Thermal headroom (MW) | 9.29 | 8.73 | 8.04 | 7.3 | 6.43 | 5.12 | 3.76 | 2.32 | 1 | -0.63 | -2.41 | -4.26 | -6.01 | -7.72 | -9.38 | -16.18 | -19.81 | -21.71
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Steady Progression | Thermal headroom (MW) | 9.29 | 9.41 | 9.41 | 9.39 | 9.36 | 9.12 | 8.8 | 8.47 | 8.17 | 7.81 | 7.28 | 6.77 | 6.21 | 5.64 | 5.08 | 0.75 | -2.45 | -3.99
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | System Transformation | Thermal headroom (MW) | 9.29 | 9.34 | 9.27 | 9.17 | 9.03 | 8.78 | 8.49 | 8.16 | 7.81 | 7.37 | 6.8 | 6.19 | 5.44 | 4.34 | 3.31 | -2.36 | -5.17 | -6.03
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | WPD Best View | Thermal headroom (MW) | 9.29 | 9.15 | 8.87 | 8.5 | 8.05 | 7.28 | 6.49 | 5.74 | 5.01 | 4.06 | 2.45 | 0.45 | -1.52 | -3.09 | -4.64 | -14.51 | -20.99 | -23.97
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Consumer Transformation | Thermal headroom (MW) | 8.92 | 8.61 | 8.16 | 7.75 | 7.23 | 6.34 | 5.5 | 4.7 | 3.86 | 2.83 | 0.18 | -2.45 | -5.13 | -7.72 | -10.39 | -20.08 | -29.97 | -36.85
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Leading the Way | Thermal headroom (MW) | 8.92 | 8.36 | 7.63 | 6.98 | 6.17 | 4.75 | 3.41 | 1.95 | 0.02 | -2.17 | -4.14 | -6.41 | -8.84 | -11.26 | -13.54 | -20.26 | -24.85 | -28.17
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Steady Progression | Thermal headroom (MW) | 8.92 | 8.82 | 8.6 | 8.43 | 8.28 | 7.94 | 7.64 | 7.26 | 6.9 | 6.26 | 5.43 | 4.92 | 4.37 | 3.69 | 3.09 | -1.49 | -4.22 | -5.26
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | System Transformation | Thermal headroom (MW) | 8.92 | 8.79 | 8.52 | 8.31 | 8.05 | 7.8 | 7.55 | 7.26 | 6.89 | 6.5 | 5.95 | 5.31 | 4.24 | 3.16 | 2.02 | -3.63 | -6.7 | -8.15
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | WPD Best View | Thermal headroom (MW) | 8.92 | 8.61 | 8.16 | 7.75 | 7.23 | 6.34 | 5.5 | 4.7 | 3.86 | 2.83 | 0.18 | -2.45 | -5.13 | -7.72 | -10.39 | -20.08 | -29.97 | -36.85
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Consumer Transformation | Thermal headroom (MW) | 5.76 | 5.82 | 5.79 | 5.72 | 5.59 | 5.39 | 5.08 | 4.83 | 4.6 | 4.36 | 3.96 | 3.08 | 2.21 | 1.4 | 0.62 | -3.48 | -5.62 | -6.41
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Leading the Way | Thermal headroom (MW) | 5.76 | 5.73 | 5.61 | 5.47 | 5.24 | 4.92 | 4.37 | 3.82 | 3.35 | 2.66 | 1.8 | 0.86 | -0.1 | -0.93 | -1.65 | -4.18 | -4.86 | -4.78
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Steady Progression | Thermal headroom (MW) | 5.76 | 5.92 | 5.98 | 6.04 | 6.07 | 6.03 | 5.93 | 5.84 | 5.76 | 5.66 | 5.5 | 5.32 | 5.13 | 4.94 | 4.75 | 2.65 | 1 | 0.68
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | System Transformation | Thermal headroom (MW) | 5.76 | 5.89 | 5.93 | 5.96 | 5.95 | 5.93 | 5.78 | 5.65 | 5.53 | 5.4 | 5.17 | 4.92 | 4.68 | 4.41 | 4.18 | 1.6 | 0.44 | 0.41
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | WPD Best View | Thermal headroom (MW) | 5.76 | 5.82 | 5.79 | 5.72 | 5.59 | 5.39 | 5.08 | 4.83 | 4.6 | 4.36 | 3.96 | 3.08 | 2.21 | 1.4 | 0.62 | -3.48 | -5.62 | -6.41
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Consumer Transformation | Thermal headroom (MW) | 16.97 | 16.26 | 15.77 | 15.26 | 14.67 | 14.18 | 13.71 | 13.22 | 12.7 | 12.23 | 11.58 | 10.93 | 10.31 | 9.73 | 9.14 | 5.63 | 3.77 | 2.83
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Leading the Way | Thermal headroom (MW) | 16.97 | 16.04 | 15.39 | 14.72 | 13.99 | 13.28 | 12.63 | 11.93 | 11.12 | 10.4 | 9.75 | 9.05 | 8.4 | 7.78 | 7.23 | 5.09 | 4.19 | 3.72
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Steady Progression | Thermal headroom (MW) | 16.97 | 16.46 | 16.16 | 15.87 | 15.56 | 15.28 | 15.02 | 14.78 | 14.57 | 14.4 | 14.19 | 13.96 | 13.69 | 13.44 | 13.2 | 11.66 | 10.89 | 10.7
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | System Transformation | Thermal headroom (MW) | 16.97 | 16.36 | 15.99 | 15.63 | 15.23 | 14.98 | 14.76 | 14.54 | 14.31 | 14.08 | 13.79 | 13.46 | 13.15 | 12.81 | 12.48 | 10.77 | 10.13 | 9.97
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | WPD Best View | Thermal headroom (MW) | 16.97 | 16.26 | 15.77 | 15.26 | 14.67 | 14.18 | 13.71 | 13.22 | 12.7 | 12.23 | 11.58 | 10.93 | 10.31 | 9.73 | 9.14 | 5.63 | 3.77 | 2.83
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Consumer Transformation | Thermal headroom (MW) | 18.65 | 18.56 | 18.34 | 18.2 | 18.04 | 17.72 | 17.5 | 16.67 | 16.25 | 15.94 | 15.33 | 14.73 | 14.13 | 13.53 | 12.93 | 9.09 | 6.9 | 5.89
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Leading the Way | Thermal headroom (MW) | 18.65 | 18.41 | 18.02 | 17.75 | 17.46 | 16.92 | 16.48 | 15.07 | 14.38 | 13.84 | 13.18 | 12.51 | 11.83 | 11.2 | 10.59 | 8.21 | 7.19 | 6.6
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Steady Progression | Thermal headroom (MW) | 18.65 | 18.64 | 18.54 | 18.5 | 18.46 | 18.33 | 18.22 | 17.75 | 17.49 | 17.29 | 17.03 | 16.74 | 16.46 | 16.18 | 15.9 | 14.15 | 13.33 | 12.98
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | System Transformation | Thermal headroom (MW) | 18.65 | 18.62 | 18.48 | 18.41 | 18.34 | 18.25 | 18.17 | 17.48 | 17.21 | 17 | 16.73 | 16.44 | 16.15 | 15.82 | 15.43 | 13.4 | 12.63 | 12.36
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | WPD Best View | Thermal headroom (MW) | 18.65 | 18.56 | 18.34 | 18.2 | 18.04 | 17.72 | 17.5 | 16.67 | 16.25 | 15.94 | 15.33 | 14.73 | 14.13 | 13.53 | 12.93 | 9.09 | 6.9 | 5.89
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Consumer Transformation | Thermal headroom (MW) | 66.864 | 65.7371 | 64.749 | 63.3495 | 60.9183 | 57.9502 | 54.9336 | 51.5471 | 47.8321 | 43.3458 | 35.9886 | 27.3196 | 18.5313 | 10.5542 | 2.6594 | -36.8112 | -64.0418 | -78.8139
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Leading the Way | Thermal headroom (MW) | 66.864 | 64.7606 | 62.778 | 60.256 | 56.3585 | 51.4803 | 46.5842 | 40.7801 | 33.9855 | 26.5891 | 18.8897 | 10.1457 | 1.7189 | -6.5103 | -13.9763 | -39.632 | -51.4816 | -56.7284
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Steady Progression | Thermal headroom (MW) | 66.864 | 66.824 | 66.7964 | 66.585 | 65.8819 | 64.8436 | 63.6535 | 62.1888 | 60.559 | 58.3428 | 55.4569 | 52.8081 | 50.09 | 47.1145 | 43.8439 | 22.6284 | 7.1949 | 1.1302
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | System Transformation | Thermal headroom (MW) | 66.864 | 66.492 | 66.2199 | 65.6338 | 64.3338 | 63.2395 | 62.0121 | 60.329 | 58.3108 | 56.0359 | 52.7451 | 48.9321 | 45.229 | 40.8056 | 36.3778 | 13.0051 | 0.47778 | -2.267
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | WPD Best View | Thermal headroom (MW) | 66.864 | 65.7371 | 64.749 | 63.3495 | 60.9183 | 57.9502 | 54.9336 | 51.5471 | 47.8321 | 43.3458 | 35.9886 | 27.3196 | 18.5313 | 10.5542 | 2.6594 | -36.8112 | -64.0418 | -78.8139
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Consumer Transformation | Thermal headroom (MW) | 4.1 | 3.99 | 3.82 | 3.62 | 3.29 | 2.76 | 2.21 | 1.66 | 1.02 | 0.21 | -0.97 | -2.54 | -4.15 | -5.3 | -6.42 | -12.58 | -16.14 | -17.72
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Leading the Way | Thermal headroom (MW) | 4.1 | 3.83 | 3.45 | 3.08 | 2.54 | 1.73 | 0.87 | -0.08 | -1.12 | -2.21 | -3.43 | -4.74 | -6.03 | -7.27 | -8.41 | -12.41 | -14.04 | -14.26
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Steady Progression | Thermal headroom (MW) | 4.1 | 4.15 | 4.11 | 4.06 | 3.99 | 3.82 | 3.64 | 3.4 | 3.11 | 2.81 | 2.36 | 1.92 | 1.44 | 0.92 | 0.33 | -4.03 | -7.02 | -8.2
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | System Transformation | Thermal headroom (MW) | 4.1 | 4.12 | 4.05 | 3.96 | 3.77 | 3.58 | 3.36 | 3.12 | 2.78 | 2.39 | 1.86 | 1.28 | 0.61 | -0.49 | -1.64 | -6.64 | -8.96 | -9.11
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | WPD Best View | Thermal headroom (MW) | 4.1 | 3.99 | 3.82 | 3.62 | 3.29 | 2.76 | 2.21 | 1.66 | 1.02 | 0.21 | -0.97 | -2.54 | -4.15 | -5.3 | -6.42 | -12.58 | -16.14 | -17.72
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Consumer Transformation | Thermal headroom (MW) | 7.76 | 7.57 | 7.2 | 6.77 | 6 | 4.92 | 3.79 | 2.59 | 1.32 | -0.04 | -1.89 | -4.82 | -7.59 | -10.34 | -13.01 | -29.33 | -39.58 | -44.82
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Leading the Way | Thermal headroom (MW) | 7.76 | 7.26 | 6.53 | 5.56 | 4.25 | 2.22 | 0.26 | -1.87 | -4.12 | -6.78 | -9.64 | -13.15 | -16.3 | -19.33 | -22.14 | -33.09 | -38.43 | -41.53
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Steady Progression | Thermal headroom (MW) | 7.76 | 7.93 | 7.94 | 7.93 | 7.84 | 7.42 | 6.93 | 6.32 | 5.62 | 4.85 | 3.87 | 2.71 | 1.6 | 0.44 | -0.71 | -7.01 | -11.47 | -14.1
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | System Transformation | Thermal headroom (MW) | 7.76 | 7.84 | 7.74 | 7.61 | 7.35 | 6.96 | 6.39 | 5.68 | 4.85 | 3.87 | 2.67 | 1.19 | -0.13 | -1.39 | -2.75 | -9.48 | -13.51 | -15.13
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | WPD Best View | Thermal headroom (MW) | 7.76 | 7.57 | 7.2 | 6.77 | 6 | 4.92 | 3.79 | 2.59 | 1.32 | -0.04 | -1.89 | -4.82 | -7.59 | -10.34 | -13.01 | -29.33 | -39.58 | -44.82
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Consumer Transformation | Thermal headroom (MW) | 15.702 | 15.732 | 15.632 | 15.482 | 15.102 | 14.542 | 13.972 | 13.342 | 12.702 | 11.852 | 10.562 | 9.212 | 7.892 | 6.652 | 5.512 | 1.462 | -0.468 | -1.028
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Leading the Way | Thermal headroom (MW) | 15.702 | 15.522 | 15.232 | 14.912 | 14.342 | 13.582 | 12.812 | 11.882 | 10.912 | 9.782 | 8.442 | 7.042 | 5.622 | 4.382 | 3.332 | 0.872 | 0.892 | 1.822
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Steady Progression | Thermal headroom (MW) | 15.702 | 15.932 | 16.032 | 16.132 | 16.082 | 16.002 | 15.912 | 15.752 | 15.552 | 15.302 | 14.992 | 14.622 | 14.182 | 13.722 | 13.202 | 9.762 | 7.752 | 7.622
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | System Transformation | Thermal headroom (MW) | 15.702 | 15.902 | 15.962 | 16.002 | 15.872 | 15.712 | 15.552 | 15.322 | 15.062 | 14.742 | 14.252 | 13.672 | 12.962 | 12.192 | 11.402 | 7.842 | 7.462 | 8.092
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | WPD Best View | Thermal headroom (MW) | 15.702 | 15.732 | 15.632 | 15.482 | 15.102 | 14.542 | 13.972 | 13.342 | 12.702 | 11.852 | 10.562 | 9.212 | 7.892 | 6.652 | 5.512 | 1.462 | -0.468 | -1.028
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Consumer Transformation | Thermal headroom (MW) | 2.91 | 2.92 | 2.89 | 2.85 | 2.78 | 2.68 | 2.58 | 2.47 | 2.35 | 2.2 | 2.03 | 1.87 | 1.61 | 1.35 | 1.1 | -0.67 | -1.71 | -2.23
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Leading the Way | Thermal headroom (MW) | 2.91 | 2.89 | 2.83 | 2.75 | 2.64 | 2.46 | 2.28 | 2.06 | 1.83 | 1.59 | 1.36 | 1.05 | 0.75 | 0.45 | 0.18 | -0.95 | -1.45 | -1.7
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Steady Progression | Thermal headroom (MW) | 2.91 | 2.96 | 2.97 | 2.98 | 2.98 | 2.94 | 2.89 | 2.84 | 2.77 | 2.7 | 2.59 | 2.48 | 2.36 | 2.23 | 2.1 | 1.07 | 0.31 | 0.12
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | System Transformation | Thermal headroom (MW) | 2.91 | 2.94 | 2.94 | 2.93 | 2.9 | 2.87 | 2.83 | 2.77 | 2.7 | 2.61 | 2.5 | 2.37 | 2.24 | 2.11 | 2 | 1.07 | 0.26 | 0.12
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | WPD Best View | Thermal headroom (MW) | 2.91 | 2.92 | 2.89 | 2.85 | 2.78 | 2.68 | 2.58 | 2.47 | 2.35 | 2.2 | 2.03 | 1.87 | 1.61 | 1.35 | 1.1 | -0.67 | -1.71 | -2.23
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Consumer Transformation | Thermal headroom (MW) | 5.21 | 5.19 | 5.11 | 5.01 | 4.85 | 4.58 | 4.31 | 4.01 | 3.71 | 3.34 | 2.9 | 2.02 | 0.92 | 0.23 | -0.45 | -5.4 | -8.49 | -9.87
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Leading the Way | Thermal headroom (MW) | 5.21 | 5.12 | 4.95 | 4.77 | 4.51 | 3.98 | 3.46 | 2.91 | 2.36 | 1.72 | 0.93 | 0.11 | -0.72 | -1.54 | -2.31 | -5.69 | -7.48 | -8.24
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Steady Progression | Thermal headroom (MW) | 5.21 | 5.3 | 5.33 | 5.35 | 5.35 | 5.27 | 5.18 | 5.06 | 4.9 | 4.71 | 4.45 | 4.19 | 3.91 | 3.61 | 3.32 | 0.65 | -1.4 | -2.27
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | System Transformation | Thermal headroom (MW) | 5.21 | 5.27 | 5.27 | 5.25 | 5.21 | 5.15 | 5.05 | 4.89 | 4.69 | 4.46 | 4.16 | 3.83 | 3.5 | 2.82 | 2.17 | -0.81 | -2.93 | -3.33
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | WPD Best View | Thermal headroom (MW) | 5.21 | 5.19 | 5.11 | 5.01 | 4.85 | 4.58 | 4.31 | 4.01 | 3.71 | 3.34 | 2.9 | 2.02 | 0.92 | 0.23 | -0.45 | -5.4 | -8.49 | -9.87
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Consumer Transformation | Thermal headroom (MW) | 2.92 | 2.84 | 2.7 | 2.51 | 1.73 | 1.19 | 0.55 | -0.34 | -1.28 | -2.2 | -3.74 | -5.23 | -6.67 | -8.07 | -9.54 | -17.82 | -22.45 | -24.76
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Leading the Way | Thermal headroom (MW) | 2.92 | 2.69 | 2.4 | 1.94 | 0.63 | -0.38 | -1.52 | -3 | -4.55 | -6.1 | -7.83 | -9.45 | -11.04 | -12.6 | -14.03 | -19.42 | -21.83 | -23.04
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Steady Progression | Thermal headroom (MW) | 2.92 | 2.99 | 2.99 | 2.98 | 2.51 | 2.25 | 1.97 | 1.58 | 1.13 | 0.68 | 0.11 | -0.47 | -1.08 | -1.69 | -2.29 | -6.17 | -9.12 | -10.17
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | System Transformation | Thermal headroom (MW) | 2.92 | 2.96 | 2.93 | 2.87 | 2.26 | 2 | 1.7 | 1.2 | 0.64 | 0.07 | -0.67 | -1.35 | -2.02 | -2.67 | -3.28 | -7.51 | -10.15 | -11
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | WPD Best View | Thermal headroom (MW) | 2.92 | 2.84 | 2.7 | 2.51 | 1.73 | 1.19 | 0.55 | -0.34 | -1.28 | -2.2 | -3.74 | -5.23 | -6.67 | -8.07 | -9.54 | -17.82 | -22.45 | -24.76
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Consumer Transformation | Thermal headroom (MW) | 36.7776 | 35.7885 | 34.2198 | 32.1428 | 30.0493 | 26.735 | 23.6607 | 20.196 | 16.0207 | 11.3275 | 2.2017 | -7.9277 | -18.2592 | -28.3689 | -38.2641 | -87.6706 | -123.418 | -143.2196
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Leading the Way | Thermal headroom (MW) | 36.7776 | 34.9096 | 31.9064 | 28.4267 | 24.709 | 18.4841 | 12.5957 | 5.6656 | -2.8333 | -12.4299 | -21.9116 | -32.2494 | -42.585 | -52.7061 | -62.1921 | -94.6954 | -109.0624 | -116.7735
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Steady Progression | Thermal headroom (MW) | 36.7776 | 37.0911 | 36.7158 | 36.1085 | 35.8363 | 34.5546 | 33.42 | 32.1442 | 30.6319 | 28.2911 | 24.9649 | 22.3764 | 19.526 | 16.1716 | 12.9626 | -9.6884 | -26.3723 | -33.9569
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | System Transformation | Thermal headroom (MW) | 36.7776 | 36.6478 | 35.8165 | 34.6003 | 33.6215 | 32.2509 | 31.0368 | 29.4422 | 27.1978 | 24.6381 | 20.5414 | 16.6336 | 12.2751 | 8.2741 | 4.2176 | -22.426 | -36.6715 | -40.9073
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | WPD Best View | Thermal headroom (MW) | 36.7776 | 35.7885 | 34.2198 | 32.1428 | 30.0493 | 26.735 | 23.6607 | 20.196 | 16.0207 | 11.3275 | 2.2017 | -7.9277 | -18.2592 | -28.3689 | -38.2641 | -87.6706 | -123.418 | -143.2196
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Consumer Transformation | Thermal headroom (MW) | 7.05 | 7.11 | 7.04 | 6.84 | 6.65 | 6.33 | 6.07 | 5.76 | 5.29 | 4.81 | 3.69 | 2.2 | 0.73 | -0.74 | -2.08 | -10.11 | -14.8 | -17.08
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Leading the Way | Thermal headroom (MW) | 7.05 | 6.98 | 6.74 | 6.36 | 5.99 | 5.31 | 4.54 | 3.7 | 2.5 | 1.11 | -0.33 | -1.87 | -3.42 | -4.88 | -6.24 | -11.34 | -13.15 | -13.97
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Steady Progression | Thermal headroom (MW) | 7.05 | 7.26 | 7.34 | 7.33 | 7.37 | 7.28 | 7.2 | 7.12 | 6.95 | 6.79 | 6.49 | 6.19 | 5.8 | 5.38 | 4.97 | 0.7 | -2.3 | -3.51
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | System Transformation | Thermal headroom (MW) | 7.05 | 7.21 | 7.24 | 7.14 | 7.1 | 7.02 | 6.94 | 6.81 | 6.54 | 6.28 | 5.78 | 5.23 | 4.67 | 4.14 | 3.67 | -1.22 | -3.72 | -4.13
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | WPD Best View | Thermal headroom (MW) | 7.05 | 7.11 | 7.04 | 6.84 | 6.65 | 6.33 | 6.07 | 5.76 | 5.29 | 4.81 | 3.69 | 2.2 | 0.73 | -0.74 | -2.08 | -10.11 | -14.8 | -17.08
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Consumer Transformation | Thermal headroom (MW) | 17.06 | 15.69 | 14.08 | 12.23 | 11.18 | 9.8 | 8.4 | 6.39 | 4.23 | 1.76 | -2.74 | -7.27 | -11.67 | -15.95 | -20.32 | -36.79 | -51.83 | -61.34
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Leading the Way | Thermal headroom (MW) | 17.06 | 15.24 | 13.11 | 10.39 | 8.62 | 6.28 | 4.06 | 0.7 | -3.85 | -8.75 | -12.21 | -16.23 | -20.45 | -24.63 | -28.55 | -38.62 | -43.21 | -45.81
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Steady Progression | Thermal headroom (MW) | 17.06 | 16.2 | 15.13 | 13.95 | 13.6 | 13 | 12.37 | 11.54 | 10.7 | 9.07 | 7.08 | 5.98 | 4.86 | 3.47 | 2.23 | -5.58 | -10.47 | -12.56
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | System Transformation | Thermal headroom (MW) | 17.06 | 15.81 | 14.4 | 12.78 | 12.05 | 11.42 | 10.77 | 9.69 | 8.36 | 6.9 | 4.83 | 3.46 | 1.41 | -0.2 | -2.32 | -12.04 | -17.09 | -19.12
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | WPD Best View | Thermal headroom (MW) | 17.06 | 15.69 | 14.08 | 12.23 | 11.18 | 9.8 | 8.4 | 6.39 | 4.23 | 1.76 | -2.74 | -7.27 | -11.67 | -15.95 | -20.32 | -36.79 | -51.83 | -61.34
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Consumer Transformation | Thermal headroom (MW) | 10.942 | 10.422 | 10.012 | 9.432 | 8.552 | 6.792 | 5.032 | 3.432 | 1.242 | -1.338 | -6.738 | -12.158 | -17.578 | -22.868 | -28.208 | -51.688 | -72.008 | -84.168
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Leading the Way | Thermal headroom (MW) | 10.942 | 10.392 | 9.192 | 8.102 | 6.342 | 3.002 | -0.288 | -3.978 | -8.448 | -13.168 | -17.768 | -22.798 | -27.888 | -32.918 | -37.648 | -53.558 | -61.878 | -66.958
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Steady Progression | Thermal headroom (MW) | 10.942 | 11.202 | 11.222 | 11.212 | 11.102 | 10.322 | 9.612 | 8.972 | 8.192 | 6.792 | 4.962 | 3.712 | 2.362 | 0.472 | -1.268 | -12.268 | -19.978 | -24.008
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | System Transformation | Thermal headroom (MW) | 10.942 | 11.092 | 11.002 | 10.812 | 10.472 | 9.602 | 8.782 | 8.012 | 6.922 | 5.752 | 3.732 | 1.632 | -0.468 | -2.518 | -4.408 | -16.958 | -23.218 | -25.688
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | WPD Best View | Thermal headroom (MW) | 10.942 | 10.422 | 10.012 | 9.432 | 8.552 | 6.792 | 5.032 | 3.432 | 1.242 | -1.338 | -6.738 | -12.158 | -17.578 | -22.868 | -28.208 | -51.688 | -72.008 | -84.168
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Consumer Transformation | Thermal headroom (MW) | 1.612 | 1.602 | 1.462 | 1.252 | 0.742 | 0.202 | -0.358 | -1.018 | -1.708 | -2.448 | -3.708 | -5.468 | -7.218 | -8.958 | -10.598 | -19.738 | -25.448 | -28.148
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Leading the Way | Thermal headroom (MW) | 1.612 | 1.412 | 1.042 | 0.642 | -0.158 | -1.128 | -2.168 | -3.268 | -4.388 | -5.958 | -7.818 | -9.778 | -11.648 | -13.498 | -15.188 | -21.688 | -24.448 | -25.608
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Steady Progression | Thermal headroom (MW) | 1.612 | 1.822 | 1.892 | 1.952 | 1.812 | 1.672 | 1.502 | 1.292 | 1.062 | 0.812 | 0.342 | -0.138 | -0.658 | -1.188 | -1.728 | -5.518 | -9.188 | -10.878
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | System Transformation | Thermal headroom (MW) | 1.612 | 1.762 | 1.772 | 1.752 | 1.492 | 1.342 | 1.162 | 0.952 | 0.642 | 0.202 | -0.458 | -1.148 | -1.828 | -2.488 | -3.078 | -7.658 | -10.588 | -11.378
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | WPD Best View | Thermal headroom (MW) | 1.612 | 1.602 | 1.462 | 1.252 | 0.742 | 0.202 | -0.358 | -1.018 | -1.708 | -2.448 | -3.708 | -5.468 | -7.218 | -8.958 | -10.598 | -19.738 | -25.448 | -28.148
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Consumer Transformation | Thermal headroom (MW) | 5.73 | 5.66 | 5.51 | 5.33 | 5.11 | 4.74 | 4.43 | 4.1 | 3.75 | 3.37 | 2.75 | 2.05 | 1.17 | 0.33 | -0.49 | -5.55 | -8.8 | -10.6
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Leading the Way | Thermal headroom (MW) | 5.73 | 5.55 | 5.27 | 4.99 | 4.62 | 3.88 | 3.3 | 2.7 | 2.1 | 1.44 | 0.53 | -0.42 | -1.34 | -2.24 | -3.12 | -6.45 | -8.05 | -9.15
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Steady Progression | Thermal headroom (MW) | 5.73 | 5.78 | 5.77 | 5.75 | 5.73 | 5.57 | 5.47 | 5.35 | 5.21 | 5.02 | 4.72 | 4.42 | 4.09 | 3.75 | 3.41 | 1.68 | 0.2 | -0.5
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | System Transformation | Thermal headroom (MW) | 5.73 | 5.75 | 5.7 | 5.63 | 5.55 | 5.38 | 5.27 | 5.1 | 4.89 | 4.63 | 4.23 | 3.8 | 3.37 | 2.96 | 2.58 | 0.56 | -0.76 | -1.23
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | WPD Best View | Thermal headroom (MW) | 5.73 | 5.66 | 5.51 | 5.33 | 5.11 | 4.74 | 4.43 | 4.1 | 3.75 | 3.37 | 2.75 | 2.05 | 1.17 | 0.33 | -0.49 | -5.55 | -8.8 | -10.6
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Consumer Transformation | Thermal headroom (MW) | 12.93 | 13.26 | 13.38 | 13.5 | 13.55 | 13.57 | 13.6 | 13.59 | 13.58 | 13.4 | 13.05 | 12.73 | 12.39 | 11.99 | 11.51 | 6.55 | 4.29 | 3.58
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Leading the Way | Thermal headroom (MW) | 12.93 | 13.18 | 13.2 | 13.25 | 13.21 | 13.06 | 12.91 | 12.74 | 12.59 | 12.2 | 11.62 | 10.97 | 10.33 | 9.55 | 8.73 | 5.55 | 4.82 | 4.91
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Steady Progression | Thermal headroom (MW) | 12.93 | 13.37 | 13.59 | 13.82 | 14.02 | 14.16 | 14.3 | 14.42 | 14.53 | 14.54 | 14.45 | 14.33 | 14.1 | 13.99 | 13.89 | 12.81 | 12.42 | 12.08
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | System Transformation | Thermal headroom (MW) | 12.93 | 13.34 | 13.53 | 13.73 | 13.88 | 14.04 | 14.19 | 14.3 | 14.38 | 14.29 | 14.07 | 13.83 | 13.55 | 13.37 | 13.2 | 11.92 | 11.18 | 11.47
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | WPD Best View | Thermal headroom (MW) | 12.93 | 13.26 | 13.38 | 13.5 | 13.55 | 13.57 | 13.6 | 13.59 | 13.58 | 13.4 | 13.05 | 12.73 | 12.39 | 11.99 | 11.51 | 6.55 | 4.29 | 3.58
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Consumer Transformation | Thermal headroom (MW) | 112.6461 | 112.6435 | 112.6334 | 112.618 | 112.5914 | 112.5521 | 112.5035 | 112.4595 | 112.4143 | 112.3657 | 112.2669 | 112.1312 | 112.0021 | 111.8966 | 111.7965 | 111.1825 | 110.8208 | 110.6579
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Leading the Way | Thermal headroom (MW) | 112.6461 | 112.628 | 112.6005 | 112.5677 | 112.5196 | 112.4464 | 112.3577 | 112.2716 | 112.186 | 112.091 | 111.9827 | 111.8528 | 111.732 | 111.6174 | 111.5123 | 111.1151 | 110.9371 | 110.871
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Steady Progression | Thermal headroom (MW) | 112.6461 | 112.656 | 112.6592 | 112.6602 | 112.6572 | 112.6432 | 112.6244 | 112.6057 | 112.5852 | 112.5628 | 112.5322 | 112.495 | 112.4586 | 112.4201 | 112.3801 | 112.0664 | 111.8513 | 111.766
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | System Transformation | Thermal headroom (MW) | 112.6461 | 112.6527 | 112.6513 | 112.6475 | 112.6369 | 112.6224 | 112.5976 | 112.574 | 112.5488 | 112.5202 | 112.4817 | 112.4325 | 112.3854 | 112.3175 | 112.2474 | 111.8752 | 111.703 | 111.6664
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | WPD Best View | Thermal headroom (MW) | 112.6461 | 112.6469 | 112.6399 | 112.6287 | 112.6093 | 112.5773 | 112.5344 | 112.4954 | 112.456 | 112.4102 | 112.3275 | 112.2189 | 112.1169 | 112.0302 | 111.9472 | 111.4064 | 111.077 | 110.9311
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Consumer Transformation | Thermal headroom (MW) | 2.78 | 2.67 | 2.49 | 2.25 | 1.86 | 1.21 | 0.23 | -0.44 | -1.15 | -1.93 | -3.78 | -6.35 | -8.66 | -10.53 | -12.3 | -23.73 | -30.47 | -33.65
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Leading the Way | Thermal headroom (MW) | 2.78 | 2.49 | 2.1 | 1.56 | 0.79 | -0.56 | -2.54 | -4.03 | -5.53 | -7.2 | -9.21 | -11.67 | -13.83 | -15.9 | -17.78 | -25.12 | -28.48 | -29.95
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Steady Progression | Thermal headroom (MW) | 2.78 | 2.89 | 2.92 | 2.92 | 2.88 | 2.61 | 2.16 | 1.83 | 1.42 | 0.96 | 0.33 | -0.4 | -1.1 | -1.83 | -2.58 | -8.41 | -12.23 | -13.86
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | System Transformation | Thermal headroom (MW) | 2.78 | 2.83 | 2.8 | 2.72 | 2.57 | 2.29 | 1.69 | 1.27 | 0.78 | 0.21 | -0.53 | -1.51 | -2.37 | -3.56 | -4.83 | -11.47 | -14.64 | -15.52
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | WPD Best View | Thermal headroom (MW) | 2.78 | 2.75 | 2.63 | 2.47 | 2.2 | 1.69 | 0.82 | 0.25 | -0.36 | -1.2 | -2.76 | -5.03 | -7.04 | -8.63 | -10.18 | -19.98 | -25.61 | -28.11
Chesterfield 132kV | Staveley | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Consumer Transformation | Thermal headroom (MW) | 0.67 | 0.78 | 0.78 | 0.7 | 0.43 | 0.13 | -0.11 | -0.34 | -0.63 | -0.97 | -1.72 | -3.11 | -4.53 | -5.54 | -6.52 | -11.79 | -14.93 | -16.12
Chesterfield 132kV | Staveley | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Leading the Way | Thermal headroom (MW) | 0.67 | 0.71 | 0.61 | 0.45 | 0.03 | -0.42 | -0.81 | -1.3 | -1.89 | -2.81 | -3.8 | -4.92 | -6.03 | -7.07 | -8.08 | -11.62 | -13.12 | -13.13
Chesterfield 132kV | Staveley | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Steady Progression | Thermal headroom (MW) | 0.67 | 0.88 | 0.99 | 1.05 | 1.04 | 0.99 | 0.95 | 0.89 | 0.82 | 0.72 | 0.55 | 0.35 | 0.12 | -0.14 | -0.41 | -3.35 | -5.99 | -7
Chesterfield 132kV | Staveley | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | System Transformation | Thermal headroom (MW) | 0.67 | 0.86 | 0.94 | 0.97 | 0.87 | 0.8 | 0.73 | 0.63 | 0.5 | 0.34 | 0.07 | -0.25 | -0.58 | -1.27 | -1.96 | -6.1 | -7.91 | -7.96
Chesterfield 132kV | Staveley | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | WPD Best View | Thermal headroom (MW) | 0.67 | 0.88 | 0.99 | 1.05 | 1.04 | 0.98 | 0.94 | 0.87 | 0.79 | 0.68 | 0.51 | 0.3 | 0.06 | -0.2 | -0.48 | -3.56 | -6.24 | -7.29
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Consumer Transformation | Thermal headroom (MW) | 8.42 | 8.18 | 7.78 | 7.23 | 6.49 | 5.47 | 4.32 | 3.3 | 2.25 | 1.06 | -1.1 | -3.89 | -6.57 | -8.86 | -10.95 | -23.94 | -31.96 | -35.76
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Leading the Way | Thermal headroom (MW) | 8.42 | 7.67 | 6.75 | 5.75 | 4.45 | 2.66 | 0.8 | -1.04 | -2.89 | -4.87 | -7.07 | -9.84 | -12.43 | -14.87 | -17.08 | -25.59 | -29.69 | -31.65
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Steady Progression | Thermal headroom (MW) | 8.42 | 8.48 | 8.43 | 8.32 | 8.17 | 7.78 | 7.34 | 6.92 | 6.49 | 5.98 | 5.32 | 4.41 | 3.57 | 2.68 | 1.76 | -5 | -9.56 | -11.49
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | System Transformation | Thermal headroom (MW) | 8.42 | 8.4 | 8.2 | 7.96 | 7.59 | 7.22 | 6.73 | 6.28 | 5.8 | 5.14 | 4.3 | 3.16 | 2.09 | 0.57 | -0.96 | -8.73 | -12.69 | -13.77
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | WPD Best View | Thermal headroom (MW) | 8.42 | 8.18 | 7.78 | 7.23 | 6.49 | 5.47 | 4.32 | 3.3 | 2.25 | 1.06 | -1.1 | -3.89 | -6.57 | -8.86 | -10.95 | -23.94 | -31.96 | -35.76
Chesterfield 132kV | Staveley | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Consumer Transformation | Thermal headroom (MW) | -4.93 | -4.8 | -4.81 | -4.84 | -4.99 | -5.33 | -5.77 | -6.58 | -7.27 | -7.89 | -8.9 | -9.94 | -11.01 | -12 | -13.01 | -19.09 | -22.12 | -23.33
Chesterfield 132kV | Staveley | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Leading the Way | Thermal headroom (MW) | -4.93 | -5.01 | -5.25 | -5.49 | -5.82 | -6.53 | -7.36 | -8.73 | -9.89 | -10.93 | -12.03 | -13.19 | -14.4 | -15.55 | -16.6 | -20.29 | -21.58 | -21.87
Chesterfield 132kV | Staveley | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Steady Progression | Thermal headroom (MW) | -4.93 | -4.69 | -4.57 | -4.44 | -4.4 | -4.5 | -4.64 | -4.95 | -5.25 | -5.48 | -5.81 | -6.12 | -6.47 | -6.83 | -7.22 | -9.84 | -11.16 | -11.34
Chesterfield 132kV | Staveley | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | System Transformation | Thermal headroom (MW) | -4.93 | -4.71 | -4.62 | -4.54 | -4.54 | -4.66 | -4.88 | -5.37 | -5.78 | -6.06 | -6.45 | -6.84 | -7.34 | -7.89 | -8.47 | -11.44 | -12.33 | -12.32
Chesterfield 132kV | Staveley | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | WPD Best View | Thermal headroom (MW) | -4.93 | -4.8 | -4.81 | -4.84 | -4.99 | -5.33 | -5.77 | -6.58 | -7.27 | -7.89 | -8.9 | -9.94 | -11.01 | -12 | -13.01 | -19.09 | -22.12 | -23.33
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Consumer Transformation | Thermal headroom (MW) | 32.9218 | 29.8981 | 26.2923 | 23.7228 | 21.5841 | 18.9123 | 16.24 | 13.4383 | 10.3136 | 6.9934 | 0.60227 | -6.0687 | -12.6685 | -18.9703 | -25.2454 | -58.679 | -82.4248 | -96.1114
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Leading the Way | Thermal headroom (MW) | 32.9218 | 28.6788 | 23.8994 | 20.1428 | 16.9937 | 12.7229 | 8.0748 | 2.6847 | -4.1731 | -11.3246 | -17.359 | -24.2344 | -31.3171 | -38.1546 | -44.638 | -67.9613 | -80.6502 | -88.6271
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Steady Progression | Thermal headroom (MW) | 32.9218 | 30.9113 | 28.4493 | 27.0207 | 26.247 | 24.9972 | 23.6025 | 22.0727 | 20.5286 | 19.192 | 17.3767 | 15.5577 | 13.6393 | 11.6281 | 9.5396 | -5.2722 | -14.6726 | -18.7152
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | System Transformation | Thermal headroom (MW) | 32.9218 | 30.4261 | 27.4091 | 25.5858 | 24.4066 | 23.2309 | 21.8244 | 20.3171 | 18.5334 | 16.9016 | 14.6145 | 12.2517 | 9.7775 | 7.1369 | 4.3939 | -13.7801 | -21.798 | -23.7774
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | WPD Best View | Thermal headroom (MW) | 32.9218 | 29.9574 | 26.4123 | 23.9245 | 21.9425 | 19.411 | 16.8601 | 14.1546 | 11.1566 | 7.9752 | 1.9206 | -4.0572 | -9.9682 | -15.83 | -21.6936 | -53.8157 | -77.2985 | -90.8846
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Consumer Transformation | Thermal headroom (MW) | -0.04 | -1.57 | -3.28 | -3.86 | -4.52 | -5.31 | -5.95 | -6.59 | -7.27 | -7.97 | -9.22 | -10.46 | -11.64 | -12.78 | -13.9 | -21.27 | -25.56 | -27.67
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Leading the Way | Thermal headroom (MW) | -0.04 | -2.06 | -4.21 | -5 | -5.79 | -6.89 | -7.91 | -9.03 | -10.22 | -11.43 | -12.75 | -14.11 | -15.35 | -16.52 | -17.62 | -22.47 | -24.59 | -25.87
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Steady Progression | Thermal headroom (MW) | -0.04 | -1.23 | -2.55 | -2.84 | -3.13 | -3.61 | -4.06 | -4.49 | -4.87 | -5.16 | -5.56 | -5.93 | -6.41 | -6.89 | -7.41 | -10.61 | -12.66 | -13.77
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | System Transformation | Thermal headroom (MW) | -0.04 | -1.45 | -2.98 | -3.35 | -3.74 | -4.08 | -4.38 | -4.61 | -4.91 | -5.19 | -5.71 | -6.24 | -6.73 | -7.25 | -7.78 | -11.91 | -13.85 | -14.47
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | WPD Best View | Thermal headroom (MW) | -0.04 | -1.57 | -3.28 | -3.86 | -4.52 | -5.31 | -5.95 | -6.59 | -7.27 | -7.97 | -9.22 | -10.46 | -11.64 | -12.78 | -13.9 | -21.27 | -25.56 | -27.67
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Consumer Transformation | Thermal headroom (MW) | 6.44 | 6.52 | 6.42 | 6.32 | 6.18 | 5.64 | 4.96 | 4.42 | 3.54 | 2.75 | -0.43 | -3.58 | -6.74 | -9.9 | -13.26 | -23.69 | -42.66 | -57.42
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Leading the Way | Thermal headroom (MW) | 6.44 | 6.23 | 5.88 | 5.51 | 4.81 | 3.52 | 1.91 | 0.11 | -4.61 | -9.39 | -11.01 | -13.79 | -17.57 | -21.59 | -25.49 | -36.27 | -47.82 | -59.48
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Steady Progression | Thermal headroom (MW) | 6.44 | 6.67 | 6.74 | 6.81 | 6.88 | 6.78 | 6.53 | 6.35 | 6.01 | 5.7 | 5.21 | 4.85 | 4.49 | 4.06 | 3.66 | 0.85 | -0.48 | -0.88
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | System Transformation | Thermal headroom (MW) | 6.44 | 6.61 | 6.61 | 6.61 | 6.58 | 6.47 | 6.19 | 6 | 5.49 | 5.2 | 4.64 | 4.26 | 3.69 | 3.23 | 2.65 | -0.48 | -2.12 | -2.65
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | WPD Best View | Thermal headroom (MW) | 6.44 | 6.52 | 6.42 | 6.32 | 6.18 | 5.65 | 4.98 | 4.44 | 3.57 | 2.79 | -0.38 | -3.53 | -6.69 | -9.85 | -13.2 | -23.56 | -42.54 | -57.26
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Consumer Transformation | Thermal headroom (MW) | 4.7 | 3.07 | 1.31 | -0.39 | -1.08 | -1.7 | -2.48 | -3.27 | -4.14 | -4.94 | -6.01 | -7.06 | -8.15 | -9.16 | -10.14 | -15.82 | -18.21 | -19.02
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Leading the Way | Thermal headroom (MW) | 4.7 | 2.71 | 0.6 | -1.61 | -2.43 | -3.17 | -4.12 | -5.27 | -6.48 | -7.48 | -8.56 | -9.73 | -10.87 | -11.96 | -12.94 | -16.43 | -17.26 | -17.07
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Steady Progression | Thermal headroom (MW) | 4.7 | 3.42 | 2.06 | 0.76 | 0.36 | -0.02 | -0.51 | -1.08 | -1.58 | -1.95 | -2.35 | -2.84 | -3.26 | -3.71 | -4.19 | -7.37 | -9.13 | -9.73
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | System Transformation | Thermal headroom (MW) | 4.7 | 3.21 | 1.59 | 0.09 | -0.42 | -0.81 | -1.32 | -1.83 | -2.38 | -2.84 | -3.3 | -3.82 | -4.41 | -4.97 | -5.58 | -9.44 | -10.63 | -10.52
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | WPD Best View | Thermal headroom (MW) | 4.7 | 3.07 | 1.31 | -0.39 | -1.08 | -1.7 | -2.48 | -3.27 | -4.14 | -4.94 | -6.01 | -7.06 | -8.15 | -9.16 | -10.14 | -15.82 | -18.21 | -19.02
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Consumer Transformation | Thermal headroom (MW) | 2.65 | 2.57 | 2.44 | 2.29 | 2.01 | 1.65 | 1.32 | 0.96 | 0.57 | 0.05 | -0.87 | -1.76 | -2.62 | -3.51 | -4.38 | -9.52 | -12.39 | -13.95
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Leading the Way | Thermal headroom (MW) | 2.65 | 2.5 | 2.3 | 2.01 | 1.57 | 0.91 | 0.2 | -0.56 | -1.37 | -2.33 | -3.27 | -4.28 | -5.24 | -6.13 | -6.98 | -10.33 | -11.97 | -12.79
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Steady Progression | Thermal headroom (MW) | 2.65 | 2.66 | 2.63 | 2.6 | 2.52 | 2.37 | 2.23 | 2.06 | 1.88 | 1.67 | 1.38 | 1.1 | 0.8 | 0.5 | 0.2 | -2.04 | -3.51 | -4.24
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | System Transformation | Thermal headroom (MW) | 2.65 | 2.64 | 2.59 | 2.53 | 2.41 | 2.24 | 2.06 | 1.84 | 1.59 | 1.31 | 0.93 | 0.53 | 0.15 | -0.22 | -0.58 | -3.21 | -4.57 | -5.15
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | WPD Best View | Thermal headroom (MW) | 2.65 | 2.57 | 2.44 | 2.29 | 2.01 | 1.65 | 1.32 | 0.96 | 0.57 | 0.05 | -0.87 | -1.76 | -2.62 | -3.51 | -4.38 | -9.52 | -12.39 | -13.95
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Consumer Transformation | Thermal headroom (MW) | 42.7581 | 37.0411 | 29.8236 | 21.9195 | 13.4396 | 3.6931 | -4.8659 | -12.9866 | -21.7062 | -30.9529 | -45.3433 | -59.9834 | -74.4883 | -87.8263 | -100.732 | -167.0348 | -211.1315 | -233.2144
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Leading the Way | Thermal headroom (MW) | 42.7581 | 34.5824 | 24.0774 | 12.3333 | 0.70946 | -12.6344 | -23.9716 | -35.9231 | -49.1686 | -62.9653 | -78.0221 | -92.9845 | -107.5847 | -122.0109 | -135.1651 | -179.5772 | -201.4682 | -212.7158
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Steady Progression | Thermal headroom (MW) | 42.7581 | 39.5023 | 35.3565 | 31.2755 | 27.3435 | 22.5785 | 18.2929 | 14.2134 | 10.1593 | 6.0464 | 0.34106 | -4.5995 | -9.6163 | -14.9016 | -20.1434 | -53.6963 | -76.2372 | -86.0351
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | System Transformation | Thermal headroom (MW) | 42.7581 | 38.3739 | 32.9695 | 27.3485 | 21.8164 | 16.6541 | 12.2656 | 7.9088 | 2.7881 | -2.2222 | -9.1103 | -15.3652 | -22.2186 | -30.0807 | -38.2638 | -75.3192 | -94.881 | -101.2587
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | WPD Best View | Thermal headroom (MW) | 42.7581 | 35.6484 | 26.1959 | 15.6054 | 5.2386 | -6.8054 | -17.1021 | -27.4227 | -38.1371 | -49.8346 | -64.5719 | -78.859 | -92.6654 | -106.3885 | -119.2063 | -168.1586 | -195.7012 | -209.917
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Consumer Transformation | Thermal headroom (MW) | 12.89 | 12.12 | 11.08 | 10.05 | 8.94 | 7.98 | 7.08 | 6.25 | 5.36 | 4.71 | 4.05 | 3.65 | 3.27 | 2.83 | 2.43 | -0.42 | -1.36 | -1.64
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Leading the Way | Thermal headroom (MW) | 12.89 | 11.98 | 10.78 | 9.55 | 8.3 | 7.13 | 6.15 | 5.13 | 3.98 | 3.21 | 2.52 | 2.05 | 1.67 | 1.15 | 0.68 | -0.69 | -0.89 | -0.72
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Steady Progression | Thermal headroom (MW) | 12.89 | 12.3 | 11.52 | 10.79 | 10.04 | 9.43 | 8.9 | 8.37 | 7.85 | 7.49 | 7.06 | 6.68 | 6.33 | 6.01 | 5.71 | 4.56 | 4.76 | 5.07
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | System Transformation | Thermal headroom (MW) | 12.89 | 12.18 | 11.26 | 10.4 | 9.5 | 8.83 | 8.21 | 7.59 | 6.9 | 6.43 | 5.98 | 5.65 | 5.34 | 5.03 | 4.76 | 3.97 | 3.91 | 4.15
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | WPD Best View | Thermal headroom (MW) | 12.89 | 12.25 | 11.34 | 10.44 | 9.52 | 8.71 | 7.97 | 7.29 | 6.58 | 6.02 | 5.42 | 4.99 | 4.62 | 4.29 | 3.98 | 2.85 | 2.71 | 2.88
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Consumer Transformation | Thermal headroom (MW) | 14.49 | 13.74 | 12.85 | 11.89 | 11.19 | 10.43 | 9.6 | 8.77 | 7.83 | 6.79 | 5.44 | 4.3 | 3.15 | 2.09 | 1.07 | -4.32 | -7.49 | -8.96
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Leading the Way | Thermal headroom (MW) | 14.49 | 13.54 | 12.42 | 11.16 | 10.34 | 9.33 | 8.38 | 7.23 | 5.87 | 4.36 | 2.7 | 1.52 | 0.31 | -0.83 | -1.77 | -4.94 | -6.33 | -6.98
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Steady Progression | Thermal headroom (MW) | 14.49 | 13.99 | 13.41 | 12.82 | 12.55 | 12.18 | 11.8 | 11.47 | 11.12 | 10.79 | 10.34 | 9.95 | 9.57 | 9.13 | 8.74 | 6.66 | 5.06 | 4.52
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | System Transformation | Thermal headroom (MW) | 14.49 | 13.87 | 13.15 | 12.42 | 12.05 | 11.73 | 11.38 | 11.01 | 10.55 | 10.03 | 9.41 | 8.92 | 8.43 | 7.94 | 7.52 | 5.43 | 4.08 | 3.63
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | WPD Best View | Thermal headroom (MW) | 14.49 | 13.59 | 12.51 | 11.31 | 10.53 | 9.56 | 8.61 | 7.58 | 6.39 | 5.04 | 3.53 | 2.35 | 1.14 | -0.06 | -1.14 | -5.05 | -6.66 | -7.48
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Consumer Transformation | Thermal headroom (MW) | 9.81 | 9.55 | 9.17 | 8.74 | 8.16 | 7.21 | 6.37 | 5.54 | 4.71 | 3.69 | 1.89 | 0 | -1.86 | -3.72 | -5.49 | -14.71 | -20.89 | -24.09
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Leading the Way | Thermal headroom (MW) | 9.81 | 9.16 | 8.39 | 7.59 | 6.59 | 5.24 | 3.96 | 2.64 | 1.3 | -0.25 | -2.11 | -4.12 | -6.15 | -8.14 | -9.98 | -16.06 | -18.75 | -19.88
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Steady Progression | Thermal headroom (MW) | 9.81 | 9.87 | 9.88 | 9.88 | 9.85 | 9.56 | 9.21 | 8.88 | 8.58 | 8.23 | 7.68 | 7.17 | 6.56 | 5.94 | 5.2 | -0.02 | -4.03 | -5.64
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | System Transformation | Thermal headroom (MW) | 9.81 | 9.79 | 9.7 | 9.54 | 9.27 | 8.88 | 8.51 | 8.16 | 7.79 | 7.34 | 6.7 | 5.95 | 5.12 | 4.25 | 3.24 | -2.43 | -5.19 | -5.89
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | WPD Best View | Thermal headroom (MW) | 9.81 | 9.37 | 8.77 | 8.15 | 7.37 | 6.24 | 5.15 | 4.05 | 2.9 | 1.53 | -0.24 | -2.15 | -4.02 | -5.91 | -7.68 | -15.34 | -19.78 | -21.92
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Consumer Transformation | Thermal headroom (MW) | 13.985 | 13.125 | 12.105 | 10.955 | 9.595 | 7.985 | 6.715 | 5.565 | 4.335 | 2.935 | 0.695 | -1.895 | -4.395 | -6.465 | -8.455 | -18.985 | -26.015 | -29.365
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Leading the Way | Thermal headroom (MW) | 13.985 | 12.745 | 11.125 | 9.245 | 7.285 | 4.995 | 3.205 | 1.425 | -0.485 | -2.615 | -4.915 | -7.445 | -9.825 | -12.145 | -14.285 | -22.035 | -26.275 | -28.665
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Steady Progression | Thermal headroom (MW) | 13.985 | 13.475 | 12.895 | 12.325 | 11.645 | 10.825 | 10.135 | 9.485 | 8.855 | 8.185 | 7.285 | 6.455 | 5.635 | 4.775 | 3.905 | -2.085 | -6.285 | -8.255
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | System Transformation | Thermal headroom (MW) | 13.985 | 13.305 | 12.545 | 11.735 | 10.825 | 9.905 | 9.235 | 8.585 | 7.835 | 7.075 | 5.945 | 4.935 | 3.765 | 2.255 | 0.615 | -6.555 | -10.375 | -11.845
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | WPD Best View | Thermal headroom (MW) | 13.985 | 12.755 | 11.145 | 9.275 | 7.335 | 5.085 | 3.335 | 1.615 | -0.095 | -1.995 | -4.285 | -6.715 | -8.955 | -11.105 | -13.095 | -20.525 | -24.315 | -26.195
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Consumer Transformation | Thermal headroom (MW) | 9.44 | 9.58 | 9.48 | 9.23 | 8.75 | 7.97 | 7.22 | 6.39 | 5.5 | 4.54 | 1.84 | -0.66 | -3.52 | -6.8 | -10.12 | -22.64 | -34.98 | -42.87
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Leading the Way | Thermal headroom (MW) | 9.44 | 9.21 | 8.73 | 8.11 | 7.18 | 6.04 | 4.87 | 3.44 | 1.62 | -0.31 | -2.47 | -5.3 | -8.41 | -11.44 | -14.33 | -22.37 | -26.68 | -29.34
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Steady Progression | Thermal headroom (MW) | 9.44 | 9.9 | 10.14 | 10.32 | 10.41 | 10.3 | 10.18 | 10.01 | 9.8 | 9.12 | 8.1 | 7.49 | 6.82 | 6.03 | 5.32 | 0.65 | -2.86 | -5.11
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | System Transformation | Thermal headroom (MW) | 9.44 | 9.79 | 9.9 | 9.92 | 9.8 | 9.68 | 9.55 | 9.35 | 8.94 | 8.43 | 7.31 | 6.12 | 4.89 | 3.71 | 2.63 | -1.93 | -4.97 | -5.9
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | WPD Best View | Thermal headroom (MW) | 9.44 | 9.58 | 9.48 | 9.23 | 8.75 | 7.97 | 7.22 | 6.39 | 5.5 | 4.54 | 1.84 | -0.66 | -3.52 | -6.8 | -10.12 | -22.64 | -34.98 | -42.87
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Consumer Transformation | Thermal headroom (MW) | 11.78 | 11.7 | 11.53 | 11.28 | 10.94 | 10.07 | 9.19 | 8.33 | 7.3 | 6.27 | 4.48 | 2.77 | 1.01 | -0.68 | -2.29 | -9.85 | -14.8 | -18.54
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Leading the Way | Thermal headroom (MW) | 11.78 | 11.31 | 10.79 | 10.21 | 9.52 | 8.38 | 7.28 | 6.05 | 4.65 | 3.2 | 1.38 | -0.48 | -2.34 | -4.12 | -5.74 | -10.6 | -13.25 | -15.38
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Steady Progression | Thermal headroom (MW) | 11.78 | 12.01 | 12.15 | 12.24 | 12.3 | 12.17 | 12.04 | 11.9 | 11.74 | 11.44 | 11.02 | 10.61 | 10.19 | 9.7 | 9.17 | 5.02 | 1.74 | 0.62
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | System Transformation | Thermal headroom (MW) | 11.78 | 11.9 | 11.88 | 11.84 | 11.75 | 11.64 | 11.51 | 11.2 | 10.79 | 10.43 | 9.98 | 9.44 | 8.87 | 8.22 | 7.55 | 3.79 | 1.55 | 0.51
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | WPD Best View | Thermal headroom (MW) | 11.78 | 11.7 | 11.53 | 11.28 | 10.94 | 10.07 | 9.19 | 8.33 | 7.3 | 6.27 | 4.48 | 2.77 | 1.01 | -0.68 | -2.29 | -9.85 | -14.8 | -18.54
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Consumer Transformation | Thermal headroom (MW) | 53.09 | 52.5359 | 51.4695 | 49.6077 | 45.9271 | 40.5788 | 35.7232 | 30.714 | 25.1215 | 18.5331 | 9.7191 | -0.73832 | -11.4453 | -21.38 | -31.036 | -75.5943 | -97.5067 | -108.5387
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Leading the Way | Thermal headroom (MW) | 53.09 | 51.7828 | 49.897 | 47.2677 | 42.3611 | 34.8859 | 28.1655 | 20.0179 | 10.7886 | 0.072116 | -9.3266 | -19.3131 | -29.0402 | -38.3665 | -46.8701 | -80.0561 | -89.1691 | -92.1409
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Steady Progression | Thermal headroom (MW) | 53.09 | 53.4646 | 53.4568 | 53.1196 | 51.6542 | 49.0925 | 47.0262 | 44.7617 | 42.1967 | 39.0611 | 34.9421 | 31.0376 | 26.8631 | 22.3934 | 17.5527 | -15.7222 | -31.1322 | -36.1446
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | System Transformation | Thermal headroom (MW) | 53.09 | 53.1635 | 52.8045 | 52.0191 | 49.7724 | 47.3043 | 45.2529 | 42.7777 | 39.7526 | 36.1634 | 31.9491 | 27.4943 | 22.7637 | 17.3677 | 11.6423 | -22.0814 | -39.2867 | -42.2962
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | WPD Best View | Thermal headroom (MW) | 53.09 | 53.1317 | 52.723 | 51.8872 | 49.6091 | 47.1394 | 45.0272 | 42.5093 | 39.4095 | 35.7779 | 31.6738 | 27.0618 | 21.9436 | 15.9771 | 10.0567 | -22.9808 | -38.9147 | -41.559
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Consumer Transformation | Thermal headroom (MW) | 6.81 | 6.16 | 5.71 | 4.71 | 2.34 | 0.86 | -0.65 | -1.98 | -3.34 | -4.97 | -6.95 | -8.76 | -10.58 | -12.34 | -14.02 | -22.2 | -26.38 | -28.24
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Leading the Way | Thermal headroom (MW) | 6.81 | 5.74 | 4.96 | 3.55 | 0.46 | -1.47 | -3.4 | -5.08 | -6.81 | -8.86 | -10.79 | -12.63 | -14.45 | -16.18 | -17.67 | -22.8 | -24.43 | -24.53
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Steady Progression | Thermal headroom (MW) | 6.81 | 6.48 | 6.42 | 5.97 | 4.52 | 3.83 | 3.17 | 2.64 | 2.12 | 1.51 | 0.78 | 0.04 | -0.7 | -1.42 | -2.14 | -6.99 | -10.27 | -11.64
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | System Transformation | Thermal headroom (MW) | 6.81 | 6.3 | 6.04 | 5.37 | 3.49 | 2.66 | 1.8 | 1.07 | 0.36 | -0.52 | -1.39 | -2.19 | -3.03 | -3.99 | -4.92 | -10.45 | -12.57 | -12.63
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | WPD Best View | Thermal headroom (MW) | 6.81 | 6.3 | 6.04 | 5.37 | 3.49 | 2.67 | 1.82 | 1.1 | 0.4 | -0.47 | -1.34 | -2.13 | -2.98 | -3.93 | -4.86 | -10.37 | -12.5 | -12.56
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Consumer Transformation | Thermal headroom (MW) | 25.59 | 25.47 | 25.23 | 24.86 | 24 | 22.08 | 20.82 | 19.54 | 18.21 | 16.8 | 15.18 | 13.53 | 11.84 | 10.09 | 8.35 | 0.65 | -0.1 | 0.15
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Leading the Way | Thermal headroom (MW) | 25.59 | 25.43 | 25.09 | 24.67 | 23.66 | 20.98 | 19.47 | 17.75 | 16 | 14.07 | 12.43 | 10.68 | 9.02 | 7.42 | 5.86 | -1.36 | -1.42 | -0.95
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Steady Progression | Thermal headroom (MW) | 25.59 | 25.56 | 25.46 | 25.35 | 24.91 | 23.75 | 23.17 | 22.54 | 21.9 | 21.24 | 20.35 | 19.43 | 18.36 | 17.27 | 16.17 | 10.02 | 9.57 | 10.01
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | System Transformation | Thermal headroom (MW) | 25.59 | 25.55 | 25.42 | 25.27 | 24.72 | 23.47 | 22.88 | 22.18 | 21.45 | 20.61 | 19.62 | 18.6 | 17.53 | 16.39 | 15.25 | 9.1 | 7.79 | 8.01
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | WPD Best View | Thermal headroom (MW) | 25.59 | 25.57 | 25.48 | 25.38 | 24.93 | 23.96 | 23.55 | 23.06 | 22.46 | 21.75 | 20.89 | 19.99 | 19.01 | 17.98 | 16.94 | 11.12 | 9.78 | 10.09
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Consumer Transformation | Thermal headroom (MW) | 12.724 | 12.424 | 11.954 | 11.334 | 10.564 | 9.504 | 8.364 | 7.014 | 5.054 | 2.384 | -1.956 | -6.396 | -10.626 | -14.736 | -18.816 | -34.736 | -45.816 | -52.446
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Leading the Way | Thermal headroom (MW) | 12.724 | 12.194 | 11.454 | 10.604 | 9.554 | 8.054 | 6.294 | 3.674 | -0.016 | -4.206 | -8.166 | -12.516 | -16.566 | -20.426 | -24.106 | -35.286 | -38.576 | -39.826
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Steady Progression | Thermal headroom (MW) | 12.724 | 12.754 | 12.664 | 12.544 | 12.404 | 12.074 | 11.704 | 11.184 | 10.394 | 9.134 | 7.634 | 6.494 | 5.324 | 3.934 | 2.394 | -7.616 | -13.646 | -16.126
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | System Transformation | Thermal headroom (MW) | 12.724 | 12.674 | 12.474 | 12.224 | 11.904 | 11.544 | 11.124 | 10.414 | 9.274 | 7.974 | 6.244 | 4.304 | 2.164 | -0.056 | -2.376 | -14.086 | -18.386 | -19.286
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | WPD Best View | Thermal headroom (MW) | 12.724 | 12.674 | 12.474 | 12.224 | 11.904 | 11.544 | 11.124 | 10.414 | 9.274 | 7.974 | 6.244 | 4.304 | 2.164 | -0.056 | -2.376 | -14.086 | -18.386 | -19.286
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Consumer Transformation | Thermal headroom (MW) | 0.076 | 0.106 | 0.076 | 0.006 | -0.134 | -0.374 | -0.634 | -0.924 | -1.224 | -1.584 | -2.374 | -3.154 | -3.974 | -4.764 | -5.524 | -9.254 | -11.124 | -12.024
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Leading the Way | Thermal headroom (MW) | 0.076 | 0.046 | -0.044 | -0.164 | -0.404 | -0.764 | -1.194 | -1.714 | -2.424 | -3.294 | -4.054 | -4.844 | -5.644 | -6.414 | -7.084 | -9.614 | -10.464 | -10.674
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Steady Progression | Thermal headroom (MW) | 0.076 | 0.176 | 0.216 | 0.246 | 0.246 | 0.156 | 0.046 | -0.074 | -0.214 | -0.374 | -0.604 | -0.824 | -1.084 | -1.394 | -1.844 | -4.904 | -6.634 | -7.144
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | System Transformation | Thermal headroom (MW) | 0.076 | 0.156 | 0.176 | 0.176 | 0.126 | 0.056 | -0.034 | -0.154 | -0.314 | -0.504 | -0.714 | -0.954 | -1.194 | -1.454 | -1.974 | -5.084 | -6.884 | -7.224
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | WPD Best View | Thermal headroom (MW) | 0.076 | 0.146 | 0.136 | 0.126 | 0.036 | -0.124 | -0.294 | -0.514 | -0.764 | -1.034 | -1.264 | -1.714 | -2.194 | -2.784 | -3.344 | -6.254 | -7.744 | -7.974
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Consumer Transformation | Thermal headroom (MW) | 7.335 | 7.365 | 7.315 | 7.225 | 7.065 | 6.715 | 6.315 | 5.895 | 5.455 | 4.975 | 4.575 | 3.615 | 2.475 | 1.765 | 1.085 | -3.455 | -5.865 | -7.035
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Leading the Way | Thermal headroom (MW) | 7.335 | 7.305 | 7.195 | 7.055 | 6.835 | 6.295 | 5.715 | 4.965 | 4.195 | 3.345 | 2.665 | 1.905 | 1.135 | 0.375 | -0.275 | -3.525 | -5.015 | -5.585
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Steady Progression | Thermal headroom (MW) | 7.335 | 7.445 | 7.485 | 7.515 | 7.525 | 7.405 | 7.285 | 7.125 | 6.955 | 6.755 | 6.475 | 6.195 | 5.885 | 5.575 | 5.255 | 2.515 | 0.715 | -0.015
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | System Transformation | Thermal headroom (MW) | 7.335 | 7.425 | 7.435 | 7.425 | 7.375 | 7.265 | 7.105 | 6.905 | 6.665 | 6.365 | 6.095 | 5.805 | 5.505 | 4.855 | 4.235 | 1.325 | -0.825 | -1.275
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | WPD Best View | Thermal headroom (MW) | 7.335 | 7.425 | 7.435 | 7.425 | 7.375 | 7.325 | 7.235 | 7.115 | 6.955 | 6.735 | 6.475 | 6.195 | 5.905 | 5.265 | 4.645 | 1.875 | -0.325 | -0.745
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Consumer Transformation | Thermal headroom (MW) | 3.02 | 3.07 | 3.04 | 2.97 | 2.83 | 2.51 | 2.18 | 1.85 | 1.51 | 1.15 | 0.73 | -0.01 | -0.76 | -1.44 | -2.11 | -4.83 | -6.23 | -7.01
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Leading the Way | Thermal headroom (MW) | 3.02 | 3.03 | 2.96 | 2.85 | 2.65 | 2.23 | 1.79 | 1.18 | 0.58 | -0.12 | -0.62 | -1.18 | -1.76 | -2.32 | -2.81 | -4.99 | -5.8 | -6.29
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Steady Progression | Thermal headroom (MW) | 3.02 | 3.12 | 3.14 | 3.15 | 3.13 | 2.95 | 2.76 | 2.55 | 2.31 | 2.05 | 1.66 | 1.28 | 0.89 | 0.5 | 0.07 | -3.36 | -4.62 | -4.98
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | System Transformation | Thermal headroom (MW) | 3.02 | 3.1 | 3.1 | 3.08 | 3.02 | 2.97 | 2.88 | 2.76 | 2.62 | 2.43 | 2.17 | 1.89 | 1.61 | 1.32 | 1.07 | -1.6 | -3.91 | -4.47
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | WPD Best View | Thermal headroom (MW) | 3.02 | 3.1 | 3.1 | 3.08 | 3.02 | 2.97 | 2.88 | 2.76 | 2.62 | 2.43 | 2.17 | 1.89 | 1.61 | 1.32 | 1.07 | -1.6 | -3.91 | -4.47
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Consumer Transformation | Thermal headroom (MW) | 2.73 | 2.76 | 2.7 | 2.57 | 2.36 | 1.91 | 1.45 | 0.98 | 0.49 | -0.07 | -0.61 | -1.62 | -2.65 | -3.69 | -4.61 | -9.49 | -12.13 | -13.51
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Leading the Way | Thermal headroom (MW) | 2.73 | 2.68 | 2.51 | 2.29 | 1.95 | 1.32 | 0.61 | -0.24 | -1.08 | -2.14 | -3.09 | -4.07 | -5.05 | -5.96 | -6.78 | -10.27 | -11.57 | -12.28
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Steady Progression | Thermal headroom (MW) | 2.73 | 2.87 | 2.91 | 2.94 | 2.92 | 2.73 | 2.53 | 2.3 | 2.03 | 1.74 | 1.32 | 0.88 | 0.42 | -0.05 | -0.52 | -4.3 | -6.17 | -6.78
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | System Transformation | Thermal headroom (MW) | 2.73 | 2.84 | 2.85 | 2.83 | 2.75 | 2.63 | 2.48 | 2.26 | 2 | 1.68 | 1.3 | 0.9 | 0.47 | 0.07 | -0.3 | -3.71 | -6.35 | -6.98
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | WPD Best View | Thermal headroom (MW) | 2.73 | 2.8 | 2.77 | 2.68 | 2.51 | 2.16 | 1.79 | 1.37 | 0.94 | 0.44 | 0.07 | -0.33 | -0.89 | -1.5 | -2.13 | -5.63 | -7.4 | -7.96
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Consumer Transformation | Thermal headroom (MW) | 43.46 | 37.2424 | 30.5344 | 22.0851 | 10.5467 | -6.3268 | -23.1768 | -44.2115 | -66.462 | -89.7866 | -124.8212 | -160.8921 | -197.8928 | -234.3032 | -269.9611 | -458.0663 | -563.7297 | -617.9362
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Leading the Way | Thermal headroom (MW) | 43.46 | 31.2007 | 17.8453 | 3.3305 | -14.9404 | -40.4595 | -65.5128 | -98.9003 | -132.5925 | -166.6557 | -204.8898 | -245.4871 | -286.7102 | -326.386 | -362.632 | -498.1568 | -548.2264 | -577.0708
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Steady Progression | Thermal headroom (MW) | 43.46 | 41.7481 | 39.8287 | 37.5151 | 33.9243 | 27.0589 | 20.3505 | 10.7006 | 0.87495 | -8.2218 | -21.0155 | -34.444 | -48.2517 | -63.236 | -78.6837 | -177.0807 | -236.8004 | -262.9525
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | System Transformation | Thermal headroom (MW) | 43.46 | 40.6982 | 37.4803 | 33.5891 | 27.4825 | 20.8833 | 13.5935 | 2.1735 | -10.0844 | -22.5996 | -37.7345 | -54.1651 | -72.6151 | -92.0196 | -111.9181 | -220.334 | -267.0476 | -285.6232
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | WPD Best View | Thermal headroom (MW) | 43.46 | 37.2424 | 30.5344 | 22.0851 | 10.5467 | -6.3238 | -23.171 | -44.2033 | -66.4517 | -89.7743 | -124.8098 | -160.8817 | -197.8825 | -234.2936 | -269.9522 | -458.0661 | -563.7234 | -617.9321
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Consumer Transformation | Thermal headroom (MW) | 1 | 0.84 | 0.57 | 0.26 | -0.1 | -0.81 | -1.42 | -2.05 | -2.95 | -3.87 | -5.44 | -6.97 | -8.52 | -9.99 | -11.43 | -20.61 | -26.01 | -28.6
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Leading the Way | Thermal headroom (MW) | 1 | 0.42 | -0.25 | -0.92 | -1.65 | -2.88 | -4.06 | -5.3 | -6.94 | -8.56 | -10.11 | -11.78 | -13.46 | -15.07 | -16.57 | -22.44 | -24.79 | -26.09
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Steady Progression | Thermal headroom (MW) | 1 | 1.04 | 1.02 | 0.95 | 0.87 | 0.59 | 0.32 | 0.04 | -0.37 | -0.85 | -1.43 | -2.02 | -2.61 | -3.2 | -3.83 | -8.31 | -10.9 | -12.15
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | System Transformation | Thermal headroom (MW) | 1 | 0.98 | 0.84 | 0.69 | 0.52 | 0.32 | 0.14 | -0.09 | -0.63 | -1.2 | -1.8 | -2.45 | -3.15 | -3.92 | -4.7 | -9.81 | -12.11 | -12.84
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | WPD Best View | Thermal headroom (MW) | 1 | 0.84 | 0.57 | 0.26 | -0.1 | -0.81 | -1.42 | -2.05 | -2.95 | -3.87 | -5.44 | -6.97 | -8.52 | -9.99 | -11.43 | -20.61 | -26.01 | -28.6
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Consumer Transformation | Thermal headroom (MW) | 20.22 | 19.64 | 19.04 | 18.3 | 17.27 | 15.77 | 14.27 | 12.36 | 10.37 | 8.29 | 5.16 | 1.95 | -1.3 | -4.52 | -7.66 | -23.78 | -32.78 | -37.44
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Leading the Way | Thermal headroom (MW) | 20.22 | 19.12 | 17.95 | 16.68 | 15.06 | 12.83 | 10.65 | 7.67 | 4.72 | 1.74 | -1.64 | -5.21 | -8.85 | -12.34 | -15.53 | -27.31 | -31.57 | -34.06
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Steady Progression | Thermal headroom (MW) | 20.22 | 20.03 | 19.84 | 19.63 | 19.29 | 18.68 | 18.09 | 17.21 | 16.34 | 15.56 | 14.44 | 13.27 | 12.06 | 10.74 | 9.38 | 0.75 | -4.48 | -6.72
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | System Transformation | Thermal headroom (MW) | 20.22 | 19.94 | 19.65 | 19.3 | 18.74 | 18.15 | 17.49 | 16.44 | 15.36 | 14.27 | 12.94 | 11.49 | 9.84 | 8.15 | 6.39 | -3.09 | -7.04 | -8.67
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | WPD Best View | Thermal headroom (MW) | 20.22 | 19.64 | 19.04 | 18.3 | 17.27 | 15.77 | 14.27 | 12.36 | 10.37 | 8.29 | 5.16 | 1.95 | -1.3 | -4.52 | -7.66 | -23.78 | -32.78 | -37.44
Coventry 132kV | Hinckley 33 | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Consumer Transformation | Thermal headroom (MW) | 3.31 | 3.22 | 2.86 | 2.36 | 1.68 | 0.87 | 0.05 | -0.85 | -1.81 | -2.86 | -4.04 | -5.57 | -7.73 | -9.69 | -11.65 | -25.19 | -32.98 | -36.79
Coventry 132kV | Hinckley 33 | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Leading the Way | Thermal headroom (MW) | 3.31 | 3 | 2.39 | 1.65 | 0.7 | -0.69 | -2.17 | -3.8 | -5.41 | -7.11 | -9.14 | -11.46 | -13.79 | -16.02 | -18.11 | -27.09 | -31.19 | -33.32
Coventry 132kV | Hinckley 33 | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Steady Progression | Thermal headroom (MW) | 3.31 | 3.52 | 3.53 | 3.49 | 3.37 | 3.06 | 2.71 | 2.3 | 1.82 | 1.27 | 0.53 | -0.25 | -1.08 | -1.95 | -2.82 | -8.04 | -11.5 | -13.5
Coventry 132kV | Hinckley 33 | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | System Transformation | Thermal headroom (MW) | 3.31 | 3.45 | 3.36 | 3.22 | 2.94 | 2.59 | 2.17 | 1.65 | 1.01 | 0.26 | -0.59 | -1.51 | -2.44 | -3.71 | -4.87 | -10.65 | -14.58 | -15.7
Coventry 132kV | Hinckley 33 | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | WPD Best View | Thermal headroom (MW) | 3.31 | 3.22 | 2.86 | 2.36 | 1.68 | 0.88 | 0.06 | -0.84 | -1.8 | -2.84 | -4.03 | -5.55 | -7.71 | -9.68 | -11.64 | -25.19 | -32.97 | -36.79
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Consumer Transformation | Thermal headroom (MW) | 46.71 | 44.7392 | 41.7028 | 38.0831 | 32.303 | 26.9796 | 21.8439 | 16.2427 | 10.1727 | 3.7597 | -6.722 | -18.2147 | -29.9827 | -41.5998 | -52.7188 | -110.1502 | -147.6463 | -167.6976
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Leading the Way | Thermal headroom (MW) | 46.71 | 43.2138 | 38.5368 | 32.9998 | 24.9231 | 16.7704 | 8.4659 | -0.42692 | -10.2297 | -21.0104 | -33.2641 | -46.2617 | -58.8796 | -70.9534 | -81.7981 | -118.6554 | -135.0637 | -144.3193
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Steady Progression | Thermal headroom (MW) | 46.71 | 46.4336 | 45.3854 | 44.242 | 41.9715 | 39.8938 | 37.7643 | 35.4923 | 32.9221 | 29.9146 | 25.8312 | 21.8622 | 17.4734 | 12.9132 | 8.6185 | -17.2817 | -34.5916 | -42.7019
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | System Transformation | Thermal headroom (MW) | 46.71 | 45.8653 | 44.1508 | 42.191 | 38.82 | 36.5677 | 34.1942 | 31.4585 | 27.9651 | 24.3008 | 19.3148 | 14.0345 | 8.4047 | 2.5466 | -2.8546 | -31.4958 | -46.2346 | -50.906
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | WPD Best View | Thermal headroom (MW) | 46.71 | 43.5191 | 39.1386 | 33.9657 | 26.4376 | 19.2319 | 11.8478 | 3.9175 | -4.8149 | -14.2357 | -25.8776 | -38.2334 | -50.4774 | -62.4475 | -73.4058 | -115.4819 | -136.7065 | -148.0964
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Consumer Transformation | Thermal headroom (MW) | 5.4 | 5.35 | 5.28 | 5.17 | 5.01 | 4.78 | 4.54 | 4.32 | 4.09 | 3.84 | 3.33 | 2.81 | 2.2 | 1.59 | 0.99 | -2.56 | -4.84 | -5.92
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Leading the Way | Thermal headroom (MW) | 5.4 | 5.27 | 5.11 | 4.91 | 4.62 | 4.14 | 3.68 | 3.23 | 2.74 | 2.17 | 1.58 | 0.93 | 0.27 | -0.33 | -0.93 | -3.19 | -4.13 | -4.61
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Steady Progression | Thermal headroom (MW) | 5.4 | 5.44 | 5.45 | 5.45 | 5.43 | 5.33 | 5.22 | 5.1 | 4.97 | 4.81 | 4.59 | 4.37 | 4.14 | 3.9 | 3.66 | 2.11 | 1.12 | 0.63
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | System Transformation | Thermal headroom (MW) | 5.4 | 5.41 | 5.39 | 5.35 | 5.28 | 5.19 | 5.09 | 4.97 | 4.83 | 4.66 | 4.42 | 4.16 | 3.9 | 3.65 | 3.43 | 1.99 | 1.03 | 0.65
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | WPD Best View | Thermal headroom (MW) | 5.4 | 5.35 | 5.28 | 5.17 | 5.01 | 4.78 | 4.54 | 4.32 | 4.09 | 3.84 | 3.33 | 2.81 | 2.2 | 1.59 | 0.99 | -2.56 | -4.84 | -5.92
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Consumer Transformation | Thermal headroom (MW) | 8.33 | 8.31 | 8.17 | 8 | 6.64 | 6.07 | 5.52 | 4.5 | 3.33 | 1.94 | -1.05 | -4.04 | -6.97 | -9.86 | -12.71 | -21.72 | -29.7 | -34.8
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Leading the Way | Thermal headroom (MW) | 8.33 | 8.09 | 7.72 | 7.34 | 5.38 | 4.5 | 3.23 | 1.81 | -0.09 | -2.21 | -4.6 | -7.22 | -9.97 | -12.64 | -15.05 | -20.25 | -22.26 | -22.62
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Steady Progression | Thermal headroom (MW) | 8.33 | 8.53 | 8.62 | 8.71 | 7.83 | 7.7 | 7.53 | 7.33 | 7.08 | 6.53 | 5.79 | 5.21 | 4.42 | 3.58 | 2.77 | -3.27 | -7.98 | -9.58
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | System Transformation | Thermal headroom (MW) | 8.33 | 8.46 | 8.48 | 8.46 | 7.3 | 7.15 | 6.96 | 6.74 | 6.4 | 6.05 | 5.27 | 4.38 | 2.98 | 1.49 | -0.06 | -7.09 | -9.48 | -9.72
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | WPD Best View | Thermal headroom (MW) | 8.33 | 8.09 | 7.72 | 7.34 | 5.38 | 4.5 | 3.23 | 1.81 | -0.09 | -2.21 | -4.6 | -7.22 | -9.97 | -12.64 | -15.05 | -20.25 | -22.26 | -22.62
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Consumer Transformation | Thermal headroom (MW) | 10.94 | 10.04 | 8.94 | 7.76 | 6.72 | 5.71 | 4.68 | 3.64 | 2.64 | 1.65 | 0.12 | -1.77 | -3.73 | -5.62 | -7.46 | -19.34 | -27.46 | -32.52
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Leading the Way | Thermal headroom (MW) | 10.94 | 9.75 | 8.33 | 6.59 | 5.21 | 3.6 | 2.06 | 0.38 | -1.25 | -3.05 | -5.11 | -7.31 | -9.46 | -11.58 | -13.6 | -22.1 | -27.02 | -30.9
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Steady Progression | Thermal headroom (MW) | 10.94 | 10.44 | 9.81 | 9.2 | 8.82 | 8.37 | 7.89 | 7.41 | 6.97 | 6.46 | 5.75 | 5.04 | 4.31 | 3.54 | 2.79 | -1.31 | -4.53 | -6.26
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | System Transformation | Thermal headroom (MW) | 10.94 | 10.29 | 9.49 | 8.69 | 8.12 | 7.67 | 7.23 | 6.72 | 6.04 | 5.36 | 4.49 | 3.57 | 2.64 | 1.74 | 0.97 | -4.2 | -7.61 | -9.25
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | WPD Best View | Thermal headroom (MW) | 10.94 | 9.75 | 8.33 | 6.59 | 5.21 | 3.6 | 2.07 | 0.39 | -1.24 | -3.04 | -5.1 | -7.3 | -9.45 | -11.56 | -13.58 | -22.1 | -27.02 | -30.9
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Consumer Transformation | Thermal headroom (MW) | 7.63 | 7.07 | 6.34 | 5.35 | 3.42 | 1.77 | 0.18 | -1.42 | -3.39 | -5.32 | -7.46 | -9.69 | -11.64 | -14.09 | -16.17 | -26.96 | -31.71 | -33.61
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Leading the Way | Thermal headroom (MW) | 7.63 | 6.87 | 5.93 | 4.76 | 2.64 | 0.58 | -1.64 | -4.02 | -6.94 | -9.79 | -12.82 | -15.95 | -18.74 | -21.29 | -23.14 | -29.64 | -31.74 | -32.56
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Steady Progression | Thermal headroom (MW) | 7.63 | 7.46 | 7.19 | 6.87 | 6.24 | 5.43 | 4.69 | 3.91 | 2.93 | 1.95 | 0.83 | -0.33 | -1.64 | -2.98 | -4.05 | -9.28 | -10.78 | -11.22
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | System Transformation | Thermal headroom (MW) | 7.63 | 7.34 | 6.97 | 6.5 | 5.61 | 4.68 | 3.74 | 2.73 | 1.36 | -0.01 | -1.51 | -3 | -4.34 | -5.68 | -6.75 | -12.06 | -14.11 | -14.34
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | WPD Best View | Thermal headroom (MW) | 7.63 | 6.88 | 5.96 | 4.8 | 2.75 | 0.87 | -1.12 | -3.28 | -5.96 | -8.59 | -11.23 | -14.11 | -16.72 | -19.22 | -21.22 | -28.55 | -31.05 | -32.05
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Consumer Transformation | Thermal headroom (MW) | 9.27 | 9.12 | 8.49 | 7.73 | 6.65 | 5.71 | 4.77 | 3.81 | 2.81 | 1.7 | -0.07 | -1.76 | -3.32 | -4.83 | -6.24 | -13.58 | -18.01 | -20.13
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Leading the Way | Thermal headroom (MW) | 9.27 | 8.77 | 7.71 | 6.47 | 4.94 | 3.69 | 2.41 | 1.04 | -0.36 | -1.95 | -3.81 | -5.72 | -7.32 | -8.9 | -10.3 | -15.01 | -16.76 | -17.52
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Steady Progression | Thermal headroom (MW) | 9.27 | 9.36 | 9.12 | 8.8 | 8.3 | 8.01 | 7.69 | 7.37 | 7.01 | 6.64 | 6.1 | 5.59 | 5.08 | 4.55 | 4.05 | 0.34 | -2.35 | -3.61
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | System Transformation | Thermal headroom (MW) | 9.27 | 9.3 | 8.93 | 8.41 | 7.72 | 7.38 | 6.97 | 6.56 | 6.09 | 5.6 | 4.94 | 4.26 | 3.63 | 2.95 | 2.27 | -2.07 | -3.87 | -4.29
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | WPD Best View | Thermal headroom (MW) | 9.27 | 8.77 | 7.71 | 6.47 | 4.94 | 3.69 | 2.41 | 1.04 | -0.36 | -1.95 | -3.81 | -5.72 | -7.32 | -8.9 | -10.3 | -15.01 | -16.76 | -17.52
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Consumer Transformation | Thermal headroom (MW) | 7.05 | 6.67 | 6.17 | 5.63 | 4.93 | 3.77 | 2.76 | 1.69 | 0.56 | -0.62 | -2.59 | -5.36 | -8.58 | -11.27 | -13.96 | -29.24 | -39.38 | -44.38
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Leading the Way | Thermal headroom (MW) | 7.05 | 6.27 | 5.37 | 4.41 | 3.1 | 1.11 | -0.64 | -2.53 | -4.38 | -6.61 | -9.48 | -12.5 | -15.66 | -18.7 | -21.56 | -31.32 | -35.93 | -38.72
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Steady Progression | Thermal headroom (MW) | 7.05 | 7.07 | 7 | 6.95 | 6.85 | 6.48 | 6.12 | 5.69 | 5.16 | 4.59 | 3.71 | 2.81 | 1.81 | 0.78 | -0.24 | -6 | -10.48 | -13.08
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | System Transformation | Thermal headroom (MW) | 7.05 | 6.93 | 6.7 | 6.49 | 6.2 | 5.76 | 5.33 | 4.73 | 4.01 | 3.21 | 2.03 | 0.76 | -0.59 | -2.2 | -3.7 | -10.01 | -14.05 | -15.45
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | WPD Best View | Thermal headroom (MW) | 7.05 | 6.34 | 5.51 | 4.68 | 3.52 | 1.69 | 0.07 | -1.63 | -3.31 | -5.15 | -7.94 | -10.86 | -13.89 | -16.84 | -19.66 | -30.62 | -36.23 | -39.41
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Consumer Transformation | Thermal headroom (MW) | 65.2416 | 62.8719 | 60.3958 | 56.747 | 51.9164 | 47.6227 | 43.1261 | 38.2584 | 33.1705 | 27.1999 | 18.6928 | 9.8117 | 0.31333 | -8.8224 | -18.0446 | -55.1 | -76.9077 | -88.6435
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Leading the Way | Thermal headroom (MW) | 65.2416 | 62.0634 | 58.6837 | 54.0482 | 48.0187 | 41.8473 | 35.699 | 28.4786 | 20.592 | 11.5123 | 3.2159 | -6.0747 | -15.139 | -24.0299 | -32.3209 | -57.8663 | -64.0039 | -65.6525
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Steady Progression | Thermal headroom (MW) | 65.2416 | 63.7647 | 62.1532 | 59.8155 | 56.8304 | 54.1957 | 51.6618 | 49.0852 | 46.4399 | 42.7743 | 38.9072 | 35.7401 | 32.5011 | 28.9193 | 25.3239 | 2.0305 | -7.1861 | -9.2947
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | System Transformation | Thermal headroom (MW) | 65.2416 | 63.4584 | 61.5628 | 58.7502 | 54.9129 | 52.4246 | 49.65 | 46.5306 | 43.3308 | 39.3847 | 35.1037 | 30.6834 | 26.1739 | 20.9522 | 15.6427 | -10.2566 | -18.3891 | -18.3139
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | WPD Best View | Thermal headroom (MW) | 65.2416 | 62.8788 | 60.4101 | 56.7699 | 51.9516 | 47.6755 | 43.1949 | 38.3408 | 33.264 | 27.316 | 18.8246 | 10.0615 | 0.63105 | -8.4743 | -17.6678 | -55.1789 | -77.3611 | -89.0149
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Consumer Transformation | Thermal headroom (MW) | 10.6 | 9.36 | 8.21 | 6.53 | 4.33 | 2.44 | 0.64 | -1.28 | -3.28 | -5.65 | -9.2 | -12.74 | -16.33 | -19.8 | -23.31 | -35.25 | -43.58 | -48.54
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Leading the Way | Thermal headroom (MW) | 10.6 | 9.04 | 7.52 | 5.43 | 2.74 | 0.12 | -2.19 | -4.93 | -7.98 | -11.57 | -14.53 | -17.75 | -21.01 | -24.21 | -27.17 | -34.96 | -37.03 | -37.69
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Steady Progression | Thermal headroom (MW) | 10.6 | 9.7 | 8.85 | 7.67 | 6.19 | 4.95 | 3.88 | 2.83 | 1.8 | 0.31 | -1.19 | -2.32 | -3.45 | -4.72 | -5.9 | -13.36 | -16.53 | -17.36
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | System Transformation | Thermal headroom (MW) | 10.6 | 9.57 | 8.62 | 7.23 | 5.39 | 4.23 | 3.14 | 1.93 | 0.75 | -0.75 | -2.35 | -3.97 | -5.67 | -7.48 | -9.34 | -17.93 | -20.53 | -20.6
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | WPD Best View | Thermal headroom (MW) | 10.6 | 9.36 | 8.21 | 6.53 | 4.33 | 2.44 | 0.64 | -1.28 | -3.28 | -5.65 | -9.2 | -12.74 | -16.33 | -19.8 | -23.31 | -35.25 | -43.58 | -48.54
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Consumer Transformation | Thermal headroom (MW) | 12.7 | 12.88 | 12.97 | 13.06 | 13.14 | 13.21 | 12.97 | 12.7 | 12.38 | 12.02 | 11.63 | 11.11 | 10.47 | 9.85 | 9.22 | 5.96 | 6.09 | 6.76
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Leading the Way | Thermal headroom (MW) | 12.7 | 12.87 | 12.96 | 13.05 | 13.13 | 13.18 | 12.8 | 12.33 | 11.84 | 11.32 | 10.56 | 9.58 | 8.85 | 8.1 | 7.38 | 4.24 | 4.77 | 5.61
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Steady Progression | Thermal headroom (MW) | 12.7 | 12.88 | 12.98 | 13.08 | 13.17 | 13.25 | 13.16 | 13.02 | 12.85 | 12.63 | 12.38 | 12.09 | 11.77 | 11.42 | 10.91 | 7.15 | 6.71 | 7.39
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | System Transformation | Thermal headroom (MW) | 12.7 | 12.88 | 12.98 | 13.08 | 13.16 | 13.25 | 13.04 | 12.78 | 12.49 | 12.17 | 11.79 | 11.38 | 11.03 | 10.47 | 9.85 | 6.14 | 5.86 | 6.59
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | WPD Best View | Thermal headroom (MW) | 12.7 | 12.88 | 12.98 | 13.08 | 13.17 | 13.25 | 13.03 | 12.76 | 12.45 | 12.11 | 11.73 | 11.3 | 10.72 | 10.12 | 9.51 | 5.9 | 5.72 | 6.46
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Consumer Transformation | Thermal headroom (MW) | 44.0649 | 42.6933 | 40.2918 | 37.1923 | 31.9746 | 21.9078 | 13.5134 | 5.3883 | -3.0307 | -12.1494 | -28.7109 | -46.8198 | -65.8265 | -84.6241 | -103.846 | -178.7348 | -246.8645 | -294.6511
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Leading the Way | Thermal headroom (MW) | 44.0649 | 41.705 | 38.002 | 33.844 | 26.6446 | 11.4605 | -0.73034 | -14.2398 | -34.6525 | -56.8001 | -71.2604 | -89.321 | -109.6253 | -130.2166 | -149.6399 | -216.4627 | -253.4486 | -286.6266
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Steady Progression | Thermal headroom (MW) | 44.0649 | 44.1308 | 43.4905 | 42.7923 | 40.8955 | 35.9202 | 32.4259 | 28.9211 | 25.0332 | 20.49 | 14.5414 | 8.9768 | 2.703 | -3.9228 | -10.6175 | -46.7957 | -59.6538 | -63.6606
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | System Transformation | Thermal headroom (MW) | 44.0649 | 43.7272 | 42.6005 | 41.3013 | 38.4932 | 33.1799 | 29.2704 | 24.9889 | 20.1564 | 14.9979 | 8.3574 | 1.5519 | -5.5842 | -13.0815 | -20.2362 | -58.8379 | -73.6954 | -77.1916
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | WPD Best View | Thermal headroom (MW) | 44.0649 | 44.1599 | 43.5455 | 42.8553 | 40.9311 | 36.547 | 33.622 | 30.5143 | 26.7183 | 22.1088 | 16.3048 | 10.852 | 4.8829 | -1.5016 | -7.931 | -42.8756 | -58.8198 | -63.2805
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Consumer Transformation | Thermal headroom (MW) | 4.17 | 3.83 | 3.24 | 2.58 | 1.67 | 0.44 | -0.77 | -2.06 | -3.42 | -4.59 | -6.04 | -7.86 | -10.25 | -12.38 | -14.42 | -26.94 | -35.34 | -39.49
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Leading the Way | Thermal headroom (MW) | 4.17 | 3.53 | 2.61 | 1.67 | 0.44 | -1.49 | -3.36 | -5.41 | -7.63 | -9.66 | -11.84 | -14.32 | -16.86 | -19.36 | -21.65 | -30.32 | -35.03 | -37.97
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Steady Progression | Thermal headroom (MW) | 4.17 | 4.2 | 4.07 | 3.94 | 3.72 | 3.27 | 2.8 | 2.25 | 1.59 | 0.85 | -0.1 | -0.97 | -1.89 | -2.87 | -3.8 | -9.16 | -12.46 | -14.44
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | System Transformation | Thermal headroom (MW) | 4.17 | 4.06 | 3.78 | 3.46 | 3.04 | 2.57 | 2.03 | 1.28 | 0.39 | -0.43 | -1.55 | -2.58 | -3.73 | -5.1 | -6.44 | -11.77 | -16.08 | -17.68
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | WPD Best View | Thermal headroom (MW) | 4.17 | 4.2 | 4.06 | 3.93 | 3.7 | 3.24 | 2.74 | 2.17 | 1.49 | 0.83 | -0.04 | -0.89 | -1.78 | -2.69 | -3.58 | -8.71 | -12.28 | -14.31
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Consumer Transformation | Thermal headroom (MW) | 6.04 | 5.46 | 4.59 | 3.58 | 2.38 | 0.21 | -2.47 | -4.61 | -6.82 | -9.2 | -17.09 | -25.67 | -34.5 | -43.27 | -52.57 | -81.72 | -132.65 | -173.42
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Leading the Way | Thermal headroom (MW) | 6.04 | 5.05 | 3.72 | 2.28 | 0.04 | -3.89 | -8.72 | -13.72 | -24.92 | -37.28 | -42.28 | -50.2 | -60.68 | -71.79 | -82.16 | -112.81 | -144.23 | -176.53
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Steady Progression | Thermal headroom (MW) | 6.04 | 5.98 | 5.73 | 5.48 | 5.18 | 4.48 | 3.45 | 2.67 | 1.75 | 0.77 | -0.47 | -1.73 | -3.13 | -4.61 | -5.94 | -12.65 | -16.86 | -18.84
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | System Transformation | Thermal headroom (MW) | 6.04 | 5.83 | 5.41 | 4.95 | 4.43 | 3.67 | 2.27 | 1.19 | -0.1 | -1.36 | -2.84 | -4.41 | -6 | -7.58 | -8.88 | -16.67 | -20.74 | -22.71
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | WPD Best View | Thermal headroom (MW) | 6.04 | 5.98 | 5.73 | 5.48 | 5.18 | 4.48 | 3.45 | 2.67 | 1.75 | 0.77 | -0.47 | -1.73 | -3.13 | -4.61 | -5.94 | -12.65 | -16.86 | -18.84
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Consumer Transformation | Thermal headroom (MW) | 3.82 | 3.67 | 3.34 | 2.9 | 2.35 | 1.45 | 0.57 | -0.38 | -1.38 | -2.86 | -5.88 | -9.49 | -13.1 | -16.57 | -20.12 | -33.24 | -45.66 | -53.79
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Leading the Way | Thermal headroom (MW) | 3.82 | 3.43 | 2.82 | 2.13 | 1.26 | -0.09 | -1.44 | -3.12 | -5.89 | -8.92 | -11.76 | -14.96 | -18.29 | -21.58 | -24.65 | -33.07 | -37.16 | -39.83
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Steady Progression | Thermal headroom (MW) | 3.82 | 4.01 | 4.04 | 4.05 | 4.03 | 3.79 | 3.54 | 3.21 | 2.78 | 1.86 | 0.67 | -0.06 | -0.85 | -1.81 | -2.99 | -8.91 | -13.82 | -15.73
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | System Transformation | Thermal headroom (MW) | 3.82 | 3.92 | 3.84 | 3.71 | 3.52 | 3.31 | 3.05 | 2.62 | 2.09 | 1.45 | 0.29 | -0.97 | -2.26 | -3.52 | -4.7 | -12.18 | -15.45 | -16.45
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | WPD Best View | Thermal headroom (MW) | 3.82 | 4.01 | 4.04 | 4.05 | 4.03 | 3.79 | 3.54 | 3.21 | 2.78 | 1.86 | 0.67 | -0.06 | -0.85 | -1.81 | -2.99 | -8.91 | -13.82 | -15.73
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Consumer Transformation | Thermal headroom (MW) | 26.96 | 26.65 | 26.2 | 25.65 | 24.99 | 23.95 | 22.83 | 21.56 | 20.4 | 19.15 | 17.21 | 15.2 | 13.25 | 11.31 | 9.43 | -0.7 | -7.8 | -12.49
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Leading the Way | Thermal headroom (MW) | 26.96 | 26.19 | 25.24 | 24.34 | 23.27 | 21.71 | 20.11 | 18.08 | 16.32 | 14.42 | 12.34 | 10.19 | 8.01 | 5.92 | 4.02 | -3.4 | -7.51 | -10.74
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Steady Progression | Thermal headroom (MW) | 26.96 | 26.98 | 26.94 | 26.84 | 26.73 | 26.43 | 26.09 | 25.62 | 25.25 | 24.82 | 24.25 | 23.63 | 23.01 | 22.38 | 21.69 | 16.85 | 13.37 | 11.73
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | System Transformation | Thermal headroom (MW) | 26.96 | 26.89 | 26.69 | 26.47 | 26.17 | 25.87 | 25.49 | 24.81 | 24.24 | 23.67 | 23.02 | 22.28 | 21.53 | 20.71 | 19.82 | 14.45 | 11.25 | 9.32
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | WPD Best View | Thermal headroom (MW) | 26.96 | 26.98 | 26.94 | 26.84 | 26.73 | 26.4 | 26.03 | 25.53 | 25.13 | 24.67 | 24.07 | 23.43 | 22.79 | 22.15 | 21.43 | 16.26 | 12.71 | 10.9
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Consumer Transformation | Thermal headroom (MW) | 63.82 | 62.7543 | 60.9551 | 58.6034 | 55.3867 | 51.5401 | 47.4032 | 43.3083 | 38.9634 | 33.3392 | 25.7672 | 17.6714 | 9.5443 | 1.6978 | -5.9185 | -40.9798 | -60.4439 | -71.1218
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Leading the Way | Thermal headroom (MW) | 63.82 | 61.8235 | 58.9254 | 55.5065 | 50.9736 | 45.4874 | 39.8542 | 33.771 | 27.0626 | 18.8833 | 10.2793 | 1.2215 | -7.146 | -15.1441 | -22.5977 | -45.3315 | -52.3401 | -54.4977
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Steady Progression | Thermal headroom (MW) | 63.82 | 63.7694 | 63.1797 | 62.2263 | 60.8139 | 59.1066 | 57.4209 | 55.6547 | 53.7322 | 51.2786 | 48.2017 | 45.2199 | 42.1181 | 38.9265 | 35.7776 | 14.4248 | 1.7272 | -2.7724
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | System Transformation | Thermal headroom (MW) | 63.82 | 63.3834 | 62.345 | 60.8506 | 58.715 | 56.8148 | 54.6677 | 52.3512 | 49.628 | 46.3069 | 42.7839 | 38.9483 | 34.9054 | 30.8534 | 26.6502 | 4.9248 | -2.9433 | -3.54
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | WPD Best View | Thermal headroom (MW) | 63.82 | 62.8913 | 61.2304 | 59.0249 | 56.0296 | 52.3599 | 48.3779 | 44.4585 | 40.3462 | 35.0323 | 27.7888 | 20.0751 | 12.1651 | 4.5548 | -2.7965 | -36.7089 | -55.8154 | -66.0748
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Consumer Transformation | Thermal headroom (MW) | 8.126 | 8.066 | 7.906 | 7.646 | 7.236 | 6.446 | 5.646 | 4.696 | 3.786 | 2.766 | 0.416 | -2.084 | -5.084 | -7.994 | -10.964 | -22.784 | -33.604 | -40.524
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Leading the Way | Thermal headroom (MW) | 8.126 | 7.846 | 7.406 | 6.916 | 6.186 | 5.066 | 3.936 | 2.506 | 0.886 | -0.914 | -3.354 | -6.034 | -8.874 | -11.714 | -14.414 | -22.574 | -27.044 | -29.834
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Steady Progression | Thermal headroom (MW) | 8.126 | 8.336 | 8.446 | 8.506 | 8.516 | 8.366 | 8.186 | 7.866 | 7.496 | 6.776 | 5.836 | 5.196 | 4.476 | 3.636 | 2.876 | -2.404 | -6.404 | -8.924
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | System Transformation | Thermal headroom (MW) | 8.126 | 8.256 | 8.266 | 8.216 | 8.076 | 7.886 | 7.616 | 7.156 | 6.636 | 6.006 | 5.176 | 4.256 | 2.946 | 1.676 | 0.346 | -5.544 | -9.034 | -10.054
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | WPD Best View | Thermal headroom (MW) | 8.126 | 8.106 | 7.976 | 7.766 | 7.416 | 6.696 | 5.936 | 5.046 | 4.186 | 3.236 | 0.936 | -1.324 | -4.184 | -6.964 | -9.814 | -21.034 | -31.694 | -38.654
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Consumer Transformation | Thermal headroom (MW) | 11.7 | 11.69 | 11.55 | 11.36 | 11.05 | 10.54 | 10.13 | 9.67 | 9.17 | 8.33 | 7.03 | 5.67 | 4.35 | 3.07 | 1.87 | -3.27 | -5.09 | -6.27
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Leading the Way | Thermal headroom (MW) | 11.7 | 11.52 | 11.21 | 10.84 | 10.36 | 9.85 | 9.42 | 8.73 | 7.81 | 6.85 | 5.51 | 4.15 | 2.78 | 1.53 | 0.42 | -2.13 | -2.6 | -2.15
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Steady Progression | Thermal headroom (MW) | 11.7 | 11.87 | 11.92 | 11.96 | 11.97 | 11.86 | 11.77 | 11.65 | 11.5 | 11.34 | 11.08 | 10.81 | 10.52 | 10.19 | 9.87 | 6.74 | 4.12 | 3.12
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | System Transformation | Thermal headroom (MW) | 11.7 | 11.79 | 11.77 | 11.71 | 11.62 | 11.51 | 11.43 | 11.32 | 11.18 | 10.97 | 10.62 | 10.21 | 9.79 | 9.37 | 8.77 | 5.81 | 4.95 | 5.14
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | WPD Best View | Thermal headroom (MW) | 11.7 | 11.69 | 11.55 | 11.36 | 11.05 | 10.54 | 10.13 | 9.67 | 9.17 | 8.33 | 7.03 | 5.67 | 4.35 | 3.07 | 1.87 | -3.27 | -5.09 | -6.27
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Consumer Transformation | Thermal headroom (MW) | 18.33 | 18.21 | 18.01 | 17.8 | 17.57 | 17.3 | 16.85 | 16.44 | 15.96 | 15.38 | 14.85 | 14.31 | 13.76 | 13.24 | 12.78 | 11.42 | 10.99 | 10.83
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Leading the Way | Thermal headroom (MW) | 18.33 | 18.17 | 17.88 | 17.63 | 17.34 | 17.08 | 16.59 | 16.05 | 15.45 | 14.69 | 14.15 | 13.58 | 13.03 | 12.53 | 12.09 | 11.45 | 11.64 | 12.06
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Steady Progression | Thermal headroom (MW) | 18.33 | 18.32 | 18.29 | 18.24 | 18.19 | 18.13 | 18.04 | 17.96 | 17.88 | 17.78 | 17.59 | 17.42 | 17.21 | 17.01 | 16.83 | 15.46 | 14.62 | 14.53
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | System Transformation | Thermal headroom (MW) | 18.33 | 18.29 | 18.23 | 18.15 | 18.06 | 17.99 | 17.87 | 17.7 | 17.47 | 17.21 | 17.02 | 16.76 | 16.44 | 16.08 | 15.76 | 14.36 | 14.19 | 14.36
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | WPD Best View | Thermal headroom (MW) | 18.33 | 18.21 | 18.01 | 17.8 | 17.57 | 17.3 | 16.85 | 16.44 | 15.96 | 15.38 | 14.85 | 14.31 | 13.76 | 13.24 | 12.78 | 11.42 | 10.99 | 10.83
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Consumer Transformation | Thermal headroom (MW) | 12.31 | 11.61 | 10.78 | 10.02 | 8.62 | 7.57 | 6.68 | 5.74 | 4.72 | 3.56 | 2.25 | 0.95 | -0.08 | -1.09 | -2.15 | -8.03 | -9.12 | -8.96
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Leading the Way | Thermal headroom (MW) | 12.31 | 11.41 | 10.4 | 9.41 | 7.68 | 6.18 | 5.01 | 3.74 | 2.38 | 0.9 | -0.67 | -2.34 | -3.46 | -4.62 | -5.74 | -10.4 | -10.32 | -9.5
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Steady Progression | Thermal headroom (MW) | 12.31 | 11.74 | 11.05 | 10.42 | 9.32 | 8.49 | 7.84 | 7.18 | 6.49 | 5.77 | 4.94 | 4.04 | 3.19 | 2.39 | 1.57 | -3.75 | -5.12 | -4.52
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | System Transformation | Thermal headroom (MW) | 12.31 | 11.63 | 10.83 | 10.09 | 8.76 | 7.81 | 7.02 | 6.2 | 5.29 | 4.29 | 3.25 | 2.21 | 1.41 | 0.55 | -0.34 | -5.68 | -6.65 | -5.77
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | WPD Best View | Thermal headroom (MW) | 12.31 | 11.73 | 11.04 | 10.4 | 9.2 | 8.3 | 7.56 | 6.78 | 5.97 | 5.11 | 4.12 | 3.09 | 2.21 | 1.37 | 0.51 | -4.5 | -5.3 | -4.65
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Consumer Transformation | Thermal headroom (MW) | 19.85 | 19.76 | 19.35 | 18.06 | 16.8 | 15.43 | 13.99 | 12.4 | 10.77 | 8.04 | 4.32 | 0.58 | -2.89 | -6.15 | -9.27 | -24.87 | -33.27 | -37.25
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Leading the Way | Thermal headroom (MW) | 19.85 | 19.29 | 18.36 | 16.46 | 14.44 | 12.1 | 9.82 | 7.1 | 4.1 | -0.22 | -4.2 | -8.36 | -11.91 | -15.09 | -18.15 | -27.24 | -29.75 | -29.93
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Steady Progression | Thermal headroom (MW) | 19.85 | 20.1 | 20.11 | 19.5 | 18.88 | 18.21 | 17.54 | 16.83 | 16.02 | 14.83 | 13.57 | 12.28 | 10.97 | 9.62 | 8.21 | -0.88 | -6.42 | -8.75
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | System Transformation | Thermal headroom (MW) | 19.85 | 19.96 | 19.81 | 18.89 | 17.95 | 17.23 | 16.44 | 15.51 | 14.45 | 12.78 | 11.23 | 9.58 | 7.87 | 6.27 | 4.67 | -4.1 | -7.07 | -7.5
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | WPD Best View | Thermal headroom (MW) | 19.85 | 19.76 | 19.35 | 18.06 | 16.8 | 15.43 | 13.99 | 12.4 | 10.77 | 8.04 | 4.32 | 0.58 | -2.89 | -6.15 | -9.27 | -24.87 | -33.27 | -37.25
Drakelow 132kV | Burton 132 11 (GT1A1) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Consumer Transformation | Thermal headroom (MW) | 55.95 | 55.28 | 54.28 | 53.07 | 51.58 | 49.21 | 46.85 | 44.35 | 41.72 | 38.76 | 32.71 | 26.96 | 21.05 | 15.29 | 9.51 | -16.73 | -38.33 | -51.06
Drakelow 132kV | Burton 132 11 (GT1A1) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Leading the Way | Thermal headroom (MW) | 55.95 | 54.04 | 51.84 | 49.5 | 46.78 | 43.24 | 39.74 | 35.67 | 31.12 | 26.15 | 20.43 | 14.71 | 8.88 | 3.14 | -2.37 | -19.48 | -28.38 | -33.88
Drakelow 132kV | Burton 132 11 (GT1A1) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Steady Progression | Thermal headroom (MW) | 55.95 | 56.01 | 55.84 | 55.62 | 55.36 | 54.57 | 53.75 | 52.81 | 51.82 | 50.43 | 48.49 | 47.02 | 45.43 | 43.63 | 41.94 | 29.57 | 20.15 | 15.28
Drakelow 132kV | Burton 132 11 (GT1A1) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | System Transformation | Thermal headroom (MW) | 55.95 | 55.76 | 55.27 | 54.69 | 53.99 | 53.12 | 52.22 | 51.11 | 49.93 | 48.58 | 46.46 | 44.25 | 41.9 | 39.41 | 36.82 | 22.95 | 15.86 | 12.79
Drakelow 132kV | Burton 132 11 (GT1A1) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | WPD Best View | Thermal headroom (MW) | 55.95 | 55.75 | 55.25 | 54.65 | 53.94 | 53.05 | 52.14 | 51.02 | 49.82 | 48.46 | 46.31 | 44.08 | 41.7 | 39.18 | 36.56 | 22.54 | 15.34 | 12.2
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Consumer Transformation | Thermal headroom (MW) | 49.4 | 48.2204 | 46.5792 | 44.5714 | 40.4332 | 35.4813 | 30.4014 | 25.294 | 19.5079 | 13.1413 | 5.1476 | -3.4946 | -12.7444 | -21.46 | -30.2185 | -78.437 | -105.4939 | -120.981
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Leading the Way | Thermal headroom (MW) | 49.4 | 47.2789 | 44.6294 | 41.8004 | 36.299 | 28.6618 | 21.1909 | 13.2291 | 4.2285 | -5.5609 | -15.5591 | -25.5913 | -35.7952 | -45.7306 | -54.967 | -91.0095 | -105.6823 | -115.1877
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Steady Progression | Thermal headroom (MW) | 49.4 | 49.4022 | 48.9896 | 48.5146 | 46.5576 | 44.2009 | 41.9489 | 39.6998 | 37.1785 | 34.3479 | 30.7962 | 27.1395 | 22.9584 | 18.6951 | 14.3284 | -13.2074 | -27.0766 | -31.0103
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | System Transformation | Thermal headroom (MW) | 49.4 | 49.0585 | 48.3034 | 47.3569 | 44.6217 | 42.2614 | 39.723 | 36.7538 | 32.9021 | 28.9342 | 24.3755 | 19.8034 | 15.0174 | 9.6527 | 4.2424 | -24.4139 | -38.7285 | -42.7609
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | WPD Best View | Thermal headroom (MW) | 49.4 | 48.5326 | 47.2212 | 45.5937 | 41.9449 | 37.7678 | 33.5853 | 29.3897 | 24.4966 | 19.1892 | 12.8856 | 5.6675 | -2.1395 | -10.0186 | -18.0047 | -64.2807 | -89.3724 | -102.5883
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Consumer Transformation | Thermal headroom (MW) | 1.32 | 1.27 | 1.09 | 0.85 | 0.49 | -0.13 | -0.76 | -1.46 | -2.25 | -3.11 | -4.54 | -6.31 | -8.12 | -9.9 | -11.63 | -21.85 | -28.46 | -31.82
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Leading the Way | Thermal headroom (MW) | 1.32 | 1.04 | 0.62 | 0 | -0.78 | -1.99 | -3.17 | -4.44 | -5.9 | -7.61 | -9.48 | -11.42 | -13.44 | -15.4 | -17.25 | -24.28 | -27.72 | -29.75
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Steady Progression | Thermal headroom (MW) | 1.32 | 1.48 | 1.52 | 1.54 | 1.53 | 1.32 | 1.08 | 0.75 | 0.37 | -0.05 | -0.65 | -1.28 | -1.96 | -2.67 | -3.38 | -7.8 | -11.62 | -13.12
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | System Transformation | Thermal headroom (MW) | 1.32 | 1.43 | 1.4 | 1.34 | 1.24 | 1.03 | 0.73 | 0.35 | -0.12 | -0.71 | -1.48 | -2.3 | -3.12 | -3.9 | -4.76 | -9.56 | -12.84 | -14.03
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | WPD Best View | Thermal headroom (MW) | 1.32 | 1.3 | 1.15 | 0.94 | 0.63 | 0.06 | -0.54 | -1.2 | -1.94 | -2.79 | -3.95 | -5.52 | -7.15 | -8.74 | -10.32 | -19.88 | -26.12 | -29.15
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Consumer Transformation | Thermal headroom (MW) | 12.45 | 11.96 | 11.23 | 10.39 | 9.38 | 8.62 | 7.95 | 7.24 | 6.48 | 5.65 | 4.65 | 3.83 | 2.75 | 1.63 | 0.11 | -9.95 | -16.42 | -19.54
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Leading the Way | Thermal headroom (MW) | 12.45 | 11.73 | 10.76 | 10.1 | 9.24 | 8.09 | 6.97 | 5.77 | 4.45 | 3.04 | 1.74 | 0.44 | -1.26 | -3.07 | -4.8 | -11.47 | -14.34 | -15.96
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Steady Progression | Thermal headroom (MW) | 12.45 | 12.31 | 11.96 | 11.62 | 11.24 | 10.61 | 9.96 | 9.64 | 9.25 | 8.8 | 8.19 | 7.56 | 6.88 | 6.15 | 5.43 | 1.28 | -0.22 | -1.12
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | System Transformation | Thermal headroom (MW) | 12.45 | 12.21 | 11.75 | 11.29 | 10.73 | 10.52 | 10.28 | 9.95 | 9.51 | 8.99 | 8.33 | 7.6 | 6.86 | 6.15 | 5.56 | 2.5 | 0.11 | -0.41
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | WPD Best View | Thermal headroom (MW) | 12.45 | 12.04 | 11.39 | 10.67 | 9.78 | 9.18 | 8.64 | 8.04 | 7.37 | 6.64 | 5.75 | 4.95 | 4.26 | 3.4 | 2.43 | -5.98 | -11.22 | -13.52
Drakelow 132kV | Burton 33 | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Consumer Transformation | Thermal headroom (MW) | 8.98 | 8.95 | 8.83 | 8.64 | 8.25 | 7.77 | 7.18 | 6.5 | 5.68 | 4.66 | 3.36 | 2.18 | 0.97 | -0.12 | -1.14 | -4.49 | -5.15 | -5.18
Drakelow 132kV | Burton 33 | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Leading the Way | Thermal headroom (MW) | 8.98 | 8.85 | 8.61 | 8.32 | 7.75 | 7.24 | 6.54 | 5.62 | 4.56 | 3.34 | 1.98 | 0.71 | -0.52 | -1.61 | -2.49 | -4.17 | -3.4 | -1.75
Drakelow 132kV | Burton 33 | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Steady Progression | Thermal headroom (MW) | 8.98 | 9.13 | 9.19 | 9.25 | 9.16 | 9.11 | 9 | 8.82 | 8.64 | 8.39 | 8.03 | 7.65 | 7.24 | 6.77 | 6.23 | 2.63 | 0.19 | -0.26
Drakelow 132kV | Burton 33 | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | System Transformation | Thermal headroom (MW) | 8.98 | 9.1 | 9.14 | 9.12 | 8.92 | 8.8 | 8.63 | 8.37 | 7.99 | 7.53 | 6.97 | 6.41 | 5.7 | 4.89 | 4.03 | -0.18 | -0.86 | 0.04
Drakelow 132kV | Burton 33 | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | WPD Best View | Thermal headroom (MW) | 8.98 | 9.1 | 9.14 | 9.12 | 8.92 | 8.8 | 8.63 | 8.37 | 7.99 | 7.53 | 6.97 | 6.41 | 5.7 | 4.89 | 4.03 | -0.18 | -0.86 | 0.04
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Consumer Transformation | Thermal headroom (MW) | 6.36 | 6.34 | 6.3 | 6.22 | 6.11 | 5.82 | 5.5 | 5.21 | 4.85 | 4.45 | 4.06 | 3.68 | 3.21 | 2.69 | 2.16 | -1 | -3.71 | -6.13
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Leading the Way | Thermal headroom (MW) | 6.36 | 6.32 | 6.23 | 6.13 | 5.98 | 5.52 | 5.05 | 4.58 | 4.03 | 3.46 | 2.89 | 2.24 | 1.58 | 0.92 | 0.32 | -2.46 | -4.75 | -7.14
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Steady Progression | Thermal headroom (MW) | 6.36 | 6.41 | 6.42 | 6.42 | 6.41 | 6.33 | 6.24 | 6.15 | 6.03 | 5.89 | 5.73 | 5.56 | 5.38 | 5.19 | 5 | 3.69 | 2.91 | 2.61
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | System Transformation | Thermal headroom (MW) | 6.36 | 6.39 | 6.39 | 6.37 | 6.34 | 6.27 | 6.18 | 6.03 | 5.78 | 5.58 | 5.37 | 5.15 | 4.92 | 4.7 | 4.49 | 3.18 | 1.5 | 0.38
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | WPD Best View | Thermal headroom (MW) | 6.36 | 6.34 | 6.3 | 6.22 | 6.11 | 5.82 | 5.5 | 5.21 | 4.85 | 4.45 | 4.06 | 3.68 | 3.21 | 2.69 | 2.16 | -1 | -3.71 | -6.13
Drakelow 132kV | Burton 33 | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Consumer Transformation | Thermal headroom (MW) | 11.816 | 10.546 | 9.546 | 8.456 | 4.146 | 0.116 | -3.984 | -8.034 | -12.414 | -16.964 | -22.144 | -26.784 | -31.604 | -36.104 | -40.664 | -63.554 | -67.274 | -66.184
Drakelow 132kV | Burton 33 | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Leading the Way | Thermal headroom (MW) | 11.816 | 10.066 | 8.646 | 7.106 | 1.536 | -4.294 | -9.624 | -15.064 | -20.894 | -26.844 | -32.744 | -37.784 | -42.604 | -47.404 | -52.054 | -71.564 | -71.224 | -68.044
Drakelow 132kV | Burton 33 | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Steady Progression | Thermal headroom (MW) | 11.816 | 11.016 | 10.466 | 9.936 | 6.776 | 4.096 | 1.906 | -0.384 | -2.824 | -5.324 | -8.164 | -10.974 | -14.534 | -17.974 | -21.554 | -41.884 | -44.604 | -42.914
Drakelow 132kV | Burton 33 | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | System Transformation | Thermal headroom (MW) | 11.816 | 10.786 | 10.086 | 9.316 | 5.466 | 2.196 | -0.934 | -3.994 | -7.414 | -10.864 | -14.444 | -17.654 | -21.044 | -24.964 | -29.034 | -49.264 | -50.694 | -47.954
Drakelow 132kV | Burton 33 | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | WPD Best View | Thermal headroom (MW) | 11.816 | 10.786 | 10.086 | 9.316 | 5.466 | 2.206 | -0.934 | -3.984 | -7.404 | -10.844 | -14.434 | -17.644 | -21.034 | -24.954 | -29.024 | -49.244 | -50.674 | -47.934
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Consumer Transformation | Thermal headroom (MW) | 10.03 | 9.79 | 9.37 | 8.87 | 8.21 | 7.52 | 6.88 | 6.23 | 5.57 | 4.8 | 3.59 | 1.58 | -0.45 | -1.99 | -3.49 | -12.22 | -17.8 | -20.41
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Leading the Way | Thermal headroom (MW) | 10.03 | 9.58 | 8.94 | 8.36 | 7.59 | 6.41 | 5.31 | 4.12 | 2.7 | 1.09 | -0.58 | -2.35 | -4.12 | -5.79 | -7.34 | -13.07 | -15.67 | -16.82
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Steady Progression | Thermal headroom (MW) | 10.03 | 10.01 | 9.85 | 9.68 | 9.46 | 9.11 | 8.78 | 8.55 | 8.29 | 7.94 | 7.44 | 6.93 | 6.38 | 5.8 | 5.23 | 1.04 | -2.09 | -3.37
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | System Transformation | Thermal headroom (MW) | 10.03 | 9.94 | 9.69 | 9.42 | 9.09 | 8.86 | 8.63 | 8.35 | 7.95 | 7.48 | 6.87 | 6.19 | 5.53 | 4.53 | 3.61 | -1.36 | -4.06 | -4.72
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | WPD Best View | Thermal headroom (MW) | 10.03 | 9.79 | 9.37 | 8.87 | 8.21 | 7.52 | 6.88 | 6.23 | 5.57 | 4.8 | 3.59 | 1.58 | -0.45 | -1.99 | -3.49 | -12.22 | -17.8 | -20.41
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Consumer Transformation | Thermal headroom (MW) | 81.9423 | 81.3398 | 80.5471 | 79.4801 | 77.1987 | 74.8766 | 72.5146 | 70.0777 | 67.218 | 64.0795 | 59.9258 | 56.021 | 52.0097 | 48.2139 | 44.5081 | 25.6063 | 18.5067 | 16.0588
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Leading the Way | Thermal headroom (MW) | 81.9423 | 80.7358 | 79.3143 | 77.7351 | 74.6087 | 71.1098 | 67.7442 | 64.1146 | 59.9948 | 55.5969 | 51.023 | 46.7087 | 42.549 | 38.5388 | 34.794 | 21.0217 | 19.0322 | 19.59
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Steady Progression | Thermal headroom (MW) | 81.9423 | 81.8509 | 81.5832 | 81.199 | 79.8629 | 78.607 | 77.489 | 76.3564 | 75.1405 | 73.7931 | 72.1184 | 70.4323 | 68.4235 | 66.3929 | 64.2563 | 51.0864 | 46.4635 | 45.9861
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | System Transformation | Thermal headroom (MW) | 81.9423 | 81.6978 | 81.2761 | 80.6471 | 78.8731 | 77.5298 | 76.2215 | 74.7872 | 73.0424 | 71.2126 | 69.0651 | 66.9844 | 64.731 | 62.1844 | 59.5372 | 45.6493 | 42.5539 | 43.2282
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | WPD Best View | Thermal headroom (MW) | 81.9423 | 81.5978 | 81.0572 | 80.2899 | 78.3884 | 76.7454 | 75.1542 | 73.4828 | 71.3865 | 69.1776 | 66.3898 | 63.6832 | 60.8329 | 57.7294 | 54.5901 | 37.7815 | 32.6874 | 32.1224
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Consumer Transformation | Thermal headroom (MW) | 11.96 | 12.03 | 11.93 | 11.65 | 11.54 | 11.33 | 11.16 | 10.96 | 10.75 | 10.48 | 10.01 | 9.55 | 9.04 | 8.53 | 8.04 | 4.99 | 3.17 | 2.41
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Leading the Way | Thermal headroom (MW) | 11.96 | 11.87 | 11.6 | 11.11 | 10.84 | 10.41 | 10.03 | 9.64 | 9.19 | 8.69 | 8.21 | 7.67 | 7.13 | 6.64 | 6.11 | 4.14 | 3.39 | 3.07
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Steady Progression | Thermal headroom (MW) | 11.96 | 12.13 | 12.13 | 11.99 | 12.03 | 11.97 | 11.92 | 11.86 | 11.8 | 11.69 | 11.53 | 11.38 | 11.2 | 11.02 | 10.84 | 9.41 | 8.79 | 8.63
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | System Transformation | Thermal headroom (MW) | 11.96 | 12.11 | 12.06 | 11.87 | 11.86 | 11.85 | 11.84 | 11.79 | 11.73 | 11.66 | 11.49 | 11.27 | 11.05 | 10.84 | 10.63 | 9.15 | 8.54 | 8.41
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | WPD Best View | Thermal headroom (MW) | 11.96 | 12.1 | 12.04 | 11.83 | 11.82 | 11.79 | 11.77 | 11.71 | 11.64 | 11.56 | 11.34 | 11.08 | 10.82 | 10.57 | 10.31 | 8.56 | 7.74 | 7.52
Drakelow 132kV | Burton South | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Consumer Transformation | Thermal headroom (MW) | 27.08 | 26.62 | 25.97 | 25.22 | 24.18 | 23.15 | 22.18 | 21.19 | 19.72 | 18.15 | 15.56 | 12.96 | 10.37 | 7.85 | 5.45 | -8.78 | -17.49 | -22.35
Drakelow 132kV | Burton South | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Leading the Way | Thermal headroom (MW) | 27.08 | 26.07 | 24.84 | 23.81 | 22.4 | 20.58 | 18.85 | 16.95 | 14.58 | 11.98 | 9.13 | 6.17 | 3.34 | 0.54 | -2.02 | -11.81 | -16.23 | -19.21
Drakelow 132kV | Burton South | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Steady Progression | Thermal headroom (MW) | 27.08 | 26.96 | 26.7 | 26.41 | 25.91 | 25.31 | 24.75 | 24.34 | 23.86 | 23.32 | 22.57 | 21.78 | 20.94 | 20.04 | 19.12 | 13.09 | 9.52 | 8.09
Drakelow 132kV | Burton South | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | System Transformation | Thermal headroom (MW) | 27.08 | 26.87 | 26.5 | 26.07 | 25.35 | 25.04 | 24.77 | 24.37 | 23.75 | 23.09 | 22.17 | 21.19 | 20.17 | 19.04 | 17.87 | 11.12 | 7.42 | 5.75
Drakelow 132kV | Burton South | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | WPD Best View | Thermal headroom (MW) | 27.08 | 26.66 | 26.05 | 25.33 | 24.34 | 23.39 | 22.51 | 21.6 | 20.2 | 18.71 | 16.43 | 14.12 | 11.85 | 9.55 | 7.35 | -5.43 | -13.22 | -17.49
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Consumer Transformation | Thermal headroom (MW) | 73.656 | 73.1952 | 72.1637 | 69.1699 | 67.0364 | 64.5236 | 61.6792 | 58.9648 | 54.5068 | 50.963 | 45.5755 | 40.0124 | 34.4253 | 28.9762 | 23.847 | -4.8666 | -21.0984 | -29.3534
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Leading the Way | Thermal headroom (MW) | 73.656 | 72.2626 | 70.2299 | 66.0691 | 62.9399 | 58.6894 | 54.0666 | 49.3532 | 41.6158 | 35.6914 | 30.169 | 24.2832 | 18.405 | 12.7356 | 7.656 | -11.116 | -18.6098 | -23.0533
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Steady Progression | Thermal headroom (MW) | 73.656 | 73.7485 | 73.4071 | 71.5006 | 70.4745 | 69.1361 | 67.5747 | 66.2287 | 64.0508 | 62.3754 | 60.1294 | 57.9143 | 55.6505 | 53.3071 | 50.9708 | 35.9355 | 29.1623 | 26.9206
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | System Transformation | Thermal headroom (MW) | 73.656 | 73.6024 | 73.0586 | 70.6658 | 69.232 | 68.4526 | 67.216 | 65.9682 | 63.2042 | 61.4701 | 59.2634 | 56.9231 | 54.5276 | 52.0206 | 49.5705 | 33.8492 | 25.921 | 23.3877
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | WPD Best View | Thermal headroom (MW) | 73.656 | 73.2286 | 72.2317 | 69.2726 | 67.18 | 64.768 | 62.0387 | 59.4328 | 55.0909 | 51.6567 | 46.5618 | 41.2768 | 35.9767 | 30.7409 | 25.81 | -1.1457 | -16.5158 | -24.0831
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Consumer Transformation | Thermal headroom (MW) | 10.63 | 10.6 | 10.25 | 7.48 | 6.9 | 6.16 | 4.84 | 3.81 | 1.74 | 0.63 | -0.68 | -1.97 | -3.28 | -4.54 | -5.59 | -10.45 | -11.85 | -11.88
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Leading the Way | Thermal headroom (MW) | 10.63 | 10.44 | 9.89 | 6.25 | 5.52 | 4.58 | 2.93 | 1.57 | -1.33 | -2.68 | -4.01 | -5.43 | -6.82 | -8.14 | -9.08 | -11.25 | -11.09 | -10.39
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Steady Progression | Thermal headroom (MW) | 10.63 | 10.71 | 10.57 | 8.39 | 8.15 | 7.79 | 7.12 | 6.58 | 5.48 | 4.89 | 4.15 | 3.43 | 2.83 | 2.21 | 1.64 | -1.74 | -2.67 | -2.27
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | System Transformation | Thermal headroom (MW) | 10.63 | 10.68 | 10.49 | 7.92 | 7.61 | 7.31 | 6.43 | 5.78 | 4.1 | 3.41 | 2.8 | 2.14 | 1.45 | 0.67 | 0.02 | -3.45 | -4.14 | -3.67
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | WPD Best View | Thermal headroom (MW) | 10.63 | 10.6 | 10.25 | 7.48 | 6.9 | 6.16 | 4.84 | 3.81 | 1.74 | 0.63 | -0.68 | -1.97 | -3.28 | -4.54 | -5.59 | -10.45 | -11.85 | -11.88
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Consumer Transformation | Thermal headroom (MW) | 1.98 | 1.98 | 1.9 | 1.81 | 1.63 | 0.94 | 0.3 | -0.39 | -1.14 | -1.95 | -3.02 | -4.15 | -5.31 | -6.42 | -7.49 | -12.89 | -15.56 | -16.87
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Leading the Way | Thermal headroom (MW) | 1.98 | 1.77 | 1.49 | 1.23 | 0.86 | -0.3 | -1.42 | -2.63 | -3.93 | -5.31 | -6.22 | -7.2 | -8.22 | -9.15 | -10 | -13.67 | -15.05 | -15.7
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Steady Progression | Thermal headroom (MW) | 1.98 | 2.01 | 1.96 | 1.91 | 1.83 | 1.45 | 1.09 | 0.72 | 0.29 | -0.13 | -0.73 | -1.27 | -1.86 | -2.5 | -3.14 | -6.96 | -8.14 | -8.55
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | System Transformation | Thermal headroom (MW) | 1.98 | 2 | 1.93 | 1.86 | 1.76 | 1.62 | 1.43 | 1.24 | 1.01 | 0.76 | 0.28 | -0.25 | -0.77 | -1.26 | -1.8 | -5.31 | -7.71 | -8.58
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | WPD Best View | Thermal headroom (MW) | 1.98 | 1.98 | 1.9 | 1.81 | 1.63 | 0.98 | 0.37 | -0.27 | -0.97 | -1.72 | -2.78 | -3.89 | -5.03 | -6.13 | -7.18 | -12.05 | -14.66 | -15.79
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Consumer Transformation | Thermal headroom (MW) | 5.4 | 5.36 | 5.15 | 4.83 | 3.83 | 3.14 | 2.45 | 1.71 | 0.18 | -0.79 | -2.66 | -4.71 | -6.77 | -8.82 | -10.84 | -23.02 | -31.1 | -35.46
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Leading the Way | Thermal headroom (MW) | 5.4 | 5.13 | 4.68 | 4.15 | 2.55 | 1.1 | -0.3 | -1.8 | -5.5 | -7.72 | -9.64 | -11.75 | -14.02 | -16.23 | -18.36 | -26.64 | -30.53 | -33.27
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Steady Progression | Thermal headroom (MW) | 5.4 | 5.58 | 5.64 | 5.65 | 5.12 | 4.78 | 4.4 | 3.99 | 3.1 | 2.49 | 1.69 | 0.88 | 0.02 | -0.82 | -1.67 | -7.66 | -10.63 | -12.05
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | System Transformation | Thermal headroom (MW) | 5.4 | 5.52 | 5.5 | 5.41 | 4.67 | 4.42 | 4.12 | 3.73 | 2.51 | 1.85 | 1.04 | 0.23 | -0.6 | -1.39 | -2.1 | -8.51 | -11.7 | -12.7
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | WPD Best View | Thermal headroom (MW) | 5.4 | 5.36 | 5.15 | 4.83 | 3.83 | 3.14 | 2.45 | 1.71 | 0.18 | -0.79 | -2.66 | -4.71 | -6.77 | -8.82 | -10.84 | -23.02 | -31.1 | -35.46
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Consumer Transformation | Thermal headroom (MW) | 10.71 | 10.9 | 10.83 | 10.32 | 9.94 | 9.35 | 8.76 | 8.06 | 7.3 | 6.48 | 5.14 | 3.57 | 1.29 | -0.92 | -3.08 | -15.1 | -23.53 | -27.94
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Leading the Way | Thermal headroom (MW) | 10.71 | 10.55 | 10.14 | 9.21 | 8.43 | 7.41 | 6.33 | 4.99 | 3.66 | 2.18 | -0.13 | -2.61 | -5.11 | -7.54 | -9.89 | -17.5 | -21.09 | -22.92
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Steady Progression | Thermal headroom (MW) | 10.71 | 11.17 | 11.38 | 11.23 | 11.31 | 11.21 | 11.09 | 10.93 | 10.75 | 10.52 | 10.05 | 9.5 | 8.91 | 8.3 | 7.67 | 4.02 | -0.41 | -2.29
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | System Transformation | Thermal headroom (MW) | 10.71 | 11.07 | 11.16 | 10.83 | 10.72 | 10.57 | 10.37 | 10.11 | 9.79 | 9.31 | 8.6 | 7.82 | 7.01 | 6.23 | 5.53 | 0.96 | -2.15 | -2.78
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | WPD Best View | Thermal headroom (MW) | 10.71 | 10.55 | 10.14 | 9.21 | 8.43 | 7.41 | 6.33 | 4.99 | 3.66 | 2.18 | -0.13 | -2.61 | -5.11 | -7.54 | -9.89 | -17.5 | -21.09 | -22.92
East Claydon 132kV | Bletchley | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Consumer Transformation | Thermal headroom (MW) | 10.29 | 10.02 | 9.84 | 9.47 | 9.03 | 8.41 | 7.81 | 7.32 | 6.75 | 6.18 | 5.56 | 5.03 | 4.53 | 3.24 | 1.99 | -4.44 | -8.22 | -9.85
East Claydon 132kV | Bletchley | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Leading the Way | Thermal headroom (MW) | 10.29 | 9.79 | 9.42 | 8.89 | 8.26 | 7.46 | 6.71 | 6.05 | 5.36 | 4.67 | 3.86 | 2.73 | 1.29 | -0.11 | -1.36 | -5.57 | -6.92 | -7.27
East Claydon 132kV | Bletchley | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Steady Progression | Thermal headroom (MW) | 10.29 | 10.4 | 10.52 | 10.58 | 10.62 | 10.53 | 10.42 | 10.34 | 10.2 | 10.02 | 9.72 | 9.39 | 9.03 | 8.64 | 8.25 | 6.08 | 5.52 | 4.75
East Claydon 132kV | Bletchley | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | System Transformation | Thermal headroom (MW) | 10.29 | 10.28 | 10.31 | 10.25 | 10.18 | 10.06 | 9.9 | 9.78 | 9.6 | 9.36 | 9.1 | 8.79 | 8.45 | 8.13 | 7.88 | 6.14 | 4.8 | 4.7
East Claydon 132kV | Bletchley | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | WPD Best View | Thermal headroom (MW) | 10.29 | 9.79 | 9.42 | 8.89 | 8.26 | 7.46 | 6.71 | 6.05 | 5.36 | 4.67 | 3.86 | 2.73 | 1.29 | -0.11 | -1.36 | -5.57 | -6.92 | -7.27
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Consumer Transformation | Thermal headroom (MW) | 13.33 | 13.53 | 13.64 | 13.75 | 13.84 | 13.95 | 14.05 | 14.16 | 14.26 | 14.34 | 14.42 | 14.5 | 14.57 | 14.66 | 14.75 | 15.12 | 15.52 | 15.92
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Leading the Way | Thermal headroom (MW) | 13.33 | 13.53 | 13.64 | 13.75 | 13.84 | 13.94 | 14.04 | 14.14 | 14.24 | 14.34 | 14.41 | 14.48 | 14.54 | 14.61 | 14.69 | 15.1 | 15.53 | 15.95
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Steady Progression | Thermal headroom (MW) | 13.33 | 13.53 | 13.64 | 13.75 | 13.85 | 13.96 | 14.06 | 14.16 | 14.27 | 14.37 | 14.47 | 14.57 | 14.66 | 14.76 | 14.85 | 14.89 | 14.9 | 15.29
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | System Transformation | Thermal headroom (MW) | 13.33 | 13.53 | 13.64 | 13.75 | 13.85 | 13.95 | 14.06 | 14.16 | 14.26 | 14.36 | 14.46 | 14.56 | 14.65 | 14.73 | 14.81 | 14.83 | 14.87 | 15.28
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | WPD Best View | Thermal headroom (MW) | 13.33 | 13.53 | 13.64 | 13.75 | 13.84 | 13.94 | 14.04 | 14.14 | 14.24 | 14.34 | 14.41 | 14.48 | 14.54 | 14.61 | 14.69 | 15.1 | 15.53 | 15.95
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Consumer Transformation | Thermal headroom (MW) | 4.2 | 4 | 3.69 | 3.3 | 2.31 | 1.13 | -0.19 | -1.62 | -3.01 | -4.43 | -6.18 | -7.83 | -9.45 | -11.4 | -13.37 | -25.63 | -31.43 | -34.2
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Leading the Way | Thermal headroom (MW) | 4.2 | 3.76 | 3.19 | 2.59 | 1.36 | -0.22 | -1.82 | -3.75 | -5.68 | -7.73 | -9.82 | -11.97 | -14.21 | -16.75 | -19.18 | -28.57 | -30.92 | -32.05
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Steady Progression | Thermal headroom (MW) | 4.2 | 4.31 | 4.32 | 4.31 | 4.09 | 3.67 | 3.24 | 2.72 | 2.2 | 1.59 | 0.81 | -0.03 | -0.95 | -1.96 | -2.98 | -8.13 | -8.86 | -9.35
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | System Transformation | Thermal headroom (MW) | 4.2 | 4.21 | 4.11 | 3.99 | 3.58 | 3.09 | 2.52 | 1.84 | 1.03 | 0.15 | -0.79 | -1.82 | -2.86 | -3.91 | -4.91 | -9.14 | -10.06 | -9.87
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | WPD Best View | Thermal headroom (MW) | 4.2 | 3.76 | 3.19 | 2.59 | 1.36 | -0.22 | -1.82 | -3.75 | -5.68 | -7.73 | -9.82 | -11.97 | -14.21 | -16.75 | -19.18 | -28.57 | -30.92 | -32.05
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Consumer Transformation | Thermal headroom (MW) | 8.56 | 8.73 | 8.68 | 8.65 | 8.59 | 8.5 | 8.41 | 8.33 | 8.21 | 8.03 | 7.73 | 7.48 | 7.15 | 6.77 | 6.4 | 3.19 | 0.53 | -0.7
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Leading the Way | Thermal headroom (MW) | 8.56 | 8.62 | 8.44 | 8.29 | 8.09 | 7.83 | 7.57 | 7.3 | 6.91 | 6.43 | 6.03 | 5.61 | 5.17 | 4.73 | 4.14 | 2.04 | 1.11 | 0.68
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Steady Progression | Thermal headroom (MW) | 8.56 | 8.81 | 8.87 | 8.96 | 9.04 | 9.06 | 9.07 | 9.06 | 9.04 | 9.01 | 8.93 | 8.84 | 8.7 | 8.55 | 8.39 | 7.67 | 7.81 | 7.78
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | System Transformation | Thermal headroom (MW) | 8.56 | 8.79 | 8.81 | 8.86 | 8.9 | 8.93 | 8.96 | 8.98 | 8.97 | 8.95 | 8.9 | 8.81 | 8.7 | 8.6 | 8.54 | 8.3 | 8.12 | 8.2
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | WPD Best View | Thermal headroom (MW) | 8.56 | 8.62 | 8.44 | 8.29 | 8.09 | 7.83 | 7.57 | 7.3 | 6.91 | 6.43 | 6.03 | 5.61 | 5.17 | 4.73 | 4.14 | 2.04 | 1.11 | 0.68
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Consumer Transformation | Thermal headroom (MW) | 14.54 | 14.23 | 13.86 | 13.3 | 12.49 | 11.37 | 10.35 | 9.45 | 8.49 | 7.37 | 5.48 | 3.55 | 1.62 | -0.2 | -1.95 | -11.67 | -18.12 | -21.58
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Leading the Way | Thermal headroom (MW) | 14.54 | 13.79 | 12.99 | 12.02 | 10.78 | 9.11 | 7.59 | 6.05 | 4.5 | 2.78 | 0.8 | -1.38 | -3.55 | -5.56 | -7.43 | -13.97 | -17.13 | -19.14
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Steady Progression | Thermal headroom (MW) | 14.54 | 14.57 | 14.56 | 14.51 | 14.34 | 13.95 | 13.58 | 13.25 | 12.92 | 12.54 | 11.99 | 11.36 | 10.67 | 9.9 | 9.11 | 4.28 | 0.87 | -0.42
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | System Transformation | Thermal headroom (MW) | 14.54 | 14.49 | 14.39 | 14.21 | 13.89 | 13.49 | 13.07 | 12.7 | 12.27 | 11.7 | 10.87 | 9.96 | 9.05 | 8.17 | 7.38 | 1.94 | -0.62 | -1.38
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | WPD Best View | Thermal headroom (MW) | 14.54 | 13.79 | 12.99 | 12.02 | 10.78 | 9.11 | 7.59 | 6.05 | 4.5 | 2.78 | 0.8 | -1.38 | -3.55 | -5.56 | -7.43 | -13.97 | -17.13 | -19.14
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Consumer Transformation | Thermal headroom (MW) | 5.4 | 5.45 | 5.49 | 5.4 | 5.39 | 5.3 | 5.1 | 4.9 | 4.85 | 4.78 | 4.66 | 4.17 | 3.68 | 3.39 | 3.09 | 1.83 | 1.08 | 0.97
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Leading the Way | Thermal headroom (MW) | 5.4 | 5.42 | 5.42 | 5.28 | 5.24 | 5.11 | 4.89 | 4.62 | 4.53 | 4.44 | 4.31 | 3.98 | 3.63 | 3.34 | 3.06 | 2.3 | 2.03 | 2.34
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Steady Progression | Thermal headroom (MW) | 5.4 | 5.49 | 5.55 | 5.52 | 5.57 | 5.57 | 5.55 | 5.52 | 5.52 | 5.51 | 5.49 | 5.48 | 5.47 | 5.46 | 5.44 | 4.51 | 3.68 | 3.32
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | System Transformation | Thermal headroom (MW) | 5.4 | 5.48 | 5.53 | 5.47 | 5.5 | 5.49 | 5.43 | 5.33 | 5.31 | 5.29 | 5.26 | 5.21 | 5.16 | 4.74 | 4.32 | 2.95 | 2.23 | 2.46
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | WPD Best View | Thermal headroom (MW) | 5.4 | 5.42 | 5.42 | 5.28 | 5.24 | 5.11 | 4.89 | 4.62 | 4.53 | 4.44 | 4.31 | 3.98 | 3.63 | 3.34 | 3.06 | 2.3 | 2.03 | 2.34
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Consumer Transformation | Thermal headroom (MW) | 15.21 | 14.73 | 14.12 | 13.37 | 12.55 | 11.54 | 10.49 | 9.43 | 8.19 | 6.57 | 2.94 | -0.78 | -4.48 | -8.13 | -11.76 | -24.31 | -35.72 | -42.84
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Leading the Way | Thermal headroom (MW) | 15.21 | 14.44 | 13.55 | 12.54 | 11.39 | 10.02 | 8.41 | 6.27 | 3.76 | 1.08 | -1.87 | -5.18 | -8.59 | -11.91 | -14.91 | -22.92 | -26.74 | -28.24
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Steady Progression | Thermal headroom (MW) | 15.21 | 15.06 | 14.85 | 14.64 | 14.45 | 14.1 | 13.73 | 13.34 | 12.96 | 12.2 | 11.18 | 10.59 | 9.93 | 9.14 | 8.48 | 1.05 | -4.89 | -7.6
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | System Transformation | Thermal headroom (MW) | 15.21 | 14.93 | 14.58 | 14.22 | 13.83 | 13.41 | 12.97 | 12.48 | 11.93 | 11.33 | 10.21 | 9.01 | 7.69 | 5.95 | 4.14 | -4.63 | -8.36 | -8.99
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | WPD Best View | Thermal headroom (MW) | 15.21 | 14.44 | 13.55 | 12.54 | 11.39 | 10.02 | 8.41 | 6.27 | 3.76 | 1.08 | -1.87 | -5.18 | -8.59 | -11.91 | -14.91 | -22.92 | -26.74 | -28.24
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Consumer Transformation | Thermal headroom (MW) | -25.9 | -27.45 | -27.71 | -28.08 | -28.95 | -30.62 | -32.22 | -33.76 | -35.42 | -36.98 | -38.77 | -40.67 | -42.33 | -43.88 | -45.39 | -53.46 | -56.9 | -57.55
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Leading the Way | Thermal headroom (MW) | -25.9 | -28.24 | -29.07 | -29.96 | -31.17 | -33.31 | -35.45 | -37.86 | -40.48 | -43.08 | -45.17 | -47.38 | -49.28 | -50.88 | -52.15 | -55.72 | -55.79 | -55.02
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Steady Progression | Thermal headroom (MW) | -25.9 | -26.78 | -26.49 | -26.2 | -26.07 | -26.26 | -26.46 | -26.65 | -26.78 | -26.89 | -27.21 | -27.49 | -27.8 | -28.16 | -28.47 | -30.87 | -31.27 | -30.35
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | System Transformation | Thermal headroom (MW) | -25.9 | -27.15 | -27 | -26.91 | -26.98 | -27.32 | -27.65 | -28.01 | -28.5 | -28.96 | -29.38 | -29.89 | -30.34 | -30.78 | -31.25 | -34.13 | -34.25 | -33.19
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | WPD Best View | Thermal headroom (MW) | -25.9 | -28.24 | -29.07 | -29.96 | -31.17 | -33.31 | -35.45 | -37.86 | -40.48 | -43.08 | -45.17 | -47.38 | -49.28 | -50.88 | -52.15 | -55.72 | -55.79 | -55.02
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Consumer Transformation | Thermal headroom (MW) | 6.56 | 6.55 | 6.38 | 6.17 | 5.84 | 5.32 | 4.74 | 4.08 | 3.31 | 2.47 | 1.42 | 0.29 | -0.87 | -1.97 | -3.04 | -8.45 | -10.96 | -12.09
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Leading the Way | Thermal headroom (MW) | 6.56 | 6.37 | 5.98 | 5.6 | 5.04 | 4.29 | 3.48 | 2.49 | 1.37 | 0.15 | -0.99 | -2.2 | -3.43 | -4.57 | -5.65 | -9.16 | -9.93 | -9.8
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Steady Progression | Thermal headroom (MW) | 6.56 | 6.74 | 6.75 | 6.77 | 6.77 | 6.69 | 6.56 | 6.4 | 6.24 | 6.09 | 5.76 | 5.46 | 5.06 | 4.63 | 4.12 | 0.65 | -1.65 | -2.37
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | System Transformation | Thermal headroom (MW) | 6.56 | 6.7 | 6.67 | 6.59 | 6.46 | 6.34 | 6.16 | 5.96 | 5.65 | 5.33 | 4.87 | 4.32 | 3.71 | 3.04 | 2.34 | -1.91 | -3.45 | -3.25
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | WPD Best View | Thermal headroom (MW) | 6.56 | 6.37 | 5.98 | 5.6 | 5.04 | 4.29 | 3.48 | 2.49 | 1.37 | 0.15 | -0.99 | -2.2 | -3.43 | -4.57 | -5.65 | -9.16 | -9.93 | -9.8
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Consumer Transformation | Thermal headroom (MW) | 10.16 | 9.98 | 9.9 | 9.81 | 9.66 | 9.4 | 9.17 | 8.85 | 8.45 | 8.04 | 7.51 | 6.97 | 6.39 | 5.8 | 5.04 | 0.66 | -2.3 | -3.69
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Leading the Way | Thermal headroom (MW) | 10.16 | 9.85 | 9.64 | 9.46 | 9.23 | 8.84 | 8.33 | 7.77 | 7.14 | 6.46 | 5.79 | 5.12 | 4.27 | 3.43 | 2.65 | -0.46 | -1.93 | -2.72
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Steady Progression | Thermal headroom (MW) | 10.16 | 10.15 | 10.2 | 10.25 | 10.28 | 10.21 | 10.13 | 10.04 | 9.92 | 9.78 | 9.52 | 9.26 | 8.97 | 8.67 | 8.37 | 6.6 | 5.56 | 5.08
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | System Transformation | Thermal headroom (MW) | 10.16 | 10.09 | 10.1 | 10.11 | 10.1 | 10.06 | 10.02 | 9.95 | 9.79 | 9.54 | 9.24 | 8.95 | 8.66 | 8.38 | 8.14 | 6.75 | 5.47 | 5.14
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | WPD Best View | Thermal headroom (MW) | 10.16 | 9.85 | 9.64 | 9.46 | 9.23 | 8.84 | 8.33 | 7.77 | 7.14 | 6.46 | 5.79 | 5.12 | 4.27 | 3.43 | 2.65 | -0.46 | -1.93 | -2.72
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Consumer Transformation | Thermal headroom (MW) | 13.93 | 13.1 | 12.36 | 11.81 | 8.88 | 6.94 | 5.79 | 4.78 | 3.79 | 2.77 | 1.69 | 0.96 | 0.24 | -0.45 | -1.13 | -3.53 | -3.31 | -2.34
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Leading the Way | Thermal headroom (MW) | 13.93 | 12.87 | 11.97 | 11.24 | 7.55 | 4.76 | 3.29 | 2.11 | 1.03 | -0.04 | -1.04 | -1.76 | -2.34 | -2.79 | -3.18 | -3.96 | -2.87 | -1.31
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Steady Progression | Thermal headroom (MW) | 13.93 | 13.3 | 12.71 | 12.3 | 9.9 | 8.43 | 7.62 | 6.89 | 6.22 | 5.59 | 4.93 | 4.28 | 3.6 | 3.12 | 2.66 | 0.09 | 0.19 | 1.28
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | System Transformation | Thermal headroom (MW) | 13.93 | 13.15 | 12.46 | 11.95 | 9.07 | 7.36 | 6.42 | 5.65 | 5 | 4.25 | 3.44 | 2.98 | 2.46 | 1.96 | 1.42 | -0.94 | -0.57 | 0.9
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | WPD Best View | Thermal headroom (MW) | 13.93 | 12.87 | 11.97 | 11.24 | 7.55 | 4.76 | 3.29 | 2.11 | 1.03 | -0.04 | -1.04 | -1.76 | -2.34 | -2.79 | -3.18 | -3.96 | -2.87 | -1.31
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Consumer Transformation | Thermal headroom (MW) | -7.92 | -7.93 | -8.06 | -8.26 | -8.52 | -9.06 | -9.59 | -10.13 | -10.69 | -11.29 | -12.16 | -13.36 | -14.61 | -15.79 | -16.94 | -23.12 | -27.41 | -30.42
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Leading the Way | Thermal headroom (MW) | -7.92 | -8.03 | -8.29 | -8.59 | -8.98 | -9.75 | -10.66 | -11.62 | -12.58 | -13.83 | -15.02 | -16.26 | -17.54 | -18.78 | -19.88 | -24.68 | -27.54 | -30.01
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Steady Progression | Thermal headroom (MW) | -7.92 | -7.83 | -7.83 | -7.84 | -7.88 | -8.09 | -8.32 | -8.57 | -8.86 | -9.17 | -9.6 | -10.03 | -10.48 | -10.95 | -11.42 | -15.49 | -17.54 | -18.29
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | System Transformation | Thermal headroom (MW) | -7.92 | -7.86 | -7.9 | -7.96 | -8.09 | -8.22 | -8.37 | -8.62 | -8.96 | -9.27 | -9.71 | -10.18 | -10.65 | -11.12 | -11.54 | -15.39 | -18.65 | -20.11
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | WPD Best View | Thermal headroom (MW) | -7.92 | -8.03 | -8.29 | -8.59 | -8.98 | -9.75 | -10.66 | -11.62 | -12.58 | -13.83 | -15.02 | -16.26 | -17.54 | -18.78 | -19.88 | -24.68 | -27.54 | -30.01
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Consumer Transformation | Thermal headroom (MW) | 15.43 | 15 | 13.32 | 11.24 | 8.24 | 6.67 | 5.2 | 3.54 | 1.46 | -0.75 | -3.36 | -5.89 | -8.45 | -10.56 | -12.64 | -23.19 | -27.46 | -28.7
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Leading the Way | Thermal headroom (MW) | 15.43 | 14.78 | 12.72 | 9.98 | 5.97 | 3.55 | 1.27 | -1.16 | -3.77 | -6.54 | -9.19 | -11.53 | -13.8 | -15.99 | -17.97 | -24.71 | -25.91 | -25.65
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Steady Progression | Thermal headroom (MW) | 15.43 | 15.32 | 14.08 | 12.59 | 10.38 | 9.38 | 8.52 | 7.55 | 6.46 | 5.4 | 4.16 | 2.88 | 1.69 | 0.58 | -0.52 | -7.57 | -10.29 | -10.66
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | System Transformation | Thermal headroom (MW) | 15.43 | 15.2 | 13.71 | 11.87 | 9.21 | 8.11 | 7.13 | 6.11 | 4.92 | 3.58 | 2.15 | 1 | -0.21 | -1.82 | -3.49 | -11.04 | -13.39 | -13.1
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | WPD Best View | Thermal headroom (MW) | 15.43 | 14.78 | 12.72 | 9.98 | 5.97 | 3.55 | 1.27 | -1.16 | -3.77 | -6.54 | -9.19 | -11.53 | -13.8 | -15.99 | -17.97 | -24.71 | -25.91 | -25.65
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Consumer Transformation | Thermal headroom (MW) | 53.68 | 53.0138 | 51.8469 | 50.455 | 47.6723 | 44.2166 | 40.727 | 37.2005 | 33.5208 | 29.5692 | 23.7208 | 17.7235 | 11.4459 | 5.0964 | -1.0527 | -34.6837 | -54.1253 | -63.4614
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Leading the Way | Thermal headroom (MW) | 53.68 | 52.1145 | 49.8763 | 47.638 | 43.5791 | 38.3451 | 33.5751 | 28.0889 | 22.4782 | 16.3197 | 9.4792 | 2.3811 | -4.873 | -11.8532 | -18.2403 | -40.039 | -47.8073 | -50.5999
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Steady Progression | Thermal headroom (MW) | 53.68 | 54.1455 | 54.0552 | 54.062 | 53.254 | 52.0783 | 51.043 | 49.82 | 48.4619 | 46.9131 | 44.819 | 42.5444 | 40.0578 | 37.4873 | 34.8883 | 18.8939 | 9.472 | 5.3288
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | System Transformation | Thermal headroom (MW) | 53.68 | 53.8126 | 53.3723 | 52.9876 | 51.4869 | 50.0001 | 48.654 | 47.0213 | 45.1301 | 42.8499 | 40.281 | 37.4788 | 34.521 | 31.3722 | 28.2422 | 11.5042 | 4.5409 | 3.7896
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | WPD Best View | Thermal headroom (MW) | 53.68 | 52.1145 | 49.8763 | 47.638 | 43.5791 | 38.3451 | 33.5751 | 28.0889 | 22.4782 | 16.3197 | 9.4792 | 2.3811 | -4.873 | -11.8532 | -18.2403 | -40.039 | -47.8073 | -50.5999
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Consumer Transformation | Thermal headroom (MW) | 1.6 | 1.66 | 1.64 | 1.65 | 1.64 | 1.58 | 1.47 | 1.36 | 1.25 | 1.13 | 0.87 | 0.62 | 0.36 | 0.11 | -0.13 | -1.89 | -2.84 | -3.16
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Leading the Way | Thermal headroom (MW) | 1.6 | 1.57 | 1.47 | 1.41 | 1.32 | 1.14 | 0.95 | 0.72 | 0.5 | 0.24 | 0.02 | -0.26 | -0.53 | -0.8 | -1.06 | -2.11 | -2.47 | -2.53
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Steady Progression | Thermal headroom (MW) | 1.6 | 1.73 | 1.79 | 1.85 | 1.91 | 1.93 | 1.95 | 1.96 | 1.98 | 2 | 1.98 | 1.92 | 1.82 | 1.72 | 1.62 | 0.84 | 0.48 | 0.45
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | System Transformation | Thermal headroom (MW) | 1.6 | 1.71 | 1.74 | 1.79 | 1.83 | 1.87 | 1.92 | 1.96 | 1.99 | 1.99 | 1.91 | 1.82 | 1.74 | 1.66 | 1.55 | 0.71 | 0.37 | 0.46
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | WPD Best View | Thermal headroom (MW) | 1.6 | 1.57 | 1.47 | 1.41 | 1.32 | 1.14 | 0.95 | 0.72 | 0.5 | 0.24 | 0.02 | -0.26 | -0.53 | -0.8 | -1.06 | -2.11 | -2.47 | -2.53
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Consumer Transformation | Thermal headroom (MW) | 5.66 | 5.35 | 5.16 | 4.86 | 4.25 | 3.61 | 2.96 | 2.26 | 1.57 | 0.79 | -0.4 | -2.02 | -4.19 | -6.11 | -7.97 | -19.87 | -28.18 | -32.36
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Leading the Way | Thermal headroom (MW) | 5.66 | 5.06 | 4.59 | 4.03 | 3.1 | 1.79 | 0.54 | -0.8 | -2.06 | -3.47 | -5.5 | -7.62 | -9.81 | -11.91 | -13.93 | -21.43 | -25.42 | -27.59
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Steady Progression | Thermal headroom (MW) | 5.66 | 5.66 | 5.74 | 5.79 | 5.67 | 5.46 | 5.25 | 4.98 | 4.68 | 4.28 | 3.7 | 3.09 | 2.44 | 1.76 | 1.09 | -3.1 | -6.09 | -8.14
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | System Transformation | Thermal headroom (MW) | 5.66 | 5.54 | 5.52 | 5.45 | 5.15 | 4.9 | 4.66 | 4.3 | 3.84 | 3.29 | 2.57 | 1.78 | 0.99 | -0.13 | -1.17 | -5.43 | -8.42 | -9.41
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | WPD Best View | Thermal headroom (MW) | 5.66 | 5.06 | 4.59 | 4.03 | 3.1 | 1.79 | 0.54 | -0.8 | -2.06 | -3.47 | -5.5 | -7.62 | -9.81 | -11.91 | -13.93 | -21.43 | -25.42 | -27.59
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Consumer Transformation | Thermal headroom (MW) | 10.9 | 10.77 | 10.35 | 9.94 | 8.48 | 7.1 | 6.09 | 5.07 | 4 | 2.83 | 0.7 | -1.35 | -3.47 | -5.43 | -7.34 | -17.2 | -23.51 | -26.78
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Leading the Way | Thermal headroom (MW) | 10.9 | 10.55 | 9.86 | 9.22 | 7.12 | 5.05 | 3.67 | 2.04 | 0.24 | -1.8 | -4.15 | -6.42 | -8.66 | -10.75 | -12.67 | -19.04 | -21.85 | -23.16
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Steady Progression | Thermal headroom (MW) | 10.9 | 11.04 | 10.92 | 10.87 | 10.05 | 9.39 | 8.97 | 8.5 | 7.95 | 7.35 | 6.6 | 5.85 | 5.06 | 4.29 | 3.52 | -0.91 | -4.45 | -5.98
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | System Transformation | Thermal headroom (MW) | 10.9 | 10.97 | 10.74 | 10.58 | 9.49 | 8.69 | 8.23 | 7.64 | 6.97 | 6.2 | 5.34 | 4.55 | 3.72 | 2.92 | 2.13 | -3.33 | -5.78 | -6.52
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | WPD Best View | Thermal headroom (MW) | 10.9 | 10.55 | 9.86 | 9.22 | 7.12 | 5.05 | 3.67 | 2.04 | 0.24 | -1.8 | -4.15 | -6.42 | -8.66 | -10.75 | -12.67 | -19.04 | -21.85 | -23.16
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Consumer Transformation | Thermal headroom (MW) | 7.8 | 7.7 | 7.3 | 6.89 | 6.58 | 6.02 | 5.16 | 4.38 | 3.64 | 2.91 | 1.84 | 0.71 | -0.37 | -1.45 | -2.4 | -6.82 | -8.79 | -9.59
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Leading the Way | Thermal headroom (MW) | 7.8 | 7.56 | 6.93 | 6.39 | 5.89 | 5.11 | 4.07 | 2.9 | 1.77 | 0.72 | -0.39 | -1.57 | -2.74 | -3.82 | -4.69 | -7.28 | -7.62 | -7.21
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Steady Progression | Thermal headroom (MW) | 7.8 | 7.92 | 7.75 | 7.7 | 7.69 | 7.6 | 7.4 | 7.17 | 6.96 | 6.74 | 6.49 | 6.16 | 5.81 | 5.44 | 5.01 | 1.99 | -0.02 | -0.66
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | System Transformation | Thermal headroom (MW) | 7.8 | 7.88 | 7.64 | 7.53 | 7.42 | 7.2 | 6.89 | 6.55 | 6.22 | 5.86 | 5.46 | 4.96 | 4.39 | 3.73 | 3.07 | -0.5 | -1.44 | -1.1
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | WPD Best View | Thermal headroom (MW) | 7.8 | 7.56 | 6.93 | 6.39 | 5.89 | 5.11 | 4.07 | 2.9 | 1.77 | 0.72 | -0.39 | -1.57 | -2.74 | -3.82 | -4.69 | -7.28 | -7.62 | -7.21
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Consumer Transformation | Thermal headroom (MW) | 11.39 | 11.17 | 10.93 | 10.57 | 10.11 | 9.22 | 8.32 | 7.36 | 6.23 | 4.94 | 3.21 | 1.47 | -0.27 | -1.85 | -3.41 | -10.74 | -14.76 | -16.7
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Leading the Way | Thermal headroom (MW) | 11.39 | 10.95 | 10.38 | 9.78 | 9.08 | 7.78 | 6.55 | 5.07 | 3.54 | 1.68 | -0.19 | -2.09 | -3.97 | -5.65 | -7.12 | -11.47 | -12.79 | -12.9
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Steady Progression | Thermal headroom (MW) | 11.39 | 11.46 | 11.44 | 11.41 | 11.37 | 11.08 | 10.84 | 10.52 | 10.13 | 9.72 | 9.13 | 8.49 | 7.8 | 7.07 | 6.37 | 1.51 | -1.76 | -2.74
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | System Transformation | Thermal headroom (MW) | 11.39 | 11.38 | 11.29 | 11.16 | 10.96 | 10.58 | 10.18 | 9.73 | 9.19 | 8.49 | 7.79 | 6.96 | 6.04 | 5.16 | 4.22 | -0.71 | -2.49 | -2.48
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | WPD Best View | Thermal headroom (MW) | 11.39 | 10.95 | 10.38 | 9.78 | 9.08 | 7.78 | 6.55 | 5.07 | 3.54 | 1.68 | -0.19 | -2.09 | -3.97 | -5.65 | -7.12 | -11.47 | -12.79 | -12.9
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Consumer Transformation | Thermal headroom (MW) | 10.14 | 10.01 | 9.79 | 9.47 | 9.06 | 8.64 | 8.15 | 7.58 | 6.96 | 6.26 | 4.8 | 3.44 | 2 | 0.71 | -0.73 | -5.11 | -10.56 | -14.96
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Leading the Way | Thermal headroom (MW) | 10.14 | 10.01 | 9.73 | 9.4 | 8.89 | 8.41 | 7.81 | 7.08 | 6.01 | 4.94 | 4.15 | 3.18 | 2.16 | 0.52 | -1.03 | -4.27 | -6.45 | -8.32
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Steady Progression | Thermal headroom (MW) | 10.14 | 10.18 | 10.12 | 10.06 | 9.98 | 9.88 | 9.73 | 9.53 | 9.28 | 8.7 | 8.03 | 7.66 | 7.24 | 6.71 | 6.27 | 3.53 | 2.31 | 1.69
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | System Transformation | Thermal headroom (MW) | 10.14 | 10.14 | 10.04 | 9.92 | 9.75 | 9.57 | 9.35 | 9.01 | 8.61 | 8.13 | 7.69 | 7.18 | 6.28 | 5.4 | 4.58 | 1.63 | 0.58 | 0.79
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | WPD Best View | Thermal headroom (MW) | 10.14 | 10.01 | 9.73 | 9.4 | 8.89 | 8.41 | 7.81 | 7.08 | 6.01 | 4.94 | 4.15 | 3.18 | 2.16 | 0.52 | -1.03 | -4.27 | -6.45 | -8.32
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Consumer Transformation | Thermal headroom (MW) | 7.116 | 7.136 | 7.116 | 7.076 | 7.006 | 6.916 | 6.816 | 6.696 | 6.566 | 6.396 | 6.306 | 6.106 | 5.816 | 5.606 | 5.416 | 4.456 | 4.196 | 4.036
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Leading the Way | Thermal headroom (MW) | 7.116 | 7.126 | 7.106 | 7.056 | 6.956 | 6.846 | 6.696 | 6.516 | 6.326 | 6.116 | 6.036 | 5.796 | 5.526 | 5.236 | 5.026 | 4.326 | 4.196 | 4.286
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Steady Progression | Thermal headroom (MW) | 7.116 | 7.166 | 7.176 | 7.166 | 7.146 | 7.156 | 7.146 | 7.126 | 7.106 | 7.066 | 7.026 | 6.986 | 6.936 | 6.886 | 6.826 | 6.116 | 5.196 | 5.116
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | System Transformation | Thermal headroom (MW) | 7.116 | 7.156 | 7.156 | 7.136 | 7.106 | 7.066 | 7.006 | 6.936 | 6.846 | 6.746 | 6.676 | 6.606 | 6.526 | 6.436 | 6.356 | 5.046 | 4.476 | 4.666
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | WPD Best View | Thermal headroom (MW) | 7.116 | 7.126 | 7.106 | 7.056 | 6.956 | 6.846 | 6.696 | 6.516 | 6.326 | 6.116 | 6.036 | 5.796 | 5.526 | 5.236 | 5.026 | 4.326 | 4.196 | 4.286
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Consumer Transformation | Thermal headroom (MW) | 14.92 | 14.72 | 11.78 | 11.05 | 10.59 | 10.27 | 9.97 | 9.79 | 9.61 | 9.39 | 9.14 | 8.87 | 8.65 | 8.46 | 8.3 | 7.81 | 7.89 | 8.18
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Leading the Way | Thermal headroom (MW) | 14.92 | 14.69 | 11.35 | 10.46 | 9.97 | 9.82 | 9.68 | 9.54 | 9.34 | 9.13 | 8.92 | 8.68 | 8.42 | 8.21 | 8.05 | 8.03 | 8.52 | 9.27
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Steady Progression | Thermal headroom (MW) | 14.92 | 14.87 | 12.48 | 11.94 | 11.61 | 11.42 | 11.24 | 11.07 | 10.9 | 10.84 | 10.74 | 10.67 | 10.64 | 10.58 | 10.48 | 9.94 | 9.7 | 10.01
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | System Transformation | Thermal headroom (MW) | 14.92 | 14.83 | 12.07 | 11.44 | 11.09 | 10.91 | 10.74 | 10.67 | 10.57 | 10.48 | 10.4 | 10.3 | 10.17 | 10.01 | 9.84 | 9.16 | 9.39 | 9.98
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | WPD Best View | Thermal headroom (MW) | 14.92 | 14.69 | 11.35 | 10.46 | 9.97 | 9.82 | 9.68 | 9.54 | 9.34 | 9.13 | 8.92 | 8.68 | 8.42 | 8.21 | 8.05 | 8.03 | 8.52 | 9.27
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Consumer Transformation | Thermal headroom (MW) | 7.55 | 7.24 | 6.46 | 5.47 | 4.02 | 2.41 | 1.01 | -0.46 | -1.94 | -3.63 | -6.21 | -9.24 | -11.86 | -14.12 | -16.29 | -27.33 | -34.31 | -37.56
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Leading the Way | Thermal headroom (MW) | 7.55 | 6.74 | 5.5 | 4.07 | 2.16 | 0.03 | -1.87 | -4.11 | -6.29 | -8.72 | -11.52 | -14.49 | -16.83 | -19.06 | -21.05 | -27.8 | -30.99 | -31.97
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Steady Progression | Thermal headroom (MW) | 7.55 | 7.59 | 7.39 | 7.17 | 6.85 | 6.35 | 5.9 | 5.43 | 4.94 | 4.4 | 3.64 | 2.87 | 2.06 | 1.23 | 0.41 | -5.4 | -9.78 | -11.88
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | System Transformation | Thermal headroom (MW) | 7.55 | 7.44 | 6.97 | 6.51 | 5.88 | 5.32 | 4.75 | 4.06 | 3.33 | 2.53 | 1.48 | 0.29 | -0.71 | -2.12 | -3.6 | -10.16 | -13.32 | -14.03
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | WPD Best View | Thermal headroom (MW) | 7.55 | 6.74 | 5.5 | 4.07 | 2.16 | 0.03 | -1.87 | -4.11 | -6.29 | -8.72 | -11.52 | -14.49 | -16.83 | -19.06 | -21.05 | -27.8 | -30.99 | -31.97
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Consumer Transformation | Thermal headroom (MW) | 12.05 | 11.87 | 11.58 | 11.22 | 10.64 | 9.92 | 9.26 | 8.56 | 7.83 | 7.03 | 5.97 | 4.38 | 2.77 | 1.15 | -0.41 | -9.85 | -17.01 | -20.7
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Leading the Way | Thermal headroom (MW) | 12.05 | 11.61 | 11.06 | 10.4 | 9.46 | 8.21 | 7.06 | 5.84 | 4.55 | 2.97 | 1.3 | -0.46 | -2.3 | -4.08 | -5.77 | -12.18 | -15.72 | -17.73
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Steady Progression | Thermal headroom (MW) | 12.05 | 12.14 | 12.16 | 12.15 | 12.09 | 11.85 | 11.54 | 11.15 | 10.71 | 10.22 | 9.62 | 9.01 | 8.35 | 7.66 | 6.98 | 3.23 | 0.72 | -0.76
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | System Transformation | Thermal headroom (MW) | 12.05 | 12.07 | 11.99 | 11.88 | 11.69 | 11.46 | 11.17 | 10.8 | 10.36 | 9.84 | 9.29 | 8.71 | 8.11 | 7.54 | 6.93 | 3.54 | 1.27 | 0.1
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | WPD Best View | Thermal headroom (MW) | 12.05 | 11.61 | 11.06 | 10.4 | 9.46 | 8.21 | 7.06 | 5.84 | 4.55 | 2.97 | 1.3 | -0.46 | -2.3 | -4.08 | -5.77 | -12.18 | -15.72 | -17.73
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Consumer Transformation | Thermal headroom (MW) | 6.61 | 1.48 | 1.4 | 1.29 | 1.12 | 0.9 | 0.68 | 0.44 | 0.19 | -0.09 | -0.43 | -0.77 | -1.34 | -1.88 | -2.42 | -5.89 | -8 | -9.07
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Leading the Way | Thermal headroom (MW) | 6.61 | 1.43 | 1.28 | 1.11 | 0.88 | 0.48 | 0.06 | -0.38 | -0.8 | -1.24 | -1.8 | -2.43 | -3.06 | -3.69 | -4.26 | -6.54 | -7.58 | -8.19
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Steady Progression | Thermal headroom (MW) | 6.61 | 6.69 | 6.71 | 6.71 | 6.69 | 6.6 | 6.49 | 6.37 | 6.22 | 6.05 | 5.82 | 5.58 | 5.32 | 5.06 | 4.8 | 3.05 | 1.94 | 1.51
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | System Transformation | Thermal headroom (MW) | 6.61 | 6.67 | 6.67 | 6.64 | 6.58 | 6.51 | 6.41 | 6.28 | 6.11 | 5.91 | 5.66 | 5.4 | 5.13 | 4.85 | 4.6 | 2.96 | 1.67 | 1.36
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | WPD Best View | Thermal headroom (MW) | 6.61 | 1.43 | 1.28 | 1.11 | 0.88 | 0.48 | 0.06 | -0.38 | -0.8 | -1.24 | -1.8 | -2.43 | -3.06 | -3.69 | -4.26 | -6.54 | -7.58 | -8.19
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Consumer Transformation | Thermal headroom (MW) | 4.69 | 4.67 | 4.56 | 4.39 | 4.17 | 3.81 | 3.4 | 2.93 | 2.46 | 1.95 | 1.53 | 1.16 | 0.79 | 0.46 | 0.14 | -2.88 | -4.99 | -7.24
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Leading the Way | Thermal headroom (MW) | 4.69 | 4.66 | 4.53 | 4.35 | 4.09 | 3.61 | 3.07 | 2.43 | 1.79 | 1.18 | 0.75 | 0.32 | -0.11 | -0.69 | -1.37 | -4.42 | -6.51 | -8.82
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Steady Progression | Thermal headroom (MW) | 4.69 | 4.74 | 4.73 | 4.69 | 4.63 | 4.54 | 4.42 | 4.28 | 4.14 | 3.97 | 3.77 | 3.56 | 3.31 | 3.05 | 2.79 | 1.34 | 0.65 | 0.14
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | System Transformation | Thermal headroom (MW) | 4.69 | 4.73 | 4.68 | 4.61 | 4.5 | 4.36 | 4.16 | 3.88 | 3.53 | 3.21 | 2.91 | 2.58 | 2.24 | 1.91 | 1.62 | -0.09 | -1.32 | -1.85
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | WPD Best View | Thermal headroom (MW) | 4.69 | 4.66 | 4.53 | 4.35 | 4.09 | 3.61 | 3.07 | 2.43 | 1.79 | 1.18 | 0.75 | 0.32 | -0.11 | -0.69 | -1.37 | -4.42 | -6.51 | -8.82
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Consumer Transformation | Thermal headroom (MW) | 14.7708 | 13.8582 | 12.1493 | 9.1788 | 6.4371 | 1.813 | -3.356 | -9.0729 | -15.2059 | -22.3548 | -34.3526 | -46.6648 | -59.6913 | -72.4435 | -85.0351 | -153.4776 | -199.7363 | -224.8712
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Leading the Way | Thermal headroom (MW) | 14.7708 | 12.2429 | 8.8464 | 4.0776 | -1.0289 | -10.2868 | -19.7513 | -30.8681 | -43.7589 | -57.9273 | -70.9014 | -84.7198 | -99.1929 | -112.9777 | -125.9868 | -172.6684 | -195.2047 | -209.8278
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Steady Progression | Thermal headroom (MW) | 14.7708 | 15.2277 | 15.0279 | 13.978 | 13.4081 | 11.3083 | 8.9545 | 6.4916 | 3.7144 | 0.43872 | -4.3703 | -9.3155 | -14.5012 | -19.8255 | -25.2957 | -57.555 | -73.558 | -79.9899
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | System Transformation | Thermal headroom (MW) | 14.7708 | 14.8241 | 14.1734 | 12.4596 | 11.2256 | 9.8443 | 8.0146 | 5.5976 | 2.4254 | -1.5117 | -6.7554 | -12.1088 | -17.7143 | -23.5097 | -29.3167 | -62.4677 | -79.5882 | -84.7641
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | WPD Best View | Thermal headroom (MW) | 14.7708 | 13.8582 | 12.1493 | 9.1788 | 6.4371 | 1.813 | -3.356 | -9.0729 | -15.2059 | -22.3548 | -34.3526 | -46.6648 | -59.6913 | -72.4435 | -85.0351 | -153.4776 | -199.7363 | -224.8712
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Consumer Transformation | Thermal headroom (MW) | 9.85 | 9.22 | 8.68 | 7.98 | 7.16 | 6.06 | 4.94 | 3.68 | 2.37 | 1.09 | -0.88 | -2.97 | -5.09 | -7.45 | -9.74 | -22.28 | -30.06 | -33.93
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Leading the Way | Thermal headroom (MW) | 9.85 | 8.9 | 8.05 | 7.02 | 5.76 | 3.94 | 2.21 | 0.2 | -1.98 | -4.4 | -6.92 | -9.64 | -12.35 | -14.97 | -17.41 | -25.59 | -29.36 | -31.69
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Steady Progression | Thermal headroom (MW) | 9.85 | 9.55 | 9.39 | 9.2 | 8.98 | 8.53 | 8.08 | 7.57 | 7.05 | 6.47 | 5.64 | 4.8 | 3.89 | 2.92 | 1.98 | -1.93 | -3.63 | -4.83
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | System Transformation | Thermal headroom (MW) | 9.85 | 9.42 | 9.16 | 8.85 | 8.48 | 8.02 | 7.54 | 6.91 | 6.13 | 5.32 | 4.26 | 3.14 | 2.04 | 0.94 | -0.02 | -3.64 | -5.9 | -6.98
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | WPD Best View | Thermal headroom (MW) | 9.85 | 9.22 | 8.68 | 7.98 | 7.16 | 6.06 | 4.94 | 3.68 | 2.37 | 1.09 | -0.88 | -2.97 | -5.09 | -7.45 | -9.74 | -22.28 | -30.06 | -33.93
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Consumer Transformation | Thermal headroom (MW) | 11.5 | 11.5 | 11.31 | 11.16 | 10.96 | 10.79 | 10.62 | 10.38 | 10 | 9.57 | 8.99 | 8.24 | 7.24 | 6.42 | 5.63 | 0.56 | -2.47 | -3.94
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Leading the Way | Thermal headroom (MW) | 11.5 | 11.4 | 11.11 | 10.96 | 10.73 | 10.37 | 9.89 | 9.37 | 8.6 | 7.75 | 6.71 | 5.54 | 4.34 | 3.39 | 2.51 | -0.87 | -2.22 | -3.04
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Steady Progression | Thermal headroom (MW) | 11.5 | 11.6 | 11.53 | 11.5 | 11.46 | 11.34 | 11.2 | 11.13 | 10.97 | 10.78 | 10.46 | 10.11 | 9.69 | 9.35 | 9.01 | 6.97 | 5.98 | 5.73
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | System Transformation | Thermal headroom (MW) | 11.5 | 11.58 | 11.47 | 11.41 | 11.33 | 11.32 | 11.27 | 11.2 | 10.97 | 10.65 | 10.23 | 9.77 | 9.29 | 8.93 | 8.61 | 6.35 | 5.34 | 5.18
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | WPD Best View | Thermal headroom (MW) | 11.5 | 11.5 | 11.31 | 11.16 | 10.96 | 10.79 | 10.62 | 10.38 | 10 | 9.57 | 8.99 | 8.24 | 7.24 | 6.42 | 5.63 | 0.56 | -2.47 | -3.94
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Consumer Transformation | Thermal headroom (MW) | 6.32 | 6.21 | 5.91 | 5.5 | 5.05 | 4.36 | 3.68 | 2.96 | 2.14 | 1.3 | 0.21 | -1.38 | -3.22 | -4.95 | -6.62 | -17.79 | -24.75 | -28.21
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Leading the Way | Thermal headroom (MW) | 6.32 | 5.99 | 5.45 | 4.81 | 3.96 | 2.63 | 1.36 | -3.5527e-15 | -1.41 | -3.01 | -4.95 | -6.98 | -8.97 | -10.99 | -12.85 | -20.2 | -23.68 | -25.73
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Steady Progression | Thermal headroom (MW) | 6.32 | 6.47 | 6.47 | 6.42 | 6.37 | 6.13 | 5.86 | 5.52 | 5.06 | 4.57 | 3.93 | 3.25 | 2.52 | 1.76 | 0.99 | -3.67 | -6.9 | -8.29
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | System Transformation | Thermal headroom (MW) | 6.32 | 6.41 | 6.32 | 6.17 | 6 | 5.78 | 5.51 | 5.09 | 4.53 | 3.91 | 3.15 | 2.34 | 1.52 | 0.73 | 0.01 | -4.71 | -7.98 | -9.05
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | WPD Best View | Thermal headroom (MW) | 6.32 | 6.21 | 5.91 | 5.5 | 5.05 | 4.36 | 3.68 | 2.96 | 2.14 | 1.3 | 0.21 | -1.38 | -3.22 | -4.95 | -6.62 | -17.79 | -24.75 | -28.21
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Consumer Transformation | Thermal headroom (MW) | 14.37 | 14.53 | 14.62 | 14.7 | 14.78 | 14.86 | 14.91 | 14.95 | 14.99 | 14.99 | 15 | 15 | 15.01 | 15.02 | 15.03 | 15.22 | 15.52 | 15.84
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Leading the Way | Thermal headroom (MW) | 14.37 | 14.53 | 14.61 | 14.7 | 14.77 | 14.82 | 14.86 | 14.9 | 14.93 | 14.97 | 14.97 | 14.93 | 14.9 | 14.92 | 14.93 | 15.19 | 15.55 | 15.98
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Steady Progression | Thermal headroom (MW) | 14.37 | 14.53 | 14.62 | 14.7 | 14.79 | 14.87 | 14.95 | 15.04 | 15.12 | 15.2 | 15.28 | 15.31 | 15.35 | 15.38 | 15.42 | 15.5 | 15.67 | 15.95
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | System Transformation | Thermal headroom (MW) | 14.37 | 14.53 | 14.62 | 14.7 | 14.78 | 14.87 | 14.95 | 15.03 | 15.11 | 15.15 | 15.19 | 15.23 | 15.23 | 15.23 | 15.25 | 15.31 | 15.58 | 15.93
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | WPD Best View | Thermal headroom (MW) | 14.37 | 14.53 | 14.62 | 14.7 | 14.78 | 14.86 | 14.91 | 14.95 | 14.99 | 14.99 | 15 | 15 | 15.01 | 15.02 | 15.03 | 15.22 | 15.52 | 15.84
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Consumer Transformation | Thermal headroom (MW) | 7.49 | 7.34 | 7.05 | 5.37 | 4.77 | 3.88 | 2.68 | 1.26 | -0.26 | -2.03 | -4.86 | -7.73 | -10.59 | -13.36 | -16.02 | -31.29 | -40.25 | -44.41
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Leading the Way | Thermal headroom (MW) | 7.49 | 7.02 | 6.39 | 3.9 | 2.43 | 0.08 | -2.08 | -4.42 | -6.8 | -9.46 | -12.37 | -15.48 | -18.63 | -21.58 | -24.35 | -34.07 | -37.67 | -38.86
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Steady Progression | Thermal headroom (MW) | 7.49 | 7.68 | 7.73 | 6.61 | 6.49 | 6.12 | 5.71 | 5.28 | 4.81 | 4.05 | 2.95 | 1.85 | 0.83 | -0.31 | -1.52 | -9.47 | -14.5 | -16.62
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | System Transformation | Thermal headroom (MW) | 7.49 | 7.57 | 7.5 | 6.06 | 5.78 | 5.42 | 5.03 | 4.58 | 3.99 | 3.09 | 1.96 | 0.72 | -0.69 | -2.2 | -3.77 | -12.76 | -16.52 | -17.56
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | WPD Best View | Thermal headroom (MW) | 7.49 | 7.34 | 7.05 | 5.37 | 4.77 | 3.88 | 2.68 | 1.26 | -0.26 | -2.03 | -4.86 | -7.73 | -10.59 | -13.36 | -16.02 | -31.29 | -40.25 | -44.41
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Consumer Transformation | Thermal headroom (MW) | 5.79 | 5.73 | 5.61 | 5.45 | 5.21 | 4.87 | 4.38 | 3.86 | 3.32 | 2.49 | 0.76 | -0.8 | -2.37 | -3.93 | -5.53 | -12.59 | -19.42 | -23.98
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Leading the Way | Thermal headroom (MW) | 5.79 | 5.62 | 5.4 | 5.15 | 4.7 | 3.92 | 2.92 | 1.54 | -0.42 | -2.58 | -4.07 | -5.51 | -7.22 | -8.94 | -10.61 | -16.07 | -19.78 | -22.92
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Steady Progression | Thermal headroom (MW) | 5.79 | 5.84 | 5.82 | 5.8 | 5.75 | 5.58 | 5.3 | 5.02 | 4.7 | 4.31 | 3.79 | 3.29 | 2.74 | 2.2 | 1.62 | -1.85 | -3.37 | -3.95
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | System Transformation | Thermal headroom (MW) | 5.79 | 5.81 | 5.77 | 5.71 | 5.6 | 5.48 | 5.2 | 4.87 | 4.48 | 4.05 | 3.48 | 3.02 | 2.52 | 1.94 | 1.29 | -2.21 | -3.8 | -4.33
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | WPD Best View | Thermal headroom (MW) | 5.79 | 5.73 | 5.61 | 5.45 | 5.21 | 4.87 | 4.38 | 3.86 | 3.32 | 2.49 | 0.76 | -0.8 | -2.37 | -3.93 | -5.53 | -12.59 | -19.42 | -23.98
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Consumer Transformation | Thermal headroom (MW) | 4.11 | 3.9 | 3.68 | 3.5 | 3.24 | 2.71 | 2.2 | 1.62 | 1.07 | 0.47 | -0.54 | -1.55 | -2.56 | -3.53 | -4.49 | -10 | -13.2 | -14.79
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Leading the Way | Thermal headroom (MW) | 4.11 | 3.68 | 3.22 | 2.84 | 2.41 | 1.5 | 0.65 | -0.34 | -1.31 | -2.35 | -3.28 | -4.32 | -5.37 | -6.37 | -7.28 | -10.87 | -12.38 | -13.25
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Steady Progression | Thermal headroom (MW) | 4.11 | 4.02 | 3.96 | 3.91 | 3.8 | 3.51 | 3.22 | 2.92 | 2.65 | 2.36 | 1.91 | 1.45 | 1 | 0.5 | 0 | -3.16 | -4.58 | -5.15
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | System Transformation | Thermal headroom (MW) | 4.11 | 3.99 | 3.88 | 3.79 | 3.63 | 3.46 | 3.31 | 3.1 | 2.85 | 2.57 | 2.14 | 1.67 | 1.21 | 0.71 | 0.19 | -2.99 | -4.69 | -5.31
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | WPD Best View | Thermal headroom (MW) | 4.11 | 3.9 | 3.68 | 3.5 | 3.24 | 2.71 | 2.2 | 1.62 | 1.07 | 0.47 | -0.54 | -1.55 | -2.56 | -3.53 | -4.49 | -10 | -13.2 | -14.79
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Consumer Transformation | Thermal headroom (MW) | 2.24 | 2.32 | 2.32 | 2.32 | 2.3 | 1.99 | 1.7 | 1.43 | 1.16 | 0.87 | 0.43 | 0.01 | -0.48 | -0.95 | -1.43 | -4.01 | -5.34 | -6.06
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Leading the Way | Thermal headroom (MW) | 2.24 | 2.23 | 2.16 | 2.07 | 1.96 | 1.42 | 0.9 | 0.38 | -0.13 | -0.68 | -1.01 | -1.4 | -1.81 | -2.21 | -2.61 | -4.5 | -5.28 | -5.83
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Steady Progression | Thermal headroom (MW) | 2.24 | 2.31 | 2.32 | 2.33 | 2.32 | 2.17 | 2.02 | 1.87 | 1.71 | 1.56 | 1.31 | 1.04 | 0.77 | 0.49 | 0.21 | -1.59 | -2.27 | -2.5
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | System Transformation | Thermal headroom (MW) | 2.24 | 2.31 | 2.32 | 2.31 | 2.29 | 2.26 | 2.23 | 2.2 | 2.16 | 2.06 | 1.88 | 1.7 | 1.51 | 1.31 | 1.08 | -0.72 | -1.92 | -2.25
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | WPD Best View | Thermal headroom (MW) | 2.24 | 2.32 | 2.32 | 2.32 | 2.3 | 1.99 | 1.7 | 1.43 | 1.16 | 0.87 | 0.43 | 0.01 | -0.48 | -0.95 | -1.43 | -4.01 | -5.34 | -6.06
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Consumer Transformation | Thermal headroom (MW) | 5.72 | 5.48 | 4.95 | 4.33 | 3.49 | 1.2 | -0.71 | -2.79 | -5.14 | -7.74 | -12.56 | -17.45 | -22.17 | -26.72 | -31.25 | -52.56 | -68.71 | -78.34
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Leading the Way | Thermal headroom (MW) | 5.72 | 4.74 | 3.4 | 2.07 | 0.43 | -3.36 | -6.56 | -10.2 | -14.36 | -18.77 | -23.32 | -28.25 | -32.98 | -37.62 | -41.91 | -56.21 | -63.53 | -68.19
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Steady Progression | Thermal headroom (MW) | 5.72 | 6.05 | 6.11 | 6.13 | 6.1 | 5.1 | 4.28 | 3.38 | 2.33 | 0.98 | -0.74 | -2.1 | -3.5 | -5.04 | -6.57 | -17.02 | -22.99 | -24.73
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | System Transformation | Thermal headroom (MW) | 5.72 | 5.94 | 5.86 | 5.68 | 5.41 | 4.27 | 3.37 | 2.23 | 0.8 | -0.59 | -2.16 | -3.9 | -5.98 | -8.17 | -10.51 | -22.35 | -27.5 | -29.65
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | WPD Best View | Thermal headroom (MW) | 5.72 | 5.49 | 4.97 | 4.36 | 3.54 | 1.4 | -0.37 | -2.3 | -4.5 | -6.9 | -11.43 | -16.03 | -20.45 | -24.72 | -28.97 | -48.54 | -63.06 | -70.71
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Consumer Transformation | Thermal headroom (MW) | 57.78 | 56.9879 | 54.8651 | 52.5057 | 49.0168 | 43.8916 | 38.2303 | 31.9052 | 24.8995 | 16.5134 | 4.625 | -8.5621 | -22.0895 | -33.9098 | -45.1443 | -99.6051 | -130.1511 | -143.5796
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Leading the Way | Thermal headroom (MW) | 57.78 | 55.6097 | 51.9173 | 48.2018 | 42.802 | 35.2525 | 27.3495 | 17.5337 | 6.8433 | -4.7631 | -18.6128 | -32.4221 | -45.7239 | -57.7357 | -68.5584 | -103.4663 | -115.5371 | -117.1549
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Steady Progression | Thermal headroom (MW) | 57.78 | 58.8223 | 58.8054 | 58.7666 | 58.3646 | 56.8888 | 55.1033 | 52.9225 | 50.2883 | 47.2725 | 43.2091 | 39.1786 | 34.8949 | 30.2194 | 25.5433 | -4.5609 | -24.5717 | -32.9935
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | System Transformation | Thermal headroom (MW) | 57.78 | 58.2413 | 57.533 | 56.7554 | 55.4165 | 53.9383 | 51.7914 | 48.8245 | 45.1855 | 41.106 | 35.7881 | 30.2559 | 24.6032 | 17.7375 | 11.0288 | -19.6463 | -32.1894 | -33.8559
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | WPD Best View | Thermal headroom (MW) | 57.78 | 56.9879 | 54.8651 | 52.5057 | 49.0168 | 43.8958 | 38.2395 | 31.9203 | 24.9204 | 16.5418 | 4.6576 | -8.5254 | -22.0486 | -33.8647 | -45.0942 | -99.3431 | -129.8152 | -143.1782
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Consumer Transformation | Thermal headroom (MW) | 4.85 | 4.48 | 3.81 | 2.9 | 1.76 | 0.1 | -1.64 | -3.47 | -5.44 | -7.41 | -9.9 | -12.88 | -15.98 | -18.65 | -21.22 | -35.91 | -44.98 | -49.33
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Leading the Way | Thermal headroom (MW) | 4.85 | 4.17 | 3.17 | 1.94 | 0.36 | -2.12 | -4.51 | -7.22 | -9.99 | -12.87 | -16.34 | -19.86 | -23.03 | -25.81 | -28.35 | -38.33 | -43.23 | -45.91
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Steady Progression | Thermal headroom (MW) | 4.85 | 4.88 | 4.72 | 4.45 | 4.14 | 3.48 | 2.83 | 2.08 | 1.18 | 0.26 | -0.92 | -2.15 | -3.39 | -4.62 | -5.8 | -11.82 | -15.62 | -18.05
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | System Transformation | Thermal headroom (MW) | 4.85 | 4.77 | 4.46 | 4.02 | 3.51 | 2.77 | 1.94 | 0.87 | -0.37 | -1.63 | -3.2 | -4.83 | -6.3 | -7.95 | -9.46 | -15.93 | -19.85 | -21
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | WPD Best View | Thermal headroom (MW) | 4.85 | 4.48 | 3.81 | 2.9 | 1.76 | 0.11 | -1.63 | -3.46 | -5.42 | -7.37 | -9.86 | -12.83 | -15.93 | -18.6 | -21.16 | -35.59 | -44.57 | -48.84
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Consumer Transformation | Thermal headroom (MW) | 7.28 | 7.24 | 6.91 | 6.61 | 6.18 | 5.43 | 4.31 | 2.99 | 1.64 | 0.19 | -1.71 | -3.87 | -6.22 | -8.28 | -10.19 | -21.06 | -27.45 | -30.16
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Leading the Way | Thermal headroom (MW) | 7.28 | 7 | 6.38 | 5.84 | 5.02 | 3.72 | 2.05 | 0.01 | -1.98 | -4.13 | -6.73 | -9.09 | -11.36 | -13.54 | -15.54 | -22.93 | -26.17 | -27.5
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Steady Progression | Thermal headroom (MW) | 7.28 | 7.47 | 7.41 | 7.43 | 7.41 | 7.18 | 6.77 | 6.23 | 5.6 | 4.87 | 3.91 | 3.05 | 2.15 | 1.22 | 0.33 | -4.47 | -7.19 | -8.69
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | System Transformation | Thermal headroom (MW) | 7.28 | 7.41 | 7.26 | 7.19 | 7.06 | 6.86 | 6.32 | 5.54 | 4.65 | 3.63 | 2.35 | 1.26 | 0.21 | -1.16 | -2.37 | -7.31 | -9.97 | -10.68
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | WPD Best View | Thermal headroom (MW) | 7.28 | 7.24 | 6.91 | 6.61 | 6.18 | 5.43 | 4.31 | 2.99 | 1.64 | 0.19 | -1.71 | -3.87 | -6.22 | -8.28 | -10.19 | -21.06 | -27.45 | -30.16
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Consumer Transformation | Thermal headroom (MW) | 17.09 | 17.13 | 17.07 | 16.9 | 16.51 | 15.92 | 15.42 | 14.88 | 14.27 | 13.44 | 11.87 | 10.27 | 8.7 | 7.21 | 5.71 | -1.04 | -5.09 | -6.93
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Leading the Way | Thermal headroom (MW) | 17.09 | 16.94 | 16.66 | 16.3 | 15.63 | 14.63 | 13.84 | 12.79 | 11.7 | 10.45 | 8.89 | 7.25 | 5.6 | 4.1 | 2.71 | -1.9 | -3.34 | -3.44
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Steady Progression | Thermal headroom (MW) | 17.09 | 17.33 | 17.44 | 17.49 | 17.4 | 17.21 | 17.08 | 16.94 | 16.73 | 16.47 | 16.09 | 15.69 | 15.28 | 14.84 | 14.41 | 10.55 | 7.39 | 5.91
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | System Transformation | Thermal headroom (MW) | 17.09 | 17.26 | 17.3 | 17.27 | 17.05 | 16.87 | 16.77 | 16.62 | 16.37 | 16.05 | 15.59 | 15.1 | 14.59 | 14.11 | 13.67 | 9.64 | 7.99 | 7.59
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | WPD Best View | Thermal headroom (MW) | 17.09 | 17.13 | 17.07 | 16.9 | 16.51 | 15.92 | 15.42 | 14.88 | 14.27 | 13.44 | 11.87 | 10.27 | 8.7 | 7.21 | 5.71 | -1.04 | -5.09 | -6.93
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Consumer Transformation | Thermal headroom (MW) | 13.75 | 13.65 | 13.36 | 12.82 | 12.04 | 10.92 | 9.81 | 8.61 | 7.25 | 5.35 | 2.13 | -1.49 | -5.11 | -8.29 | -11.31 | -24.83 | -33.13 | -36.86
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Leading the Way | Thermal headroom (MW) | 13.75 | 13.24 | 12.52 | 11.55 | 10.26 | 8.65 | 6.99 | 4.73 | 2.42 | -0.16 | -3.28 | -6.55 | -9.84 | -12.96 | -15.8 | -24.47 | -27.48 | -27.3
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Steady Progression | Thermal headroom (MW) | 13.75 | 14.1 | 14.27 | 14.31 | 14.3 | 14.03 | 13.73 | 13.37 | 13.02 | 12.52 | 11.8 | 11.07 | 10.29 | 9.46 | 8.62 | -0.32 | -7.45 | -10.52
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | System Transformation | Thermal headroom (MW) | 13.75 | 13.94 | 13.93 | 13.74 | 13.44 | 13.22 | 12.93 | 12.56 | 12.11 | 11.55 | 10.73 | 9.86 | 8.95 | 7.33 | 5.39 | -3.48 | -7.23 | -8.02
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | WPD Best View | Thermal headroom (MW) | 13.75 | 13.65 | 13.36 | 12.82 | 12.04 | 10.92 | 9.81 | 8.61 | 7.25 | 5.35 | 2.13 | -1.49 | -5.11 | -8.29 | -11.31 | -24.83 | -33.13 | -36.86
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Consumer Transformation | Thermal headroom (MW) | 17.83 | 17.36 | 16.61 | 16.13 | 15.44 | 14.55 | 13.71 | 12.78 | 11.46 | 9.99 | 8.26 | 6.42 | 4.66 | 3.35 | 2.14 | -1.1 | -1.34 | -0.97
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Leading the Way | Thermal headroom (MW) | 17.83 | 17.22 | 16.28 | 15.71 | 14.91 | 14.09 | 13.23 | 12.19 | 10.57 | 8.83 | 7.09 | 5.25 | 3.46 | 2.28 | 1.29 | 0.27 | 1.75 | 4.1
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Steady Progression | Thermal headroom (MW) | 17.83 | 17.83 | 17.72 | 17.72 | 17.68 | 17.51 | 17.33 | 17.1 | 16.75 | 16.41 | 15.94 | 15.37 | 14.7 | 14.06 | 13.38 | 9.6 | 7.74 | 8.27
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | System Transformation | Thermal headroom (MW) | 17.83 | 17.69 | 17.4 | 17.27 | 17.07 | 16.89 | 16.65 | 16.33 | 15.78 | 15.2 | 14.47 | 13.61 | 12.65 | 11.72 | 10.72 | 6.91 | 7.22 | 8.46
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | WPD Best View | Thermal headroom (MW) | 17.83 | 17.36 | 16.61 | 16.13 | 15.44 | 14.55 | 13.71 | 12.78 | 11.46 | 9.99 | 8.26 | 6.42 | 4.66 | 3.35 | 2.14 | -1.1 | -1.34 | -0.97
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Consumer Transformation | Thermal headroom (MW) | 16.94 | 16.87 | 16.65 | 16.37 | 15.88 | 15.32 | 14.82 | 14.3 | 13.66 | 12.33 | 10.39 | 8.34 | 6.34 | 4.52 | 2.79 | -3.55 | -6.07 | -7.31
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Leading the Way | Thermal headroom (MW) | 16.94 | 16.7 | 16.3 | 15.87 | 15.19 | 14.56 | 14 | 13.21 | 11.85 | 10.33 | 8.47 | 6.46 | 4.49 | 2.66 | 1.13 | -1.89 | -1.72 | -0.05
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Steady Progression | Thermal headroom (MW) | 16.94 | 17.2 | 17.33 | 17.41 | 17.45 | 17.4 | 17.35 | 17.28 | 17.21 | 17.1 | 16.89 | 16.68 | 16.4 | 15.68 | 14.86 | 9.47 | 5.74 | 4.9
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | System Transformation | Thermal headroom (MW) | 16.94 | 17.07 | 17.05 | 16.99 | 16.84 | 16.8 | 16.77 | 16.69 | 16.63 | 16.52 | 16.31 | 15.61 | 14.61 | 13.48 | 12.31 | 7.23 | 6.35 | 7.13
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | WPD Best View | Thermal headroom (MW) | 16.94 | 16.87 | 16.65 | 16.37 | 15.88 | 15.32 | 14.82 | 14.3 | 13.66 | 12.33 | 10.39 | 8.34 | 6.34 | 4.52 | 2.79 | -3.55 | -6.07 | -7.31
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Consumer Transformation | Thermal headroom (MW) | 40.9563 | 40.1233 | 38.0071 | 35.4512 | 31.2712 | 24.1479 | 16.631 | 9.4332 | 1.2059 | -8.4651 | -22.8683 | -38.5944 | -54.9888 | -70.519 | -85.695 | -161.6814 | -202.9093 | -222.8786
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Leading the Way | Thermal headroom (MW) | 40.9563 | 38.0777 | 33.796 | 28.952 | 21.9066 | 11.5296 | 0.61529 | -10.5765 | -23.2982 | -37.8284 | -53.993 | -71.1557 | -88.1342 | -104.3338 | -119.3278 | -169.6516 | -187.3164 | -191.3547
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Steady Progression | Thermal headroom (MW) | 40.9563 | 42.4951 | 42.8906 | 43.2309 | 42.9733 | 40.8398 | 38.4109 | 35.8024 | 32.7554 | 29.215 | 24.5533 | 19.6483 | 14.4502 | 8.8891 | 2.8444 | -37.2807 | -65.5162 | -77.6824
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | System Transformation | Thermal headroom (MW) | 40.9563 | 41.7909 | 41.3387 | 40.7659 | 39.312 | 36.9985 | 33.6463 | 30.3722 | 26.2891 | 21.5646 | 15.8793 | 9.42 | 2.5071 | -5.0175 | -13.1496 | -53.8233 | -71.0929 | -74.9839
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | WPD Best View | Thermal headroom (MW) | 40.9563 | 40.1888 | 38.1448 | 35.6879 | 31.6811 | 24.7113 | 17.3669 | 10.2749 | 2.1394 | -7.4495 | -21.5823 | -36.8805 | -52.9804 | -68.199 | -83.1329 | -157.495 | -197.7877 | -217.0737
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Consumer Transformation | Thermal headroom (MW) | 7.13 | 7.15 | 6.9 | 6.53 | 5.8 | 5.02 | 4.26 | 3.46 | 2.56 | 1.57 | 0.24 | -1.1 | -2.47 | -3.96 | -5.46 | -13.85 | -16.66 | -17.83
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Leading the Way | Thermal headroom (MW) | 7.13 | 6.95 | 6.51 | 5.98 | 5 | 3.98 | 3.01 | 1.81 | 0.56 | -0.9 | -2.34 | -3.87 | -5.4 | -7 | -8.5 | -15.5 | -16.89 | -17.11
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Steady Progression | Thermal headroom (MW) | 7.13 | 7.35 | 7.38 | 7.41 | 7.24 | 7.11 | 6.99 | 6.86 | 6.67 | 6.41 | 6.07 | 5.72 | 5.36 | 4.92 | 4.44 | 1.2 | -0.48 | -1.12
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | System Transformation | Thermal headroom (MW) | 7.13 | 7.3 | 7.26 | 7.22 | 6.92 | 6.73 | 6.43 | 6.07 | 5.68 | 5.26 | 4.8 | 4.25 | 3.71 | 3.08 | 2.39 | -1.92 | -2.98 | -3.14
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | WPD Best View | Thermal headroom (MW) | 7.13 | 7.15 | 6.9 | 6.53 | 5.8 | 5.02 | 4.26 | 3.46 | 2.56 | 1.57 | 0.24 | -1.1 | -2.47 | -3.96 | -5.46 | -13.85 | -16.66 | -17.83
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Consumer Transformation | Thermal headroom (MW) | 7.49 | 7.45 | 7.25 | 7.17 | 7.01 | 6.5 | 6.24 | 5.97 | 5.68 | 4.8 | 3.5 | 2.14 | 0.83 | -0.35 | -1.49 | -5.48 | -6.63 | -7.14
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Leading the Way | Thermal headroom (MW) | 7.49 | 7.34 | 7 | 6.83 | 6.58 | 5.96 | 5.72 | 5.36 | 4.46 | 3.42 | 2.19 | 0.84 | -0.47 | -1.66 | -2.64 | -4.35 | -3.9 | -2.63
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Steady Progression | Thermal headroom (MW) | 7.49 | 7.71 | 7.79 | 7.95 | 8.08 | 7.95 | 7.96 | 7.94 | 7.9 | 7.86 | 7.72 | 7.56 | 7.35 | 7.11 | 6.61 | 3.13 | 0.81 | 0.45
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | System Transformation | Thermal headroom (MW) | 7.49 | 7.61 | 7.6 | 7.68 | 7.7 | 7.55 | 7.6 | 7.61 | 7.6 | 7.55 | 7.37 | 7.11 | 6.58 | 5.85 | 5.1 | 1.82 | 1.42 | 2.01
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | WPD Best View | Thermal headroom (MW) | 7.49 | 7.45 | 7.25 | 7.17 | 7.01 | 6.5 | 6.24 | 5.97 | 5.68 | 4.8 | 3.5 | 2.14 | 0.83 | -0.35 | -1.49 | -5.48 | -6.63 | -7.14
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Consumer Transformation | Thermal headroom (MW) | 4.092 | 3.722 | 3.272 | 2.702 | 1.882 | 0.522 | -0.798 | -2.178 | -3.718 | -5.518 | -8.468 | -11.448 | -14.508 | -17.398 | -20.228 | -32.008 | -37.408 | -39.948
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Leading the Way | Thermal headroom (MW) | 4.092 | 3.262 | 2.332 | 1.332 | -0.038 | -1.658 | -3.258 | -5.118 | -7.118 | -9.398 | -12.298 | -15.318 | -18.348 | -21.198 | -23.838 | -31.018 | -32.718 | -31.538
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Steady Progression | Thermal headroom (MW) | 4.092 | 4.272 | 4.332 | 4.322 | 4.202 | 3.792 | 3.372 | 2.852 | 2.342 | 1.722 | 0.912 | 0.072 | -0.848 | -1.858 | -2.968 | -11.208 | -17.848 | -20.808
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | System Transformation | Thermal headroom (MW) | 4.092 | 4.112 | 3.942 | 3.732 | 3.372 | 2.962 | 2.492 | 1.942 | 1.302 | 0.502 | -0.488 | -1.648 | -3.028 | -4.498 | -6.108 | -14.428 | -17.398 | -17.378
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | WPD Best View | Thermal headroom (MW) | 4.092 | 3.722 | 3.272 | 2.702 | 1.882 | 0.522 | -0.798 | -2.178 | -3.718 | -5.518 | -8.468 | -11.448 | -14.508 | -17.398 | -20.228 | -32.008 | -37.408 | -39.948
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Consumer Transformation | Thermal headroom (MW) | 3.984 | 3.954 | 3.694 | 3.424 | 2.924 | 1.734 | 0.564 | -0.756 | -2.416 | -4.266 | -7.486 | -11.096 | -14.756 | -17.956 | -21.056 | -35.166 | -43.756 | -47.706
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Leading the Way | Thermal headroom (MW) | 3.984 | 3.534 | 2.834 | 2.174 | 0.954 | -0.646 | -2.596 | -4.736 | -6.996 | -9.516 | -12.746 | -16.146 | -19.506 | -22.756 | -25.756 | -35.186 | -38.866 | -39.326
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Steady Progression | Thermal headroom (MW) | 3.984 | 4.294 | 4.374 | 4.494 | 4.534 | 4.254 | 3.964 | 3.624 | 3.244 | 2.754 | 2.024 | 1.274 | 0.474 | -0.366 | -1.236 | -10.056 | -17.396 | -20.816
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | System Transformation | Thermal headroom (MW) | 3.984 | 4.154 | 4.084 | 4.024 | 3.844 | 3.564 | 3.254 | 2.864 | 2.284 | 1.624 | 0.584 | -0.526 | -1.706 | -3.196 | -5.026 | -14.046 | -18.036 | -18.926
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | WPD Best View | Thermal headroom (MW) | 3.984 | 3.954 | 3.694 | 3.424 | 2.924 | 1.734 | 0.564 | -0.756 | -2.416 | -4.266 | -7.486 | -11.096 | -14.756 | -17.956 | -21.056 | -35.166 | -43.756 | -47.706
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Consumer Transformation | Thermal headroom (MW) | 4.53 | 4.28 | 3.86 | 3.3 | 2.4 | 1.23 | 0 | -1.19 | -2.45 | -3.78 | -5.48 | -7.3 | -9.67 | -12.04 | -14.34 | -26.69 | -35.09 | -39.62
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Leading the Way | Thermal headroom (MW) | 4.53 | 3.97 | 3.2 | 2.32 | 1.07 | -0.71 | -2.47 | -4.29 | -6.15 | -8.44 | -10.95 | -13.54 | -16.17 | -18.71 | -21.06 | -29.32 | -33.37 | -35.52
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Steady Progression | Thermal headroom (MW) | 4.53 | 4.7 | 4.72 | 4.7 | 4.59 | 4.22 | 3.71 | 3.14 | 2.5 | 1.76 | 0.86 | -0.08 | -1.08 | -2.13 | -3.16 | -8.61 | -11.56 | -13.47
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | System Transformation | Thermal headroom (MW) | 4.53 | 4.57 | 4.46 | 4.26 | 3.95 | 3.59 | 3.06 | 2.42 | 1.67 | 0.77 | -0.16 | -1.15 | -2.13 | -3.09 | -4.12 | -8.11 | -10.81 | -12.14
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | WPD Best View | Thermal headroom (MW) | 4.53 | 4.32 | 3.94 | 3.45 | 2.66 | 1.59 | 0.46 | -0.69 | -1.91 | -3.21 | -4.83 | -6.44 | -8.68 | -10.92 | -13.12 | -24.54 | -32.34 | -36.52
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Consumer Transformation | Thermal headroom (MW) | 3.41 | 3.46 | 3.31 | 3.14 | 2.85 | 1.9 | 0.42 | -0.49 | -1.7 | -2.85 | -4.54 | -6.39 | -8.23 | -9.96 | -11.63 | -19.66 | -23.9 | -25.57
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Leading the Way | Thermal headroom (MW) | 3.41 | 3.19 | 2.81 | 2.39 | 1.75 | 0.28 | -1.88 | -3.29 | -5.03 | -6.53 | -8.25 | -10.3 | -12.16 | -13.94 | -15.65 | -21.15 | -22.98 | -23.09
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Steady Progression | Thermal headroom (MW) | 3.41 | 3.73 | 3.87 | 4.01 | 4.11 | 3.71 | 3.09 | 2.66 | 2.06 | 1.53 | 0.86 | 0.08 | -0.66 | -1.5 | -2.38 | -7.92 | -11.16 | -12.06
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | System Transformation | Thermal headroom (MW) | 3.41 | 3.69 | 3.79 | 3.88 | 3.84 | 3.35 | 2.24 | 1.67 | 0.89 | 0.23 | -0.5 | -1.49 | -2.44 | -3.5 | -4.65 | -10.62 | -12.74 | -12.79
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | WPD Best View | Thermal headroom (MW) | 3.41 | 3.46 | 3.31 | 3.14 | 2.85 | 1.9 | 0.42 | -0.49 | -1.7 | -2.85 | -4.54 | -6.39 | -8.23 | -9.96 | -11.63 | -19.66 | -23.9 | -25.57
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Consumer Transformation | Thermal headroom (MW) | 3.72 | 3.53 | 3.15 | 2.6 | 1.83 | 0.52 | -0.98 | -2.47 | -4.07 | -5.95 | -8.59 | -11.83 | -15.01 | -18.02 | -21 | -39.29 | -50.38 | -56.05
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Leading the Way | Thermal headroom (MW) | 3.72 | 3.18 | 2.4 | 1.17 | -0.24 | -2.66 | -5.21 | -7.84 | -10.78 | -14.37 | -17.81 | -21.39 | -24.95 | -28.25 | -31.35 | -43.22 | -48.8 | -51.98
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Steady Progression | Thermal headroom (MW) | 3.72 | 3.9 | 3.9 | 3.84 | 3.73 | 3.29 | 2.72 | 2.07 | 1.32 | 0.41 | -0.73 | -1.92 | -3.16 | -4.42 | -5.68 | -12.37 | -17.58 | -20
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | System Transformation | Thermal headroom (MW) | 3.72 | 3.79 | 3.67 | 3.45 | 3.16 | 2.67 | 1.86 | 1 | -0.01 | -1.33 | -2.77 | -4.33 | -5.85 | -7.24 | -8.6 | -15.88 | -20.38 | -22.35
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | WPD Best View | Thermal headroom (MW) | 3.72 | 3.55 | 3.19 | 2.67 | 1.94 | 0.69 | -0.77 | -2.2 | -3.75 | -5.59 | -8.06 | -11.1 | -14.14 | -17 | -19.85 | -37.59 | -48.42 | -53.81
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Consumer Transformation | Thermal headroom (MW) | 73.0323 | 72.0853 | 70.5352 | 68.7076 | 66.1576 | 62.6711 | 59.2041 | 55.8081 | 52.2092 | 47.8601 | 40.1925 | 32.167 | 24.053 | 16.3273 | 8.6926 | -23.1933 | -45.9943 | -58.6479
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Leading the Way | Thermal headroom (MW) | 73.0323 | 70.8309 | 68.0172 | 64.9474 | 60.9413 | 56.1753 | 51.3103 | 45.9708 | 39.9347 | 33.5245 | 26.5796 | 19.042 | 11.3465 | 3.9472 | -2.9247 | -23.5657 | -32.4184 | -35.7313
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Steady Progression | Thermal headroom (MW) | 73.0323 | 73.1438 | 72.8233 | 72.3518 | 71.553 | 70.374 | 69.0446 | 67.6808 | 66.4136 | 64.6681 | 62.3412 | 60.4834 | 58.3629 | 55.8208 | 52.9554 | 34.6227 | 20.6362 | 14.7099
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | System Transformation | Thermal headroom (MW) | 73.0323 | 72.8125 | 72.0629 | 71.1592 | 69.7315 | 68.388 | 66.8741 | 65.3807 | 63.91 | 62.3158 | 59.5721 | 56.3564 | 52.9538 | 49.2117 | 45.5346 | 25.4641 | 16.8894 | 15.0952
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | WPD Best View | Thermal headroom (MW) | 73.0323 | 72.0853 | 70.5352 | 68.7076 | 66.1576 | 62.6711 | 59.2041 | 55.8081 | 52.2092 | 47.8601 | 40.1925 | 32.167 | 24.053 | 16.3273 | 8.6926 | -23.1933 | -45.9943 | -58.6479
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Consumer Transformation | Thermal headroom (MW) | 13.67 | 13.71 | 13.56 | 13.2 | 12.91 | 12.26 | 11.35 | 10.44 | 9.78 | 9 | 7.49 | 5.96 | 4.37 | 2.83 | 1.32 | -6.2 | -10.63 | -12.36
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Leading the Way | Thermal headroom (MW) | 13.67 | 13.3 | 12.76 | 11.99 | 11.32 | 10.24 | 8.81 | 7.27 | 6.18 | 4.96 | 3.44 | 1.9 | 0.33 | -1.26 | -2.73 | -7.04 | -8.37 | -8.31
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Steady Progression | Thermal headroom (MW) | 13.67 | 14 | 14.15 | 14.14 | 14.24 | 14.11 | 13.78 | 13.42 | 13.19 | 12.91 | 12.51 | 12.14 | 11.66 | 11.18 | 10.66 | 6.76 | 4.03 | 3.19
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | System Transformation | Thermal headroom (MW) | 13.67 | 13.91 | 13.97 | 13.83 | 13.8 | 13.65 | 13.2 | 12.72 | 12.49 | 12.23 | 11.79 | 11.26 | 10.69 | 10.12 | 9.48 | 5.67 | 4.17 | 4.11
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | WPD Best View | Thermal headroom (MW) | 13.67 | 13.71 | 13.56 | 13.2 | 12.91 | 12.26 | 11.35 | 10.44 | 9.78 | 9 | 7.49 | 5.96 | 4.37 | 2.83 | 1.32 | -6.2 | -10.63 | -12.36
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Consumer Transformation | Thermal headroom (MW) | 8.68 | 8.12 | 6.93 | 5.73 | 4.12 | 2.19 | 0.04 | -1.86 | -3.85 | -5.86 | -8.74 | -11.52 | -14.27 | -16.96 | -19.67 | -32.96 | -40.19 | -43.82
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Leading the Way | Thermal headroom (MW) | 8.68 | 7.57 | 5.83 | 4.02 | 1.73 | -0.92 | -3.86 | -6.65 | -9.56 | -12.36 | -15.5 | -18.64 | -21.63 | -24.49 | -27.15 | -35.88 | -39.5 | -41.24
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Steady Progression | Thermal headroom (MW) | 8.68 | 8.52 | 7.89 | 7.3 | 6.5 | 5.71 | 4.71 | 3.82 | 2.91 | 2.11 | 1.03 | -0.01 | -1.15 | -2.34 | -3.55 | -10.39 | -14.83 | -16.63
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | System Transformation | Thermal headroom (MW) | 8.68 | 8.4 | 7.58 | 6.78 | 5.73 | 4.73 | 3.46 | 2.45 | 1.25 | 0.19 | -1.16 | -2.63 | -4.07 | -5.48 | -6.83 | -14.48 | -17.81 | -18.74
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | WPD Best View | Thermal headroom (MW) | 8.68 | 8.12 | 6.93 | 5.73 | 4.12 | 2.19 | 0.04 | -1.86 | -3.85 | -5.86 | -8.74 | -11.52 | -14.27 | -16.96 | -19.67 | -32.96 | -40.19 | -43.82
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Consumer Transformation | Thermal headroom (MW) | 5.14 | 4.97 | 4.63 | 4.19 | 3.62 | 2.53 | 1.59 | 0.64 | -0.39 | -1.55 | -3.86 | -6.35 | -9.14 | -11.76 | -14.2 | -27.4 | -35.99 | -40.17
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Leading the Way | Thermal headroom (MW) | 5.14 | 4.37 | 3.35 | 2.31 | 1.13 | -0.64 | -2.28 | -4.07 | -5.82 | -7.77 | -10.14 | -12.9 | -15.77 | -18.52 | -21.05 | -30.51 | -34.87 | -37.64
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Steady Progression | Thermal headroom (MW) | 5.14 | 5.36 | 5.41 | 5.44 | 5.42 | 5.08 | 4.75 | 4.4 | 4.05 | 3.63 | 2.95 | 2.24 | 1.49 | 0.54 | -0.43 | -7.03 | -12.23 | -14.65
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | System Transformation | Thermal headroom (MW) | 5.14 | 5.25 | 5.17 | 5.04 | 4.84 | 4.55 | 4.29 | 3.94 | 3.6 | 3.1 | 2.22 | 1.04 | -0.22 | -1.4 | -2.38 | -9.85 | -13.65 | -14.97
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | WPD Best View | Thermal headroom (MW) | 5.14 | 4.97 | 4.63 | 4.19 | 3.62 | 2.53 | 1.59 | 0.64 | -0.39 | -1.55 | -3.86 | -6.35 | -9.14 | -11.76 | -14.2 | -27.4 | -35.99 | -40.17
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Consumer Transformation | Thermal headroom (MW) | 13.45 | 12.92 | 12.39 | 11.85 | 11.12 | 10.08 | 9.17 | 8.25 | 7.28 | 5.8 | 2.64 | -0.55 | -3.72 | -6.88 | -10.08 | -20.76 | -31.83 | -39.06
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Leading the Way | Thermal headroom (MW) | 13.45 | 12.54 | 11.66 | 10.79 | 9.63 | 8.36 | 7.13 | 5.78 | 3.59 | 1.2 | -1.03 | -3.56 | -6.31 | -8.99 | -11.54 | -18.51 | -22.21 | -24
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Steady Progression | Thermal headroom (MW) | 13.45 | 13.32 | 13.27 | 13.17 | 12.98 | 12.67 | 12.37 | 12.01 | 11.66 | 10.82 | 9.8 | 9.25 | 8.68 | 7.9 | 6.9 | 0.83 | -4.28 | -6.77
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | System Transformation | Thermal headroom (MW) | 13.45 | 13.21 | 12.99 | 12.76 | 12.35 | 12.04 | 11.78 | 11.46 | 11.12 | 10.68 | 9.7 | 8.68 | 7.57 | 6.37 | 5.15 | -1.44 | -4.4 | -5.42
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | WPD Best View | Thermal headroom (MW) | 13.45 | 12.92 | 12.39 | 11.85 | 11.12 | 10.08 | 9.17 | 8.25 | 7.28 | 5.8 | 2.64 | -0.55 | -3.72 | -6.88 | -10.08 | -20.76 | -31.83 | -39.06
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Consumer Transformation | Thermal headroom (MW) | 11.304 | 11.304 | 11.244 | 10.974 | 10.314 | 9.594 | 8.984 | 8.274 | 7.274 | 6.114 | 4.514 | 2.444 | 0.424 | -1.196 | -2.736 | -8.316 | -10.406 | -11.116
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Leading the Way | Thermal headroom (MW) | 11.304 | 11.184 | 11.004 | 10.604 | 9.714 | 8.844 | 8.194 | 7.004 | 5.824 | 4.494 | 2.894 | 1.144 | -0.566 | -2.106 | -3.476 | -6.496 | -6.886 | -5.456
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Steady Progression | Thermal headroom (MW) | 11.304 | 11.464 | 11.544 | 11.544 | 11.324 | 11.074 | 10.904 | 10.714 | 10.594 | 10.444 | 10.224 | 9.974 | 9.524 | 8.944 | 8.244 | 3.024 | -1.016 | -2.336
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | System Transformation | Thermal headroom (MW) | 11.304 | 11.384 | 11.394 | 11.304 | 10.924 | 10.604 | 10.374 | 10.104 | 9.924 | 9.694 | 9.194 | 8.414 | 7.514 | 6.124 | 4.694 | -1.066 | -2.826 | -2.056
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | WPD Best View | Thermal headroom (MW) | 11.304 | 11.304 | 11.244 | 10.974 | 10.314 | 9.594 | 8.984 | 8.274 | 7.274 | 6.114 | 4.514 | 2.444 | 0.424 | -1.196 | -2.736 | -8.316 | -10.406 | -11.116
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Consumer Transformation | Thermal headroom (MW) | 18.99 | 18.71 | 18.24 | 17.65 | 16.8 | 15.38 | 14.15 | 12.88 | 11.49 | 9.83 | 6.75 | 3.3 | -0.25 | -3.3 | -6.27 | -22.72 | -33.21 | -38.33
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Leading the Way | Thermal headroom (MW) | 18.99 | 17.96 | 16.74 | 15.46 | 13.94 | 11.73 | 9.71 | 7.54 | 5.24 | 2.62 | -0.61 | -4.01 | -7.48 | -10.8 | -13.89 | -24.96 | -30.19 | -32.7
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Steady Progression | Thermal headroom (MW) | 18.99 | 19.15 | 19.19 | 19.16 | 19.04 | 18.57 | 18.12 | 17.67 | 17.09 | 16.44 | 15.54 | 14.66 | 13.77 | 12.71 | 11.61 | 3.33 | -2.9 | -5.75
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | System Transformation | Thermal headroom (MW) | 18.99 | 19.01 | 18.84 | 18.62 | 18.28 | 17.84 | 17.39 | 16.87 | 16.26 | 15.55 | 14.5 | 13.32 | 12.01 | 10.25 | 8.41 | -0.69 | -5 | -6.45
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | WPD Best View | Thermal headroom (MW) | 18.99 | 18.79 | 18.4 | 17.91 | 17.22 | 16.05 | 15.04 | 14.02 | 12.84 | 11.5 | 9.02 | 6.5 | 3.86 | 0.92 | -1.96 | -17.28 | -26.24 | -30.11
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Consumer Transformation | Thermal headroom (MW) | 18.3348 | 17.1897 | 15.314 | 12.9235 | 10.1669 | 6.3695 | 2.8336 | -0.77477 | -4.6285 | -9.2911 | -17.1851 | -26.229 | -35.4021 | -44.2896 | -52.9524 | -99.7167 | -131.8656 | -149.5685
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Leading the Way | Thermal headroom (MW) | 18.3348 | 15.9221 | 12.5688 | 8.5503 | 4.219 | -1.9851 | -7.8147 | -14.0154 | -20.9876 | -29.4175 | -38.1367 | -47.6747 | -57.3616 | -66.7855 | -75.4624 | -107.9369 | -123.5068 | -132.4155
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Steady Progression | Thermal headroom (MW) | 18.3348 | 18.5331 | 18.057 | 17.4119 | 16.9357 | 15.5872 | 14.1825 | 12.6123 | 10.7834 | 8.2881 | 5.2234 | 2.4221 | -0.57568 | -3.8485 | -7.152 | -28.705 | -43.7767 | -51.3459
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | System Transformation | Thermal headroom (MW) | 18.3348 | 18.2297 | 17.2945 | 16.188 | 15.1014 | 13.6967 | 12.1628 | 10.4321 | 8.4576 | 5.7572 | 2.2297 | -1.6299 | -5.8427 | -10.1918 | -14.6776 | -39.395 | -51.7493 | -55.8125
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | WPD Best View | Thermal headroom (MW) | 18.3348 | 17.5823 | 16.1037 | 14.1956 | 12.2369 | 9.358 | 6.5981 | 3.6262 | 0.30943 | -3.8475 | -10.0374 | -16.3375 | -22.7575 | -29.0322 | -34.9807 | -72.4595 | -93.809 | -103.9039
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Consumer Transformation | Thermal headroom (MW) | 9.89 | 9.78 | 9.54 | 9.13 | 8.79 | 8.26 | 7.78 | 7.24 | 6.67 | 5.97 | 4.76 | 3.56 | 2.3 | 1.12 | 0.01 | -6.45 | -10.37 | -12.2
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Leading the Way | Thermal headroom (MW) | 9.89 | 9.53 | 9.02 | 8.38 | 7.81 | 6.96 | 6.17 | 5.3 | 4.34 | 3.31 | 2.07 | 0.72 | -0.62 | -1.95 | -3.14 | -7.91 | -9.87 | -10.71
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Steady Progression | Thermal headroom (MW) | 9.89 | 9.99 | 9.96 | 9.81 | 9.77 | 9.61 | 9.46 | 9.31 | 9.1 | 8.82 | 8.49 | 8.13 | 7.73 | 7.34 | 6.86 | 3.32 | 0.87 | -0.3
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | System Transformation | Thermal headroom (MW) | 9.89 | 9.95 | 9.82 | 9.61 | 9.51 | 9.34 | 9.2 | 9 | 8.79 | 8.49 | 8.05 | 7.58 | 6.97 | 6.34 | 5.69 | 1.5 | -0.31 | -0.71
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | WPD Best View | Thermal headroom (MW) | 9.89 | 9.78 | 9.54 | 9.13 | 8.79 | 8.26 | 7.78 | 7.24 | 6.67 | 5.97 | 4.76 | 3.56 | 2.3 | 1.12 | 0.01 | -6.45 | -10.37 | -12.2
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Consumer Transformation | Thermal headroom (MW) | 7.32 | 7.04 | 6.52 | 5.97 | 5.41 | 4.65 | 3.98 | 3.29 | 2.5 | 1.54 | 0.02 | -1.56 | -3.12 | -4.61 | -6.04 | -15.04 | -20.18 | -22.74
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Leading the Way | Thermal headroom (MW) | 7.32 | 6.71 | 5.78 | 4.88 | 3.99 | 2.75 | 1.6 | 0.32 | -0.97 | -2.49 | -4.09 | -5.87 | -7.62 | -9.27 | -10.78 | -16.85 | -19.37 | -20.53
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Steady Progression | Thermal headroom (MW) | 7.32 | 7.32 | 7.09 | 6.93 | 6.81 | 6.54 | 6.32 | 6.04 | 5.72 | 5.39 | 4.93 | 4.43 | 3.92 | 3.32 | 2.73 | -1.58 | -4.47 | -5.77
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | System Transformation | Thermal headroom (MW) | 7.32 | 7.24 | 6.92 | 6.64 | 6.37 | 6.08 | 5.82 | 5.54 | 5.25 | 4.8 | 4.25 | 3.61 | 2.87 | 2.08 | 1.24 | -3.97 | -6.22 | -6.72
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | WPD Best View | Thermal headroom (MW) | 7.32 | 7.04 | 6.52 | 5.97 | 5.41 | 4.65 | 3.98 | 3.29 | 2.5 | 1.54 | 0.02 | -1.56 | -3.12 | -4.61 | -6.04 | -15.04 | -20.18 | -22.74
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Consumer Transformation | Thermal headroom (MW) | 8.49 | 7.83 | 6.92 | 5.79 | 4.12 | 1.94 | -0.18 | -2.24 | -4.38 | -6.92 | -11.38 | -17.05 | -22.79 | -28.47 | -34.11 | -61.72 | -83.25 | -96.11
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Leading the Way | Thermal headroom (MW) | 8.49 | 7.34 | 5.86 | 3.85 | 1.32 | -2.3 | -5.72 | -9.22 | -13.43 | -18.81 | -24.01 | -29.67 | -35.56 | -41.32 | -46.71 | -65.64 | -75.91 | -82.71
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Steady Progression | Thermal headroom (MW) | 8.49 | 8.55 | 8.4 | 8.19 | 7.89 | 7.06 | 6.09 | 5.01 | 3.8 | 1.97 | -0.19 | -1.96 | -3.87 | -5.95 | -7.93 | -19.39 | -27.64 | -32.12
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | System Transformation | Thermal headroom (MW) | 8.49 | 8.38 | 8.04 | 7.6 | 6.97 | 6.1 | 5.03 | 3.85 | 2.44 | 0.6 | -1.77 | -4.31 | -6.87 | -9.44 | -12.07 | -24.57 | -31.89 | -35
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | WPD Best View | Thermal headroom (MW) | 8.49 | 8.28 | 7.81 | 7.24 | 6.47 | 5.33 | 4.08 | 2.75 | 1.21 | -0.76 | -3.28 | -5.85 | -8.47 | -11.19 | -13.75 | -30.84 | -40.14 | -44.38
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Consumer Transformation | Thermal headroom (MW) | 61.99 | 61.4227 | 59.9325 | 57.831 | 54.0453 | 47.1572 | 38.9382 | 29.6129 | 20.1863 | 8.8577 | -5.9869 | -19.7296 | -33.5758 | -46.2995 | -58.7373 | -121.6505 | -152.7875 | -166.4891
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Leading the Way | Thermal headroom (MW) | 61.99 | 59.8604 | 56.7033 | 53.182 | 47.5104 | 37.0385 | 24.7752 | 9.7575 | -5.6268 | -22.9938 | -39.8156 | -53.9618 | -67.5307 | -80.2898 | -92.2412 | -135.428 | -148.788 | -153.6668
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Steady Progression | Thermal headroom (MW) | 61.99 | 62.8532 | 62.8585 | 62.6939 | 61.7464 | 58.4132 | 54.6071 | 50.0546 | 45.2384 | 39.6343 | 33.1244 | 27.2491 | 20.6267 | 14.0305 | 7.4665 | -35.6193 | -55.2413 | -60.5158
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | System Transformation | Thermal headroom (MW) | 61.99 | 62.4188 | 61.9752 | 61.178 | 59.1942 | 55.4802 | 50.3608 | 43.9996 | 37.4465 | 29.7248 | 21.5131 | 14.795 | 8.0221 | 0.19115 | -7.5477 | -53.6202 | -70.2894 | -71.4862
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | WPD Best View | Thermal headroom (MW) | 61.99 | 60.3725 | 57.8091 | 54.7835 | 49.7732 | 40.6116 | 29.8904 | 16.803 | 3.6636 | -11.4808 | -26.5988 | -38.9133 | -50.7289 | -62.5273 | -73.8517 | -119.4396 | -136.3563 | -141.2938
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Consumer Transformation | Thermal headroom (MW) | 11.72 | 11.85 | 11.92 | 11.95 | 11.62 | 10.75 | 9.77 | 8.29 | 6.42 | 4.52 | 2.68 | 1.46 | 0.19 | -0.86 | -1.91 | -6.45 | -6.62 | -5.73
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Leading the Way | Thermal headroom (MW) | 11.72 | 11.85 | 11.89 | 11.91 | 11.41 | 10.09 | 8.71 | 6.58 | 3.87 | 1.34 | -0.96 | -2.27 | -3.49 | -4.4 | -5.29 | -7.67 | -6.78 | -5.22
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Steady Progression | Thermal headroom (MW) | 11.72 | 11.94 | 12.05 | 12.17 | 12.02 | 11.46 | 10.92 | 10.07 | 8.95 | 7.74 | 6.47 | 5.52 | 4.43 | 3.53 | 2.67 | -1.83 | -2.58 | -2.03
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | System Transformation | Thermal headroom (MW) | 11.72 | 11.93 | 12.05 | 12.12 | 11.84 | 11.06 | 10.16 | 8.75 | 6.95 | 5.21 | 3.56 | 2.46 | 1.34 | 0.39 | -0.56 | -4.94 | -5.03 | -3.8
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | WPD Best View | Thermal headroom (MW) | 11.72 | 11.85 | 11.89 | 11.91 | 11.41 | 10.1 | 8.72 | 6.59 | 3.88 | 1.35 | -0.95 | -2.26 | -3.48 | -4.4 | -5.28 | -7.67 | -6.78 | -5.22
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Consumer Transformation | Thermal headroom (MW) | 19.1 | 18.79 | 18.36 | 17.48 | 16.19 | 14.07 | 12.12 | 10.23 | 8.01 | 5.12 | 1.57 | -1.88 | -5.44 | -8.96 | -12.48 | -30.48 | -38.98 | -43.81
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Leading the Way | Thermal headroom (MW) | 19.1 | 18.53 | 17.85 | 16.73 | 15.08 | 12.05 | 9.38 | 6.63 | 2.95 | -2.23 | -6.9 | -10.8 | -14.7 | -18.52 | -22.13 | -36.98 | -41.53 | -44.47
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Steady Progression | Thermal headroom (MW) | 19.1 | 19.1 | 19.01 | 18.69 | 18.16 | 17.07 | 16.25 | 15.48 | 14.53 | 13.17 | 11.63 | 10.25 | 8.6 | 6.92 | 5.26 | -6.06 | -10.09 | -10.98
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | System Transformation | Thermal headroom (MW) | 19.1 | 18.98 | 18.79 | 18.29 | 17.5 | 16.24 | 15.17 | 14.07 | 12.53 | 10.44 | 8.34 | 6.63 | 4.88 | 3.09 | 1.37 | -11.36 | -15.31 | -16.17
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | WPD Best View | Thermal headroom (MW) | 19.1 | 18.58 | 17.93 | 16.84 | 15.23 | 12.35 | 9.79 | 7.16 | 3.72 | -1.3 | -5.85 | -9.66 | -13.47 | -17.21 | -20.78 | -36.02 | -41.08 | -43.98
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Consumer Transformation | Thermal headroom (MW) | 3.42 | 3.72 | 3.86 | 3.97 | 3.99 | 4.05 | 3.51 | 2.97 | 2.19 | 0.96 | -0.25 | -1.44 | -2.47 | -3.14 | -3.78 | -7.4 | -8.11 | -7.53
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Leading the Way | Thermal headroom (MW) | 3.42 | 3.7 | 3.78 | 3.85 | 3.79 | 3.78 | 2.89 | 2 | 0.82 | -0.93 | -2.48 | -3.36 | -4.02 | -4.65 | -5.23 | -7.31 | -7.1 | -5.84
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Steady Progression | Thermal headroom (MW) | 3.42 | 3.78 | 3.98 | 4.17 | 4.34 | 4.49 | 4.33 | 4.09 | 3.72 | 3.08 | 2.44 | 1.96 | 1.57 | 1.1 | 0.66 | -2.52 | -3.66 | -3.52
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | System Transformation | Thermal headroom (MW) | 3.42 | 3.77 | 3.96 | 4.13 | 4.21 | 4.33 | 3.9 | 3.5 | 2.9 | 1.86 | 0.84 | 0.25 | -0.22 | -1.09 | -1.96 | -5.61 | -6.35 | -5.36
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | WPD Best View | Thermal headroom (MW) | 3.42 | 3.7 | 3.78 | 3.85 | 3.79 | 3.78 | 2.89 | 2 | 0.82 | -0.93 | -2.48 | -3.36 | -4.02 | -4.65 | -5.23 | -7.31 | -7.1 | -5.84
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Consumer Transformation | Thermal headroom (MW) | 12.992 | 12.652 | 12.082 | 11.332 | 10.282 | 8.122 | 6.152 | 3.652 | 1.532 | -0.698 | -4.448 | -8.268 | -12.018 | -15.348 | -18.598 | -35.028 | -45.598 | -50.508
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Leading the Way | Thermal headroom (MW) | 12.992 | 11.902 | 10.582 | 9.142 | 7.372 | 4.132 | 1.212 | -2.818 | -6.068 | -9.508 | -13.518 | -17.238 | -20.718 | -24.088 | -27.238 | -37.918 | -42.938 | -45.478
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Steady Progression | Thermal headroom (MW) | 12.992 | 13.172 | 13.132 | 13.062 | 12.922 | 12.022 | 11.262 | 10.172 | 9.272 | 8.352 | 7.092 | 5.862 | 4.662 | 3.462 | 2.272 | -6.028 | -11.818 | -14.608
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | System Transformation | Thermal headroom (MW) | 12.992 | 13.012 | 12.802 | 12.512 | 12.102 | 11.112 | 10.142 | 8.612 | 7.532 | 6.332 | 4.832 | 3.362 | 1.992 | 0.222 | -1.638 | -11.488 | -15.498 | -16.568
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | WPD Best View | Thermal headroom (MW) | 12.992 | 11.912 | 10.602 | 9.172 | 7.412 | 4.202 | 1.312 | -2.688 | -5.908 | -9.318 | -13.318 | -17.018 | -20.498 | -23.848 | -26.988 | -37.638 | -42.678 | -45.208
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Consumer Transformation | Thermal headroom (MW) | 15.11 | 15.08 | 14.97 | 14.81 | 14.58 | 14.15 | 13.27 | 12.38 | 11.8 | 11.19 | 10.16 | 9.19 | 8.19 | 7.17 | 6.17 | 0.38 | -3.25 | -5.1
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Leading the Way | Thermal headroom (MW) | 15.11 | 14.85 | 14.51 | 14.15 | 13.68 | 12.87 | 11.52 | 10.04 | 9.12 | 8.13 | 7.03 | 5.92 | 4.82 | 3.77 | 2.75 | -0.95 | -2.75 | -3.82
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Steady Progression | Thermal headroom (MW) | 15.11 | 15.18 | 15.19 | 15.18 | 15.15 | 14.98 | 14.58 | 14.15 | 13.89 | 13.63 | 13.28 | 12.87 | 12.44 | 12.01 | 11.58 | 8.57 | 6.64 | 5.93
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | System Transformation | Thermal headroom (MW) | 15.11 | 15.15 | 15.12 | 15.06 | 14.96 | 14.79 | 14.21 | 13.63 | 13.36 | 12.98 | 12.52 | 12.06 | 11.54 | 11.05 | 10.61 | 7.32 | 5.83 | 5.42
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | WPD Best View | Thermal headroom (MW) | 15.11 | 14.85 | 14.51 | 14.15 | 13.68 | 12.87 | 11.52 | 10.04 | 9.12 | 8.13 | 7.03 | 5.92 | 4.82 | 3.77 | 2.75 | -0.95 | -2.75 | -3.82
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Consumer Transformation | Thermal headroom (MW) | 6.28 | 6.1 | 5.83 | 5.6 | 5.24 | 4.73 | 4.25 | 3.76 | 3.26 | 2.45 | 1.23 | 0.03 | -1.21 | -2.35 | -3.42 | -8.45 | -11.23 | -12.63
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Leading the Way | Thermal headroom (MW) | 6.28 | 6.01 | 5.61 | 5.32 | 4.87 | 4.21 | 3.4 | 2.39 | 1.25 | 0.07 | -1 | -2.16 | -3.29 | -4.39 | -5.36 | -8.9 | -10.14 | -10.66
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Steady Progression | Thermal headroom (MW) | 6.28 | 6.26 | 6.15 | 6.09 | 6 | 5.74 | 5.46 | 5.17 | 4.84 | 4.5 | 4.06 | 3.63 | 3.04 | 2.39 | 1.72 | -2.87 | -5.12 | -5.84
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | System Transformation | Thermal headroom (MW) | 6.28 | 6.21 | 6.05 | 5.95 | 5.77 | 5.59 | 5.4 | 5.16 | 4.89 | 4.59 | 4.19 | 3.78 | 3.37 | 2.64 | 1.92 | -2.53 | -5.1 | -5.66
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | WPD Best View | Thermal headroom (MW) | 6.28 | 6.21 | 6.05 | 5.95 | 5.77 | 5.59 | 5.4 | 5.16 | 4.89 | 4.59 | 4.19 | 3.78 | 3.37 | 2.64 | 1.92 | -2.5 | -5.07 | -5.63
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Consumer Transformation | Thermal headroom (MW) | -4.8597 | -6.9182 | -11.8316 | -16.3399 | -21.3868 | -27.9306 | -33.7661 | -39.549 | -45.7151 | -52.5501 | -64.344 | -77.4822 | -91.311 | -104.5467 | -117.6954 | -189.5543 | -238.6709 | -264.9607
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Leading the Way | Thermal headroom (MW) | -4.8597 | -8.6791 | -16.4336 | -23.5158 | -31.3998 | -42.0714 | -51.3568 | -61.9378 | -73.094 | -85.3062 | -98.1811 | -112.4448 | -126.5082 | -140.4051 | -153.6702 | -202.3426 | -224.1147 | -236.6901
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Steady Progression | Thermal headroom (MW) | -4.8597 | -4.6572 | -7.1643 | -8.9769 | -10.8758 | -13.9069 | -16.5106 | -19.2062 | -21.9387 | -25.3269 | -29.9737 | -34.0612 | -38.3183 | -43.1573 | -47.9447 | -78.3106 | -98.9419 | -107.4659
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | System Transformation | Thermal headroom (MW) | -4.8597 | -5.292 | -8.7605 | -11.6116 | -14.6384 | -17.7672 | -20.5068 | -23.3424 | -26.7075 | -30.3972 | -35.2859 | -40.5741 | -45.9188 | -51.8148 | -57.4572 | -92.838 | -111.5023 | -117.6352
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | WPD Best View | Thermal headroom (MW) | -4.8597 | -5.983 | -10.3936 | -14.4075 | -18.4933 | -23.3394 | -27.0564 | -31.0162 | -35.4563 | -40.3635 | -46.4969 | -53.1579 | -59.7124 | -66.6472 | -73.2487 | -111.8582 | -132.4167 | -140.6858
Grendon 132kV | Irthlingborough | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Consumer Transformation | Thermal headroom (MW) | -2.74 | -3.3 | -6.07 | -8.73 | -11.32 | -13.25 | -14.33 | -15.13 | -15.96 | -16.8 | -17.59 | -18.41 | -19.16 | -19.85 | -20.47 | -25.48 | -28.29 | -29.08
Grendon 132kV | Irthlingborough | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Leading the Way | Thermal headroom (MW) | -2.74 | -3.55 | -6.81 | -10.24 | -13.44 | -16.02 | -17.08 | -18.04 | -19.04 | -20.09 | -20.9 | -21.7 | -22.3 | -23.04 | -23.91 | -26.81 | -27.55 | -27.56
Grendon 132kV | Irthlingborough | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Steady Progression | Thermal headroom (MW) | -2.74 | -3.01 | -5.22 | -7.24 | -9.18 | -10.62 | -11.39 | -12.13 | -12.86 | -13.47 | -14.08 | -14.66 | -15.11 | -15.47 | -15.77 | -17.27 | -17 | -16.29
Grendon 132kV | Irthlingborough | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | System Transformation | Thermal headroom (MW) | -2.74 | -3.16 | -5.77 | -8.21 | -10.51 | -12.18 | -12.96 | -13.56 | -14.23 | -14.91 | -15.38 | -15.75 | -16.1 | -16.47 | -16.82 | -17.7 | -17.39 | -16.45
Grendon 132kV | Irthlingborough | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | WPD Best View | Thermal headroom (MW) | -2.74 | -3.45 | -6.6 | -9.88 | -12.89 | -15.37 | -16.19 | -16.94 | -17.81 | -18.71 | -19.44 | -20.18 | -20.74 | -21.23 | -21.72 | -24.52 | -25.32 | -25.25
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Consumer Transformation | Thermal headroom (MW) | 9 | 8.54 | 7.82 | 7.35 | 6.66 | 5.53 | 4.31 | 3.04 | 1.9 | 0.6 | -1.49 | -4.29 | -7.04 | -9.4 | -11.7 | -24.96 | -32.37 | -35.48
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Leading the Way | Thermal headroom (MW) | 9 | 8.26 | 7.2 | 6.41 | 5.24 | 3.23 | 1.33 | -0.83 | -2.85 | -5.14 | -7.74 | -10.48 | -13.05 | -15.57 | -17.95 | -26.93 | -30.23 | -31.55
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Steady Progression | Thermal headroom (MW) | 9 | 8.86 | 8.5 | 8.43 | 8.24 | 7.67 | 7.13 | 6.52 | 5.99 | 5.37 | 4.53 | 3.64 | 2.72 | 1.76 | 0.81 | -5.22 | -9.31 | -10.88
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | System Transformation | Thermal headroom (MW) | 9 | 8.74 | 8.24 | 8.05 | 7.7 | 7.06 | 6.37 | 5.61 | 4.88 | 4.03 | 2.98 | 1.84 | 0.74 | -0.69 | -2.02 | -9.04 | -12.32 | -13.18
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | WPD Best View | Thermal headroom (MW) | 9 | 8.74 | 8.24 | 8.05 | 7.7 | 7.06 | 6.37 | 5.61 | 4.88 | 4.03 | 2.98 | 1.84 | 0.74 | -0.69 | -2.02 | -9.04 | -12.32 | -13.18
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Consumer Transformation | Thermal headroom (MW) | 5.19 | 5.26 | 5.18 | 5.09 | 4.89 | 4.4 | 3.96 | 3.48 | 2.97 | 2.35 | 1.24 | 0.09 | -1.07 | -2.19 | -3.33 | -10.83 | -15.74 | -18.71
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Leading the Way | Thermal headroom (MW) | 5.19 | 4.99 | 4.61 | 4.25 | 3.79 | 2.8 | 1.89 | 0.89 | -0.14 | -1.23 | -2.47 | -3.82 | -5.17 | -6.47 | -7.72 | -13.06 | -15.91 | -18.06
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Steady Progression | Thermal headroom (MW) | 5.19 | 5.41 | 5.52 | 5.62 | 5.64 | 5.49 | 5.36 | 5.22 | 5.08 | 4.88 | 4.57 | 4.28 | 3.97 | 3.61 | 3.2 | 0.2 | -1.58 | -2.39
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | System Transformation | Thermal headroom (MW) | 5.19 | 5.37 | 5.43 | 5.47 | 5.43 | 5.35 | 5.24 | 5.08 | 4.82 | 4.6 | 4.26 | 3.83 | 3.38 | 2.89 | 2.38 | -1.32 | -3.45 | -4.43
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | WPD Best View | Thermal headroom (MW) | 5.19 | 4.99 | 4.61 | 4.25 | 3.79 | 2.8 | 1.89 | 0.89 | -0.14 | -1.23 | -2.47 | -3.82 | -5.17 | -6.47 | -7.72 | -13.07 | -15.91 | -18.07
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Consumer Transformation | Thermal headroom (MW) | 18.23 | 17.49 | 16.8 | 15.93 | 14.86 | 13.11 | 11.36 | 9.75 | 7.68 | 5.36 | 0.62 | -4.19 | -9.06 | -13.85 | -18.72 | -38.13 | -56.02 | -66.67
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Leading the Way | Thermal headroom (MW) | 18.23 | 17.06 | 15.19 | 13.56 | 11.64 | 9.12 | 6.45 | 3.36 | -0.42 | -4.43 | -8.32 | -12.69 | -17.26 | -21.8 | -26.09 | -39.45 | -45.78 | -49.38
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Steady Progression | Thermal headroom (MW) | 18.23 | 18.43 | 18.38 | 18.29 | 18.18 | 17.65 | 17 | 16.41 | 15.74 | 14.55 | 12.93 | 11.93 | 10.82 | 9.17 | 7.59 | -1.84 | -8.81 | -12.28
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | System Transformation | Thermal headroom (MW) | 18.23 | 18.29 | 18.07 | 17.73 | 17.28 | 16.76 | 16.06 | 15.46 | 14.68 | 13.82 | 12.31 | 10.66 | 8.93 | 7.07 | 5.17 | -5.83 | -10.89 | -12.78
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | WPD Best View | Thermal headroom (MW) | 18.23 | 18.28 | 18.04 | 17.69 | 17.23 | 16.68 | 15.96 | 15.34 | 14.55 | 13.67 | 12.15 | 10.49 | 8.75 | 6.87 | 4.96 | -6.09 | -11.16 | -13.05
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Consumer Transformation | Thermal headroom (MW) | 2.11 | 1.9 | 1.48 | 1.14 | 0.89 | 0.57 | 0.27 | -0.07 | -0.44 | -0.85 | -1.76 | -2.84 | -3.92 | -4.96 | -6.01 | -12.74 | -16.86 | -18.78
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Leading the Way | Thermal headroom (MW) | 2.11 | 1.74 | 1.14 | 0.63 | 0.15 | -0.59 | -1.27 | -2.11 | -2.98 | -4 | -5.11 | -6.32 | -7.54 | -8.7 | -9.81 | -13.97 | -15.75 | -16.58
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Steady Progression | Thermal headroom (MW) | 2.11 | 2.08 | 1.87 | 1.75 | 1.71 | 1.57 | 1.42 | 1.25 | 1.08 | 0.88 | 0.55 | 0.22 | -0.14 | -0.5 | -0.88 | -3.64 | -5.63 | -6.33
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | System Transformation | Thermal headroom (MW) | 2.11 | 2.02 | 1.73 | 1.53 | 1.43 | 1.31 | 1.19 | 1.05 | 0.84 | 0.57 | 0.2 | -0.22 | -0.63 | -1.03 | -1.38 | -4.49 | -6.25 | -6.85
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | WPD Best View | Thermal headroom (MW) | 2.11 | 2.02 | 1.73 | 1.53 | 1.43 | 1.31 | 1.19 | 1.05 | 0.84 | 0.57 | 0.2 | -0.22 | -0.63 | -1.03 | -1.38 | -4.49 | -6.25 | -6.85
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Consumer Transformation | Thermal headroom (MW) | 4.56 | 4.57 | 4.42 | 4.26 | 3.99 | 3.47 | 2.96 | 2.4 | 1.82 | 1.22 | 0.47 | -0.23 | -1.46 | -2.82 | -4.13 | -11.93 | -17.05 | -20.42
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Leading the Way | Thermal headroom (MW) | 4.56 | 4.44 | 4.13 | 3.84 | 3.42 | 2.63 | 1.84 | 0.86 | -0.12 | -1.16 | -2.36 | -3.86 | -5.38 | -6.87 | -8.26 | -14.04 | -17.13 | -19.63
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Steady Progression | Thermal headroom (MW) | 4.56 | 4.74 | 4.78 | 4.85 | 4.87 | 4.72 | 4.56 | 4.36 | 4.1 | 3.82 | 3.42 | 3.01 | 2.57 | 2.1 | 1.63 | -1.08 | -3.35 | -4.46
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | System Transformation | Thermal headroom (MW) | 4.56 | 4.69 | 4.67 | 4.67 | 4.6 | 4.49 | 4.34 | 4.1 | 3.75 | 3.42 | 2.96 | 2.47 | 1.96 | 1.47 | 1.03 | -2.6 | -5.53 | -6.79
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | WPD Best View | Thermal headroom (MW) | 4.56 | 4.69 | 4.67 | 4.67 | 4.6 | 4.49 | 4.35 | 4.1 | 3.75 | 3.42 | 2.97 | 2.49 | 1.99 | 1.52 | 1.1 | -2.34 | -5.38 | -6.69
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Consumer Transformation | Thermal headroom (MW) | 44.44 | 40.7488 | 33.2858 | 26.3667 | 18.5464 | 11.0026 | 4.3248 | -1.5093 | -7.5752 | -14.3375 | -23.0758 | -31.6094 | -40.2306 | -48.5857 | -56.6644 | -97.7507 | -121.9641 | -133.4964
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Leading the Way | Thermal headroom (MW) | 44.44 | 39.2034 | 29.0824 | 19.6858 | 9.3989 | -1.3737 | -10.2758 | -18.973 | -27.8992 | -37.9656 | -46.9388 | -55.8173 | -64.4261 | -72.7714 | -80.5996 | -106.6282 | -116.0349 | -120.3523
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Steady Progression | Thermal headroom (MW) | 44.44 | 42.2685 | 36.888 | 32.0529 | 26.7227 | 21.8865 | 17.9275 | 14.2663 | 10.6922 | 6.8721 | 2.6227 | -1.0462 | -4.6844 | -8.2634 | -11.8534 | -34.7472 | -46.1485 | -49.1587
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | System Transformation | Thermal headroom (MW) | 44.44 | 41.5045 | 34.8487 | 28.8763 | 22.3056 | 17.1918 | 12.9203 | 9.1882 | 5.1234 | 0.81491 | -3.4759 | -7.3124 | -11.4346 | -15.4628 | -19.4573 | -43.5622 | -52.8555 | -53.9789
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | WPD Best View | Thermal headroom (MW) | 44.44 | 39.6493 | 30.0788 | 21.2166 | 11.6579 | 1.9555 | -5.8377 | -13.2873 | -21.0049 | -29.4345 | -37.374 | -45.2224 | -53.1686 | -60.7907 | -68.1045 | -96.0576 | -108.1601 | -113.1023
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Consumer Transformation | Thermal headroom (MW) | 5.2 | 5.03 | 4.63 | 4.06 | 2.84 | 1.37 | -0.27 | -1.77 | -3.12 | -4.48 | -6.3 | -8.18 | -10.05 | -11.89 | -13.59 | -22.34 | -26.63 | -28.52
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Leading the Way | Thermal headroom (MW) | 5.2 | 4.74 | 4 | 3.08 | 1.4 | -0.69 | -2.84 | -5.03 | -6.94 | -8.87 | -10.69 | -12.66 | -14.55 | -16.25 | -17.72 | -23.22 | -24.98 | -25.43
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Steady Progression | Thermal headroom (MW) | 5.2 | 5.28 | 5.17 | 5.03 | 4.55 | 3.97 | 3.33 | 2.7 | 2.14 | 1.62 | 0.9 | 0.18 | -0.61 | -1.45 | -2.32 | -8.24 | -11.44 | -12.62
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | System Transformation | Thermal headroom (MW) | 5.2 | 5.18 | 5.01 | 4.72 | 3.98 | 3.33 | 2.6 | 1.93 | 1.3 | 0.65 | -0.12 | -0.97 | -1.92 | -2.94 | -4 | -10.26 | -13.19 | -13.56
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | WPD Best View | Thermal headroom (MW) | 5.2 | 5.17 | 4.95 | 4.53 | 3.59 | 2.65 | 1.54 | 0.55 | -0.35 | -1.17 | -2.02 | -2.95 | -3.97 | -4.99 | -6 | -11.96 | -14.85 | -15.19
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Consumer Transformation | Thermal headroom (MW) | 10.04 | 9.8 | 9.46 | 8.92 | 8.3 | 7.35 | 6.54 | 5.73 | 4.84 | 3.84 | 2.14 | 0.45 | -1.3 | -2.97 | -4.57 | -14.33 | -20.42 | -23.56
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Leading the Way | Thermal headroom (MW) | 10.04 | 9.38 | 8.58 | 7.58 | 6.44 | 4.78 | 3.34 | 1.8 | 0.2 | -1.62 | -3.34 | -5.25 | -7.23 | -9.16 | -10.93 | -17.48 | -20.81 | -23.05
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Steady Progression | Thermal headroom (MW) | 10.04 | 10 | 9.89 | 9.6 | 9.28 | 8.75 | 8.31 | 7.89 | 7.49 | 6.96 | 6.18 | 5.55 | 4.85 | 4.09 | 3.36 | -1.73 | -4.7 | -5.94
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | System Transformation | Thermal headroom (MW) | 10.04 | 9.9 | 9.68 | 9.25 | 8.76 | 8.32 | 7.93 | 7.5 | 7.04 | 6.55 | 5.62 | 4.81 | 3.86 | 3.05 | 2.26 | -3.12 | -6.47 | -7.82
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | WPD Best View | Thermal headroom (MW) | 10.04 | 9.37 | 8.58 | 7.58 | 6.45 | 4.83 | 3.44 | 1.95 | 0.52 | -1.08 | -2.93 | -4.76 | -6.71 | -8.51 | -10.25 | -16.9 | -20.41 | -22.58
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Consumer Transformation | Thermal headroom (MW) | 4.202 | 3.962 | 3.372 | 2.702 | 1.892 | 0.962 | 0.012 | -0.948 | -1.948 | -2.918 | -4.028 | -5.718 | -7.468 | -9.128 | -10.688 | -17.908 | -22.118 | -24.058
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Leading the Way | Thermal headroom (MW) | 4.202 | 3.762 | 2.952 | 2.042 | 1.032 | -0.198 | -1.528 | -2.958 | -4.398 | -6.328 | -8.118 | -9.928 | -11.678 | -13.338 | -14.848 | -19.638 | -21.238 | -21.818
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Steady Progression | Thermal headroom (MW) | 4.202 | 4.232 | 3.962 | 3.702 | 3.422 | 3.042 | 2.672 | 2.222 | 1.732 | 1.222 | 0.652 | 0.072 | -0.518 | -1.148 | -1.778 | -5.848 | -8.728 | -9.408
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | System Transformation | Thermal headroom (MW) | 4.202 | 4.142 | 3.752 | 3.352 | 2.922 | 2.532 | 2.102 | 1.572 | 0.972 | 0.342 | -0.308 | -0.978 | -1.648 | -2.288 | -2.848 | -7.548 | -9.618 | -9.848
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | WPD Best View | Thermal headroom (MW) | 4.202 | 3.972 | 3.392 | 2.722 | 1.952 | 1.082 | 0.202 | -0.698 | -1.638 | -2.548 | -3.558 | -4.988 | -6.668 | -8.248 | -9.738 | -17.038 | -21.448 | -23.298
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Consumer Transformation | Thermal headroom (MW) | 10.038 | 9.328 | 8.698 | 7.958 | 6.858 | 4.998 | 2.618 | 0.188 | -2.292 | -5.602 | -12.582 | -19.522 | -26.522 | -33.342 | -40.172 | -67.812 | -92.122 | -106.342
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Leading the Way | Thermal headroom (MW) | 10.038 | 8.968 | 7.238 | 5.788 | 3.508 | 0.208 | -3.262 | -7.772 | -13.052 | -18.832 | -24.812 | -31.222 | -37.892 | -44.402 | -50.522 | -69.282 | -77.992 | -82.402
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Steady Progression | Thermal headroom (MW) | 10.038 | 10.378 | 10.408 | 10.438 | 10.308 | 9.648 | 8.968 | 8.218 | 7.338 | 5.678 | 3.478 | 1.938 | -0.082 | -2.332 | -4.402 | -18.572 | -29.642 | -34.562
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | System Transformation | Thermal headroom (MW) | 10.038 | 10.138 | 9.908 | 9.628 | 9.118 | 8.518 | 7.888 | 7.058 | 5.918 | 4.568 | 2.388 | 0.088 | -2.252 | -4.512 | -6.922 | -22.882 | -29.972 | -32.422
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | WPD Best View | Thermal headroom (MW) | 10.038 | 8.968 | 7.238 | 5.788 | 3.508 | 0.208 | -3.262 | -7.772 | -13.052 | -18.832 | -24.812 | -31.222 | -37.892 | -44.402 | -50.522 | -69.282 | -77.992 | -82.402
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Consumer Transformation | Thermal headroom (MW) | 17.4 | 16.13 | 13.82 | 11.92 | 9.92 | 8.36 | 7.07 | 6.1 | 5.04 | 3.84 | 2.83 | 2.09 | 1.36 | 0.63 | -0.08 | -3.28 | -4.16 | -4.12
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Leading the Way | Thermal headroom (MW) | 17.4 | 15.93 | 13.09 | 10.74 | 8.39 | 6.38 | 4.88 | 3.71 | 2.48 | 1.07 | 0.06 | -0.69 | -1.34 | -1.98 | -2.6 | -4.15 | -3.96 | -3.5
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Steady Progression | Thermal headroom (MW) | 17.4 | 16.36 | 14.47 | 12.87 | 11.2 | 9.92 | 8.89 | 8 | 7.15 | 6.33 | 5.61 | 4.98 | 4.47 | 4.06 | 3.62 | 1.29 | 1.03 | 1.46
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | System Transformation | Thermal headroom (MW) | 17.4 | 16.18 | 13.93 | 12.11 | 10.2 | 8.79 | 7.64 | 6.75 | 5.8 | 4.8 | 4.14 | 3.67 | 3.17 | 2.68 | 2.21 | 0.04 | 0.15 | 0.8
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | WPD Best View | Thermal headroom (MW) | 17.4 | 15.93 | 13.09 | 10.74 | 8.39 | 6.38 | 4.88 | 3.71 | 2.48 | 1.07 | 0.06 | -0.69 | -1.34 | -1.98 | -2.6 | -4.15 | -3.96 | -3.5
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Consumer Transformation | Thermal headroom (MW) | 82.2336 | 81.7986 | 80.795 | 79.5817 | 78.1627 | 76.2719 | 74.4563 | 72.5914 | 70.652 | 68.4645 | 64.03 | 58.5847 | 52.9959 | 47.8115 | 42.6801 | 21.561 | 2.4598 | -10.3804
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Leading the Way | Thermal headroom (MW) | 82.2336 | 81.4136 | 79.9739 | 78.3481 | 76.2225 | 73.1831 | 69.9525 | 66.0752 | 59.4729 | 51.6299 | 46.8557 | 40.9594 | 34.2396 | 27.4485 | 21.1863 | -0.7555 | -18.9181 | -35.8299
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Steady Progression | Thermal headroom (MW) | 82.2336 | 82.347 | 82.0123 | 81.6939 | 81.3525 | 80.5689 | 79.7391 | 78.8224 | 77.7993 | 75.3024 | 72.2258 | 70.8305 | 69.286 | 67.2645 | 65.6125 | 53.9859 | 46.7052 | 44.6199
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | System Transformation | Thermal headroom (MW) | 82.2336 | 82.0247 | 81.4012 | 80.7154 | 79.8762 | 79.0459 | 78.055 | 76.8132 | 75.273 | 73.7438 | 70.635 | 69.066 | 66.3149 | 64.3351 | 61.6633 | 45.5985 | 32.4673 | 26.4341
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | WPD Best View | Thermal headroom (MW) | 82.2336 | 81.8021 | 80.8055 | 79.6038 | 78.1992 | 76.3464 | 74.5579 | 72.7152 | 70.7976 | 68.6395 | 64.262 | 59.0375 | 53.5479 | 48.4342 | 43.3704 | 22.2493 | 3.0469 | -9.6327
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Consumer Transformation | Thermal headroom (MW) | -0.052 | -0.072 | -0.132 | -0.212 | -0.342 | -0.572 | -0.802 | -1.012 | -1.242 | -1.472 | -1.972 | -2.592 | -3.192 | -3.802 | -4.352 | -6.752 | -7.932 | -8.512
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Leading the Way | Thermal headroom (MW) | -0.052 | -0.122 | -0.202 | -0.312 | -0.472 | -0.772 | -1.112 | -1.532 | -2.002 | -2.602 | -3.142 | -3.682 | -4.212 | -4.702 | -5.102 | -6.852 | -7.362 | -7.552
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Steady Progression | Thermal headroom (MW) | -0.052 | -0.002 | 0.018 | 0.028 | 0.028 | -0.082 | -0.212 | -0.342 | -0.482 | -0.642 | -0.852 | -1.072 | -1.312 | -1.572 | -1.902 | -4.602 | -5.852 | -6.102
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | System Transformation | Thermal headroom (MW) | -0.052 | -0.032 | -0.032 | -0.052 | -0.102 | -0.142 | -0.202 | -0.272 | -0.372 | -0.492 | -0.682 | -0.872 | -1.082 | -1.292 | -1.512 | -4.082 | -5.692 | -5.972
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | WPD Best View | Thermal headroom (MW) | -0.052 | -0.072 | -0.132 | -0.212 | -0.342 | -0.572 | -0.802 | -1.012 | -1.242 | -1.472 | -1.972 | -2.592 | -3.192 | -3.802 | -4.352 | -6.742 | -7.932 | -8.512
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Consumer Transformation | Thermal headroom (MW) | 11.61 | 11.3 | 10.68 | 9.95 | 9.22 | 8.22 | 7.31 | 6.39 | 5.42 | 4.37 | 1.46 | -1.89 | -5.51 | -9.01 | -12.66 | -25.39 | -42.72 | -56.28
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Leading the Way | Thermal headroom (MW) | 11.61 | 11.08 | 10.22 | 9.24 | 7.84 | 5.82 | 3.75 | 1.13 | -4.84 | -11.58 | -14.15 | -18.34 | -23.88 | -29.77 | -35.35 | -54.51 | -75.91 | -98.06
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Steady Progression | Thermal headroom (MW) | 11.61 | 11.54 | 11.29 | 11.03 | 10.83 | 10.43 | 10.03 | 9.59 | 9.1 | 6.74 | 3.85 | 3.25 | 2.54 | 1.24 | 0.58 | -2.93 | -5.58 | -6.5
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | System Transformation | Thermal headroom (MW) | 11.61 | 11.26 | 10.81 | 10.26 | 9.67 | 9.04 | 8.3 | 7.37 | 6.18 | 5.33 | 2.52 | 1.78 | -0.63 | -1.67 | -3.79 | -12.51 | -23.74 | -31.03
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | WPD Best View | Thermal headroom (MW) | 11.61 | 11.31 | 10.7 | 10 | 9.27 | 8.28 | 7.37 | 6.45 | 5.49 | 4.43 | 1.53 | -1.74 | -5.33 | -8.81 | -12.44 | -24.96 | -42.16 | -55.68
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Consumer Transformation | Thermal headroom (MW) | 6.37 | 6.26 | 5.87 | 5.41 | 4.8 | 4.06 | 3.31 | 2.5 | 1.65 | 0.5 | -1.52 | -3.97 | -6.35 | -8.23 | -10.05 | -19.44 | -24.86 | -27.32
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Leading the Way | Thermal headroom (MW) | 6.37 | 6.11 | 5.53 | 4.92 | 4.13 | 3.07 | 1.88 | 0.56 | -1.21 | -3.47 | -5.86 | -8.16 | -10.26 | -12.24 | -13.99 | -20.27 | -22.64 | -23.49
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Steady Progression | Thermal headroom (MW) | 6.37 | 6.5 | 6.42 | 6.35 | 6.25 | 5.94 | 5.6 | 5.22 | 4.78 | 4.16 | 3.38 | 2.67 | 1.92 | 1.15 | 0.37 | -5.85 | -9.95 | -11.28
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | System Transformation | Thermal headroom (MW) | 6.37 | 6.43 | 6.25 | 6.08 | 5.83 | 5.58 | 5.25 | 4.85 | 4.36 | 3.57 | 2.64 | 1.83 | 1.06 | -0.06 | -1.09 | -8.3 | -11.67 | -12.21
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | WPD Best View | Thermal headroom (MW) | 6.37 | 6.24 | 5.85 | 5.38 | 4.75 | 4.01 | 3.25 | 2.43 | 1.58 | 0.44 | -1.58 | -3.95 | -6.24 | -8.09 | -9.88 | -19.49 | -25.06 | -27.37
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Consumer Transformation | Thermal headroom (MW) | 6.7252 | 6.7374 | 6.9073 | 5.9288 | 4.9446 | 2.9693 | 0.90345 | -1.1967 | -3.4182 | -5.9475 | -10.7177 | -15.5013 | -20.3366 | -25.1424 | -30.5665 | -51.3782 | -71.5898 | -85.4001
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Leading the Way | Thermal headroom (MW) | 6.7252 |  |  | 4.3437 |  |  | -4.4931 | -8.6935 |  | -23.1238 | -27.0608 |  | -39.6474 | -46.5019 |  | -74.7196 |  | -109.7626
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Steady Progression | Thermal headroom (MW) | 6.7252 | 7.2413 |  | 7.7668 | 7.7368 |  |  | 5.9389 |  |  | -0.33299 | -1.5976 |  | -4.9419 | -6.4234 | -13.506 |  | -16.8913
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | System Transformation | Thermal headroom (MW) | 6.7252 | 6.9446 | 7.5087 | 6.9328 | 6.4632 | 5.6893 | 4.6562 | 3.383 | 1.7754 | 0.24254 | -2.7804 | -4.376 | -7.4354 | -9.5318 | -12.408 | -22.6758 | -31.9805 | -37.3047
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | WPD Best View | Thermal headroom (MW) | 6.7252 | 6.7458 | 6.9262 | 5.9578 | 4.9854 | 3.0241 | 0.97201 | -1.1107 | -3.3156 | -5.8362 | -10.5988 |  | -20.1695 | -24.8987 | -30.316 | -50.8882 | -70.9138 | -84.6514
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Consumer Transformation | Thermal headroom (MW) | 5.56 | 5.42 | 5.06 | 4.76 | 4.37 | 3.68 | 3.01 | 2.36 | 1.66 | 0.84 | -0.41 | -1.64 | -2.89 | -4.05 | -5.19 | -11.3 | -14.53 | -15.98
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Leading the Way | Thermal headroom (MW) | 5.56 | 5.15 | 4.5 | 3.92 | 3.27 | 2.22 | 1.16 | 0 | -1.19 | -2.56 | -3.83 | -5.24 | -6.64 | -7.9 | -9.06 | -12.87 | -13.98 | -14.31
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Steady Progression | Thermal headroom (MW) | 5.56 | 5.65 | 5.55 | 5.52 | 5.47 | 5.28 | 5.1 | 4.87 | 4.64 | 4.39 | 3.95 | 3.49 | 3.01 | 2.51 | 2.01 | -0.97 | -2.47 | -2.72
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | System Transformation | Thermal headroom (MW) | 5.56 | 5.6 | 5.43 | 5.32 | 5.19 | 5 | 4.76 | 4.51 | 4.15 | 3.74 | 3.24 | 2.69 | 2.08 | 1.42 | 0.76 | -2.54 | -3.51 | -3.58
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | WPD Best View | Thermal headroom (MW) | 5.56 | 5.42 | 5.06 | 4.76 | 4.37 | 3.68 | 3.01 | 2.36 | 1.66 | 0.84 | -0.41 | -1.64 | -2.89 | -4.05 | -5.19 | -11.3 | -14.53 | -15.98
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Consumer Transformation | Thermal headroom (MW) | 3.5 | 3.21 | 3.97 | 2.9 | 2.03 | 0.08 | -2.04 | -4.19 | -6.48 | -9.08 | -14.84 | -20.69 | -26.67 | -32.77 | -39.72 | -62.71 | -89.95 | -110.2
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Leading the Way | Thermal headroom (MW) | 3.5 | 2.84 | 3.37 | 1.81 | 0 | -3.56 | -7.41 | -12 | -20.78 | -30.42 | -34.86 | -41.94 | -50.61 | -59.65 | -68.57 | -96.42 | -123.83 | -151.29
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Steady Progression | Thermal headroom (MW) | 3.5 | 3.57 | 4.66 | 4.24 | 4.12 | 3.41 | 2.64 | 1.87 | 0.96 | -2.52 | -6.81 | -8.15 | -9.66 | -11.97 | -13.58 | -20.84 | -24.36 | -26.56
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | System Transformation | Thermal headroom (MW) | 3.5 | 3.22 | 4.22 | 3.37 | 2.74 | 1.72 | 0.4 | -1.2 | -3.17 | -4.94 | -9.01 | -10.72 | -14.68 | -17.08 | -20.79 | -33.25 | -47.53 | -56.97
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | WPD Best View | Thermal headroom (MW) | 3.5 | 3.22 | 4 | 2.94 | 2.1 | 0.17 | -1.93 | -4.06 | -6.32 | -8.9 | -14.65 | -20.45 | -26.4 | -32.38 | -39.33 | -61.94 | -88.89 | -109.02
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Consumer Transformation | Thermal headroom (MW) | -0.17 | -0.11 | -0.2 | -0.3 | -0.45 | -0.65 | -0.83 | -1.03 | -1.23 | -1.46 | -1.61 | -1.73 | -1.81 | -1.88 | -2.03 | -3.5 | -4.23 | -4.51
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Leading the Way | Thermal headroom (MW) | -0.17 | -0.16 | -0.31 | -0.46 | -0.66 | -0.92 | -1.19 | -1.49 | -1.79 | -2.11 | -2.24 | -2.44 | -2.62 | -2.77 | -3.02 | -4.06 | -4.26 | -4.26
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Steady Progression | Thermal headroom (MW) | -0.17 | -0.04 | -0.04 | -0.02 | -0.02 | -0.03 | -0.04 | -0.08 | -0.12 | -0.18 | -0.27 | -0.36 | -0.45 | -0.55 | -0.65 | -1.09 | -0.84 | -0.68
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | System Transformation | Thermal headroom (MW) | -0.17 | -0.06 | -0.08 | -0.1 | -0.13 | -0.16 | -0.2 | -0.28 | -0.38 | -0.5 | -0.58 | -0.69 | -0.79 | -0.88 | -0.94 | -1.13 | -1.17 | -1.05
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | WPD Best View | Thermal headroom (MW) | -0.17 | -0.11 | -0.2 | -0.3 | -0.45 | -0.65 | -0.83 | -1.03 | -1.23 | -1.46 | -1.61 | -1.73 | -1.81 | -1.88 | -2.03 | -3.5 | -4.23 | -4.51
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Consumer Transformation | Thermal headroom (MW) | 35.3088 | 34.5735 | 31.4719 | 29.7418 | 27.3713 | 24.205 | 21.1052 | 18.0268 | 14.6607 | 10.7762 | 5.1922 | -0.85091 | -7.9405 | -14.6771 | -21.1324 | -53.6448 | -71.248 | -79.5694
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Leading the Way | Thermal headroom (MW) | 35.3088 | 33.546 | 29.0828 | 26.3667 | 22.929 | 18.5598 | 14.2603 | 9.5328 | 4.4986 | -1.3406 | -8.3451 | -16.0658 | -23.7794 | -30.8317 | -37.1246 | -56.8051 | -62.8835 | -63.6179
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Steady Progression | Thermal headroom (MW) | 35.3088 | 35.7932 | 34.127 | 33.9419 | 33.629 | 32.6154 | 31.5884 | 30.4203 | 28.9506 | 27.3915 | 25.2119 | 22.9551 | 20.4955 | 17.8742 | 15.1709 | -2.3695 | -13.4022 | -17.7033
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | System Transformation | Thermal headroom (MW) | 35.3088 | 35.4442 | 33.1495 | 32.4605 | 31.4965 | 30.442 | 29.4007 | 28.1457 | 26.3875 | 24.3494 | 21.7986 | 18.9641 | 15.8691 | 12.8328 | 9.9525 | -6.9832 | -14.7271 | -14.9588
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | WPD Best View | Thermal headroom (MW) | 35.3088 | 33.546 | 29.0828 | 26.3667 | 22.929 | 18.5598 | 14.2603 | 9.5328 | 4.4986 | -1.3406 | -8.3451 | -16.0658 | -23.7794 | -30.8317 | -37.1246 | -56.8051 | -62.8835 | -63.6179
Grendon 132kV | Northampton | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Consumer Transformation | Thermal headroom (MW) | -1.26 | -1.13 | -1.21 | -1.4 | -1.76 | -2.52 | -3.39 | -4.3 | -5.23 | -6.23 | -7.67 | -8.92 | -11.08 | -13.19 | -15.21 | -24.14 | -28.33 | -30.61
Grendon 132kV | Northampton | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Leading the Way | Thermal headroom (MW) | -1.26 | -1.41 | -1.84 | -2.32 | -3.02 | -3.87 | -4.86 | -5.97 | -7.05 | -8.11 | -10.14 | -12.41 | -14.66 | -16.82 | -18.82 | -23.93 | -25.1 | -24.75
Grendon 132kV | Northampton | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Steady Progression | Thermal headroom (MW) | -1.26 | -0.8 | -0.59 | -0.41 | -0.28 | -0.42 | -0.59 | -0.82 | -1.16 | -1.63 | -2.2 | -2.82 | -3.48 | -4.19 | -4.91 | -9.33 | -12.36 | -14.26
Grendon 132kV | Northampton | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | System Transformation | Thermal headroom (MW) | -1.26 | -0.91 | -0.81 | -0.77 | -0.84 | -0.95 | -1.1 | -1.39 | -1.85 | -2.42 | -3.08 | -3.83 | -4.61 | -5.35 | -6 | -9.11 | -10.91 | -10.81
Grendon 132kV | Northampton | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | WPD Best View | Thermal headroom (MW) | -1.26 | -1.41 | -1.84 | -2.32 | -3.02 | -3.87 | -4.86 | -5.97 | -7.05 | -8.11 | -10.14 | -12.41 | -14.66 | -16.82 | -18.82 | -23.93 | -25.1 | -24.75
Grendon 132kV | Northampton | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Consumer Transformation | Thermal headroom (MW) | 10.74 | 10.45 | 9.99 | 9.44 | 8.96 | 8.28 | 7.65 | 6.99 | 6.28 | 5.52 | 4.64 | 3.74 | 2.43 | 1.31 | 0.22 | -6.36 | -10.31 | -12.2
Grendon 132kV | Northampton | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Leading the Way | Thermal headroom (MW) | 10.74 | 10.27 | 9.61 | 8.85 | 8.21 | 7.1 | 6.23 | 5.23 | 4.24 | 3.12 | 1.74 | 0.3 | -1.13 | -2.32 | -3.45 | -7.95 | -9.87 | -10.88
Grendon 132kV | Northampton | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Steady Progression | Thermal headroom (MW) | 10.74 | 10.65 | 10.4 | 10.13 | 9.96 | 9.64 | 9.38 | 9.1 | 8.77 | 8.4 | 7.93 | 7.44 | 6.91 | 6.39 | 5.88 | 3.23 | 1.86 | 0.77
Grendon 132kV | Northampton | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | System Transformation | Thermal headroom (MW) | 10.74 | 10.57 | 10.23 | 9.86 | 9.6 | 9.27 | 9.02 | 8.7 | 8.28 | 7.79 | 7.24 | 6.66 | 6.05 | 5.56 | 5.14 | 2.6 | 0.94 | 0.46
Grendon 132kV | Northampton | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | WPD Best View | Thermal headroom (MW) | 10.74 | 10.27 | 9.61 | 8.85 | 8.21 | 7.1 | 6.23 | 5.23 | 4.24 | 3.12 | 1.74 | 0.3 | -1.13 | -2.32 | -3.45 | -7.95 | -9.87 | -10.88
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Consumer Transformation | Thermal headroom (MW) | 6.56 | 6.23 | 5.8 | 5.78 | 5.69 | 5.63 | 5.56 | 5.48 | 5.4 | 5.2 | 4.87 | 4.52 | 4.16 | 3.84 | 3.55 | 2.28 | 2.02 | 2.25
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Leading the Way | Thermal headroom (MW) | 6.56 | 6.16 | 5.61 | 5.58 | 5.46 | 5.38 | 5.26 | 5.13 | 4.91 | 4.67 | 4.31 | 3.93 | 3.53 | 3.15 | 2.88 | 2.3 | 2.66 | 3.51
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Steady Progression | Thermal headroom (MW) | 6.56 | 6.37 | 6.06 | 6.15 | 6.16 | 6.17 | 6.18 | 6.22 | 6.24 | 6.28 | 6.28 | 6.29 | 6.25 | 6.18 | 6.08 | 4.88 | 4.09 | 4.4
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | System Transformation | Thermal headroom (MW) | 6.56 | 6.3 | 5.92 | 5.94 | 5.94 | 5.95 | 5.99 | 6.05 | 6.07 | 6.08 | 6.02 | 5.88 | 5.71 | 5.5 | 5.28 | 3.87 | 3.6 | 4.3
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | WPD Best View | Thermal headroom (MW) | 6.56 | 6.16 | 5.61 | 5.58 | 5.46 | 5.38 | 5.26 | 5.13 | 4.91 | 4.67 | 4.31 | 3.93 | 3.53 | 3.15 | 2.88 | 2.3 | 2.66 | 3.51
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Consumer Transformation | Thermal headroom (MW) | 17.87 | 17.56 | 16.43 | 15.75 | 14.87 | 13.59 | 12.34 | 11.08 | 9.65 | 7.97 | 5.27 | 2.53 | -0.2 | -2.79 | -5.21 | -14.92 | -19.33 | -21.66
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Leading the Way | Thermal headroom (MW) | 17.87 | 17.1 | 15.42 | 14.3 | 12.91 | 11.42 | 9.9 | 8.13 | 6.17 | 4 | 1.38 | -1.43 | -4.15 | -6.68 | -8.89 | -13.44 | -13.67 | -11.73
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Steady Progression | Thermal headroom (MW) | 17.87 | 18.03 | 17.44 | 17.32 | 17.22 | 16.83 | 16.45 | 16.02 | 15.45 | 14.92 | 14.16 | 13.32 | 12.43 | 11.48 | 10.42 | 2.98 | -2.44 | -3.8
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | System Transformation | Thermal headroom (MW) | 17.87 | 17.91 | 17.05 | 16.71 | 16.28 | 15.87 | 15.45 | 14.98 | 14.37 | 13.69 | 12.73 | 11.67 | 10.39 | 8.99 | 7.53 | 0.71 | -1.05 | -0.34
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | WPD Best View | Thermal headroom (MW) | 17.87 | 17.1 | 15.42 | 14.3 | 12.91 | 11.42 | 9.9 | 8.13 | 6.17 | 4 | 1.38 | -1.43 | -4.15 | -6.68 | -8.89 | -13.44 | -13.67 | -11.73
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Consumer Transformation | Thermal headroom (MW) | 20.59 | 20.29 | 17.53 | 16.89 | 15.94 | 14.79 | 13.71 | 12.84 | 11.91 | 10.85 | 8.96 | 7.02 | 5.06 | 3.14 | 1.31 | -7.05 | -12.03 | -14.35
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Leading the Way | Thermal headroom (MW) | 20.59 | 19.86 | 16.36 | 15.32 | 13.97 | 12.63 | 11.29 | 9.88 | 8.47 | 6.84 | 4.9 | 2.82 | 0.76 | -1.24 | -2.98 | -8.19 | -9.7 | -9.76
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Steady Progression | Thermal headroom (MW) | 20.59 | 20.71 | 18.65 | 18.5 | 18.28 | 17.94 | 17.54 | 17.11 | 16.7 | 16.36 | 15.77 | 15.24 | 14.66 | 13.99 | 13.29 | 8.18 | 4.43 | 3.03
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | System Transformation | Thermal headroom (MW) | 20.59 | 20.62 | 18.17 | 17.91 | 17.48 | 17.06 | 16.66 | 16.35 | 15.92 | 15.49 | 14.85 | 14.15 | 13.31 | 12.4 | 11.45 | 6.06 | 4.08 | 3.87
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | WPD Best View | Thermal headroom (MW) | 20.59 | 19.86 | 16.36 | 15.32 | 13.97 | 12.63 | 11.29 | 9.88 | 8.47 | 6.84 | 4.9 | 2.82 | 0.76 | -1.24 | -2.98 | -8.19 | -9.7 | -9.76
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Consumer Transformation | Thermal headroom (MW) | 17.05 | 17.13 | 17.15 | 17.15 | 17.15 | 17.14 | 17.12 | 17.09 | 17.06 | 17.02 | 16.97 | 16.92 | 16.87 | 16.81 | 16.75 | 16.76 | 17.05 | 17.33
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Leading the Way | Thermal headroom (MW) | 17.05 | 17.12 | 17.14 | 17.14 | 17.13 | 17.11 | 17.09 | 17.06 | 17.02 | 16.98 | 16.94 | 16.89 | 16.85 | 16.81 | 16.78 | 16.97 | 17.28 | 17.56
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Steady Progression | Thermal headroom (MW) | 17.05 | 17.14 | 17.18 | 17.22 | 17.26 | 17.29 | 17.32 | 17.35 | 17.37 | 17.39 | 17.41 | 17.42 | 17.43 | 17.43 | 17.43 | 17.54 | 17.82 | 18.1
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | System Transformation | Thermal headroom (MW) | 17.05 | 17.14 | 17.17 | 17.21 | 17.24 | 17.27 | 17.29 | 17.3 | 17.31 | 17.31 | 17.31 | 17.31 | 17.3 | 17.29 | 17.29 | 17.41 | 17.69 | 17.96
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | WPD Best View | Thermal headroom (MW) | 17.05 | 17.12 | 17.14 | 17.14 | 17.13 | 17.11 | 17.09 | 17.06 | 17.02 | 16.98 | 16.94 | 16.89 | 16.85 | 16.81 | 16.78 | 16.97 | 17.28 | 17.56
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Consumer Transformation | Thermal headroom (MW) | 6.13 | 6.11 | 6.04 | 5.92 | 5.72 | 5.47 | 5.21 | 4.92 | 4.61 | 4.19 | 3.56 | 2.65 | 1.68 | 0.85 | 0.03 | -4.57 | -7.14 | -8.42
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Leading the Way | Thermal headroom (MW) | 6.13 | 6.04 | 5.89 | 5.71 | 5.42 | 4.98 | 4.48 | 3.94 | 3.35 | 2.45 | 1.52 | 0.5 | -0.57 | -1.5 | -2.3 | -5.24 | -6.45 | -7.01
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Steady Progression | Thermal headroom (MW) | 6.13 | 6.2 | 6.23 | 6.25 | 6.23 | 6.12 | 5.99 | 5.85 | 5.68 | 5.46 | 5.15 | 4.84 | 4.5 | 4.15 | 3.8 | 1.26 | -0.54 | -1.08
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | System Transformation | Thermal headroom (MW) | 6.13 | 6.18 | 6.18 | 6.16 | 6.08 | 5.98 | 5.86 | 5.69 | 5.48 | 5.2 | 4.85 | 4.46 | 4.07 | 3.71 | 3.4 | 0.5 | -1.13 | -1.46
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | WPD Best View | Thermal headroom (MW) | 6.13 | 6.04 | 5.89 | 5.71 | 5.42 | 4.98 | 4.48 | 3.94 | 3.35 | 2.45 | 1.52 | 0.5 | -0.57 | -1.5 | -2.3 | -5.24 | -6.45 | -7.01
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Consumer Transformation | Thermal headroom (MW) | 3.67 | 3.46 | 3.03 | 2.45 | 1.57 | 0.51 | -0.45 | -1.35 | -2.39 | -3.42 | -4.53 | -5.64 | -7.21 | -9.04 | -10.8 | -22 | -29.46 | -33.18
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Leading the Way | Thermal headroom (MW) | 3.67 | 3.21 | 2.49 | 1.67 | 0.52 | -1.05 | -2.54 | -4.02 | -5.66 | -7.27 | -8.92 | -11.02 | -13.11 | -15.09 | -16.97 | -24.64 | -28.29 | -30.41
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Steady Progression | Thermal headroom (MW) | 3.67 | 3.82 | 3.8 | 3.73 | 3.56 | 3.2 | 2.85 | 2.42 | 1.83 | 1.2 | 0.46 | -0.3 | -1.13 | -1.99 | -2.85 | -7.4 | -9.26 | -11.05
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | System Transformation | Thermal headroom (MW) | 3.67 | 3.73 | 3.59 | 3.38 | 3.05 | 2.7 | 2.32 | 1.83 | 1.11 | 0.38 | -0.36 | -1.16 | -1.97 | -2.76 | -3.42 | -7.08 | -9.75 | -10.7
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | WPD Best View | Thermal headroom (MW) | 3.67 | 3.21 | 2.49 | 1.67 | 0.52 | -1.05 | -2.54 | -4.02 | -5.66 | -7.27 | -8.92 | -11.02 | -13.11 | -15.09 | -16.97 | -24.64 | -28.29 | -30.41
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Consumer Transformation | Thermal headroom (MW) | 42.51 | 41.5274 | 39.8151 | 38.0932 | 35.7033 | 32.074 | 28.5879 | 24.8483 | 20.8883 | 16.3588 | 9.6625 | 1.8168 | -6.8992 | -15.4264 | -23.6149 | -70.9136 | -100.2258 | -115.3087
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Leading the Way | Thermal headroom (MW) | 42.51 | 40.0194 | 36.7863 | 33.7095 | 29.6014 | 23.9581 | 18.2864 | 12 | 5.5455 | -2.0817 | -10.8471 | -20.4347 | -30.0459 | -39.2215 | -47.7291 | -79.5685 | -93.3849 | -100.7627
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Steady Progression | Thermal headroom (MW) | 42.51 | 42.8976 | 42.6686 | 42.6719 | 42.4507 | 41.4318 | 40.3075 | 38.8738 | 37.3039 | 35.4363 | 32.7885 | 30.0334 | 26.9161 | 23.5032 | 20.058 | -3.1123 | -19.5034 | -27.1022
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | System Transformation | Thermal headroom (MW) | 42.51 | 42.4937 | 41.7865 | 41.2446 | 40.3407 | 39.1918 | 37.8409 | 36.123 | 34.1066 | 31.6621 | 28.2555 | 24.4819 | 20.496 | 16.5177 | 12.7292 | -12.7347 | -27.6085 | -31.0432
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | WPD Best View | Thermal headroom (MW) | 42.51 | 40.758 | 38.2362 | 35.938 | 32.7958 | 28.4062 | 23.8876 | 18.9213 | 13.8135 | 7.6741 | 0.20329 | -7.9603 | -16.348 | -24.5224 | -32.1758 | -63.827 | -78.1721 | -84.7215
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Consumer Transformation | Thermal headroom (MW) | 19.68 | 19.27 | 18.56 | 17.58 | 16.44 | 14.83 | 13.39 | 11.95 | 10.55 | 8.94 | 6.25 | 3.51 | 0.73 | -1.94 | -4.58 | -18.09 | -26.99 | -31.64
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Leading the Way | Thermal headroom (MW) | 19.68 | 18.68 | 17.34 | 15.75 | 14 | 11.74 | 9.64 | 7.35 | 5.2 | 2.72 | -0.18 | -3.26 | -6.34 | -9.19 | -11.86 | -20.43 | -24.57 | -27.04
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Steady Progression | Thermal headroom (MW) | 19.68 | 19.69 | 19.58 | 19.3 | 19.06 | 18.59 | 18.1 | 17.6 | 17.14 | 16.68 | 15.92 | 15.08 | 14.07 | 13.04 | 12 | 6.18 | 1.68 | -0.37
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | System Transformation | Thermal headroom (MW) | 19.68 | 19.57 | 19.29 | 18.77 | 18.25 | 17.68 | 17.15 | 16.54 | 15.91 | 15.17 | 13.95 | 12.63 | 11.3 | 10.02 | 8.9 | 2.33 | -1.06 | -2.2
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | WPD Best View | Thermal headroom (MW) | 19.68 | 18.89 | 17.86 | 16.66 | 15.38 | 13.75 | 12.17 | 10.5 | 8.84 | 6.91 | 4.52 | 1.98 | -0.6 | -3.13 | -5.56 | -14.44 | -18.89 | -21.19
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Consumer Transformation | Thermal headroom (MW) | 1.66 | 1.65 | 1.59 | 1.5 | 1.36 | 1.2 | 1.03 | 0.84 | 0.64 | 0.39 | 0.14 | -0.07 | -0.52 | -0.97 | -1.41 | -4 | -5.57 | -6.39
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Leading the Way | Thermal headroom (MW) | 1.66 | 1.6 | 1.5 | 1.36 | 1.17 | 0.92 | 0.65 | 0.33 | 0 | -0.35 | -0.8 | -1.34 | -1.88 | -2.35 | -2.81 | -4.56 | -5.32 | -5.77
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Steady Progression | Thermal headroom (MW) | 1.66 | 1.72 | 1.74 | 1.75 | 1.74 | 1.68 | 1.61 | 1.52 | 1.41 | 1.29 | 1.12 | 0.95 | 0.75 | 0.55 | 0.35 | -1.06 | -1.94 | -2.25
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | System Transformation | Thermal headroom (MW) | 1.66 | 1.71 | 1.71 | 1.69 | 1.65 | 1.6 | 1.53 | 1.43 | 1.3 | 1.15 | 0.96 | 0.75 | 0.54 | 0.34 | 0.16 | -1.12 | -2.21 | -2.44
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | WPD Best View | Thermal headroom (MW) | 1.66 | 1.6 | 1.5 | 1.36 | 1.17 | 0.92 | 0.65 | 0.33 | 0 | -0.35 | -0.8 | -1.34 | -1.88 | -2.35 | -2.81 | -4.56 | -5.32 | -5.77
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Consumer Transformation | Thermal headroom (MW) | 5.06 | 4.96 | 4.85 | 4.72 | 4.54 | 4.25 | 4 | 3.7 | 3.34 | 2.92 | 2.21 | 1.49 | 0.75 | 0.01 | -0.65 | -5.01 | -7.48 | -8.75
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Leading the Way | Thermal headroom (MW) | 5.06 | 4.78 | 4.52 | 4.24 | 3.89 | 3.41 | 2.95 | 2.42 | 1.89 | 1.24 | 0.52 | -0.3 | -1.08 | -1.85 | -2.54 | -5.58 | -6.8 | -7.43
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Steady Progression | Thermal headroom (MW) | 5.06 | 5.08 | 5.08 | 5.07 | 5.06 | 4.98 | 4.91 | 4.79 | 4.66 | 4.48 | 4.26 | 4.05 | 3.83 | 3.51 | 3.2 | 0.83 | -0.88 | -1.85
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | System Transformation | Thermal headroom (MW) | 5.06 | 5.05 | 5.02 | 4.99 | 4.92 | 4.81 | 4.66 | 4.51 | 4.36 | 4.17 | 3.9 | 3.58 | 3.2 | 2.78 | 2.38 | -0.6 | -2.02 | -2.32
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | WPD Best View | Thermal headroom (MW) | 5.06 | 5.05 | 5.02 | 4.98 | 4.91 | 4.78 | 4.62 | 4.46 | 4.28 | 4.05 | 3.73 | 3.36 | 2.94 | 2.49 | 2.08 | -0.92 | -2.33 | -2.64
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Consumer Transformation | Thermal headroom (MW) | 10.75 | 10.74 | 10.64 | 10.47 | 10.21 | 9.7 | 9.19 | 8.64 | 8.08 | 7.46 | 6.57 | 5.37 | 3.98 | 2.67 | 1.35 | -6.5 | -11.77 | -14.47
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Leading the Way | Thermal headroom (MW) | 10.75 | 10.53 | 10.2 | 9.83 | 9.24 | 8.35 | 7.52 | 6.62 | 5.73 | 4.67 | 3.23 | 1.69 | 0.17 | -1.35 | -2.79 | -8.41 | -11 | -12.5
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Steady Progression | Thermal headroom (MW) | 10.75 | 10.94 | 11.02 | 11.08 | 11.11 | 11.02 | 10.9 | 10.73 | 10.49 | 10.2 | 9.77 | 9.32 | 8.84 | 8.34 | 7.82 | 4.72 | 2.35 | 0.79
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | System Transformation | Thermal headroom (MW) | 10.75 | 10.88 | 10.9 | 10.88 | 10.81 | 10.71 | 10.57 | 10.32 | 9.99 | 9.6 | 9.06 | 8.47 | 7.86 | 7.28 | 6.76 | 3.32 | 1.06 | 0.32
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | WPD Best View | Thermal headroom (MW) | 10.75 | 10.55 | 10.22 | 9.86 | 9.32 | 8.47 | 7.66 | 6.8 | 5.93 | 4.94 | 3.53 | 2.02 | 0.53 | -0.96 | -2.37 | -7.95 | -10.51 | -12.01
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Consumer Transformation | Thermal headroom (MW) | 1.89 | 1.56 | 1.11 | 0.73 | 0.2 | -0.52 | -1.25 | -2.01 | -2.81 | -3.68 | -4.61 | -6.21 | -7.82 | -9.38 | -10.88 | -19.49 | -24.44 | -27.16
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Leading the Way | Thermal headroom (MW) | 1.89 | 1.38 | 0.75 | 0.24 | -0.46 | -1.45 | -2.64 | -3.94 | -5.41 | -7.16 | -8.69 | -10.32 | -11.99 | -13.6 | -15.08 | -20.91 | -23.36 | -24.65
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Steady Progression | Thermal headroom (MW) | 1.89 | 1.8 | 1.61 | 1.55 | 1.41 | 1.13 | 0.8 | 0.43 | 0.02 | -0.44 | -1.02 | -1.62 | -2.25 | -2.91 | -3.58 | -8.31 | -11.44 | -12.65
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | System Transformation | Thermal headroom (MW) | 1.89 | 1.71 | 1.42 | 1.28 | 1 | 0.71 | 0.37 | -0.04 | -0.53 | -1.11 | -1.66 | -2.26 | -2.89 | -3.51 | -4.05 | -9.4 | -12.59 | -13.47
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | WPD Best View | Thermal headroom (MW) | 1.89 | 1.42 | 0.83 | 0.36 | -0.29 | -1.15 | -2.12 | -3.23 | -4.39 | -5.89 | -7.27 | -8.75 | -10.27 | -11.77 | -13.13 | -18.68 | -21.11 | -22.35
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Consumer Transformation | Thermal headroom (MW) | -8.61 | -8.7 | -8.94 | -9.2 | -9.58 | -10.3 | -11.01 | -11.74 | -12.52 | -13.35 | -14.69 | -16.48 | -18.4 | -20.31 | -22.17 | -32.11 | -39.2 | -43.04
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Leading the Way | Thermal headroom (MW) | -8.61 | -8.99 | -9.53 | -10.09 | -10.93 | -12.12 | -13.26 | -14.48 | -15.7 | -17.26 | -19.27 | -21.36 | -23.54 | -25.64 | -27.62 | -34.37 | -37.77 | -39.88
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Steady Progression | Thermal headroom (MW) | -8.61 | -8.45 | -8.42 | -8.39 | -8.39 | -8.56 | -8.78 | -9.09 | -9.45 | -9.85 | -10.45 | -11.08 | -11.76 | -12.46 | -13.17 | -17.42 | -20.77 | -22.54
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | System Transformation | Thermal headroom (MW) | -8.61 | -8.53 | -8.61 | -8.68 | -8.81 | -9.02 | -9.33 | -9.73 | -10.2 | -10.78 | -11.59 | -12.46 | -13.34 | -14.2 | -15.11 | -19.2 | -22.04 | -22.96
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | WPD Best View | Thermal headroom (MW) | -8.61 | -8.99 | -9.53 | -10.09 | -10.93 | -12.12 | -13.26 | -14.48 | -15.7 | -17.26 | -19.27 | -21.36 | -23.54 | -25.64 | -27.62 | -34.37 | -37.77 | -39.88
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Consumer Transformation | Thermal headroom (MW) | 37.57 | 35.3867 | 32.5199 | 29.8216 | 26.4234 | 21.9434 | 17.5402 | 13.1929 | 8.6718 | 3.8482 | -3.5699 | -11.7875 | -20.8589 | -29.0361 | -36.8642 | -77.308 | -101.07 | -112.3555
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Leading the Way | Thermal headroom (MW) | 37.57 | 33.8696 | 29.4024 | 25.3573 | 20.5162 | 14.2753 | 8.1913 | 1.5758 | -5.3533 | -12.874 | -21.4668 | -30.8182 | -40.1909 | -48.5334 | -56.2228 | -82.244 | -92.6382 | -96.8088
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Steady Progression | Thermal headroom (MW) | 37.57 | 36.8819 | 35.6346 | 34.8991 | 34.0694 | 32.4897 | 30.8507 | 29.0973 | 27.2233 | 25.1914 | 22.5117 | 19.6642 | 16.6047 | 13.425 | 10.2399 | -9.8743 | -23.8585 | -29.9927
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | System Transformation | Thermal headroom (MW) | 37.57 | 36.2863 | 34.41 | 33.042 | 31.4119 | 29.8178 | 28.1919 | 26.2827 | 23.9807 | 21.3201 | 18.1277 | 14.5194 | 10.7868 | 6.7713 | 2.8624 | -18.6727 | -29.8764 | -31.6804
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | WPD Best View | Thermal headroom (MW) | 37.57 | 34.1858 | 30.1115 | 26.4608 | 22.1988 | 16.7285 | 11.3577 | 5.5287 | -0.71827 | -7.4976 | -15.4397 | -24.1104 | -32.9008 | -40.809 | -48.1906 | -74.4454 | -85.5267 | -89.5884
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Consumer Transformation | Thermal headroom (MW) | 2.16 | 2.02 | 1.64 | 1.54 | 1.41 | 1.19 | 0.99 | 0.8 | 0.6 | 0.37 | 0.14 | -0.13 | -0.43 | -0.84 | -1.23 | -3.73 | -5.23 | -5.99
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Leading the Way | Thermal headroom (MW) | 2.16 | 1.93 | 1.43 | 1.27 | 1.09 | 0.78 | 0.46 | 0.11 | -0.22 | -0.59 | -0.89 | -1.33 | -1.79 | -2.23 | -2.64 | -4.31 | -4.99 | -5.49
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Steady Progression | Thermal headroom (MW) | 2.16 | 2.11 | 1.84 | 1.84 | 1.83 | 1.76 | 1.68 | 1.57 | 1.46 | 1.35 | 1.18 | 1.01 | 0.82 | 0.61 | 0.41 | -0.6 | -1.15 | -1.36
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | System Transformation | Thermal headroom (MW) | 2.16 | 2.07 | 1.74 | 1.71 | 1.67 | 1.63 | 1.58 | 1.51 | 1.41 | 1.29 | 1.12 | 0.91 | 0.7 | 0.51 | 0.35 | -0.61 | -1.41 | -1.57
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | WPD Best View | Thermal headroom (MW) | 2.16 | 1.93 | 1.43 | 1.27 | 1.09 | 0.78 | 0.46 | 0.11 | -0.22 | -0.59 | -0.89 | -1.33 | -1.79 | -2.23 | -2.64 | -4.31 | -4.99 | -5.49
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Consumer Transformation | Thermal headroom (MW) | 6.71 | 5.45 | 4.02 | 2.89 | 1.89 | 0.68 | -0.5 | -1.68 | -2.97 | -4.29 | -6.39 | -9.04 | -11.69 | -13.92 | -16.07 | -27.65 | -35.47 | -39.19
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Leading the Way | Thermal headroom (MW) | 6.71 | 5.01 | 3.14 | 1.64 | 0.28 | -1.34 | -3.14 | -5.06 | -7.17 | -9.42 | -11.8 | -14.32 | -16.89 | -19.33 | -21.58 | -29.77 | -33.67 | -35.91
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Steady Progression | Thermal headroom (MW) | 6.71 | 5.94 | 5.08 | 4.55 | 4.21 | 3.71 | 3.15 | 2.58 | 1.93 | 1.19 | 0.34 | -0.54 | -1.45 | -2.4 | -3.33 | -9.35 | -14.3 | -16.21
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | System Transformation | Thermal headroom (MW) | 6.71 | 5.72 | 4.64 | 3.91 | 3.4 | 2.95 | 2.42 | 1.79 | 0.93 | 0 | -0.99 | -2.06 | -3.11 | -4.48 | -5.88 | -12.91 | -16.69 | -17.5
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | WPD Best View | Thermal headroom (MW) | 6.71 | 5.01 | 3.15 | 1.65 | 0.3 | -1.3 | -3.08 | -5 | -7.09 | -9.34 | -11.71 | -14.22 | -16.78 | -19.21 | -21.45 | -29.61 | -33.5 | -35.74
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Consumer Transformation | Thermal headroom (MW) | 8.36 | 7.36 | 6.79 | 6.02 | 5.07 | 3.94 | 3.02 | 2.2 | 1.27 | 0.21 | -1.75 | -4.09 | -6.5 | -8.45 | -10.32 | -20.74 | -28.06 | -31.58
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Leading the Way | Thermal headroom (MW) | 8.36 | 6.81 | 5.71 | 4.55 | 3.19 | 1.6 | 0.19 | -1.26 | -2.77 | -4.47 | -6.52 | -8.7 | -10.86 | -12.94 | -14.9 | -22.18 | -25.9 | -27.69
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Steady Progression | Thermal headroom (MW) | 8.36 | 7.81 | 7.67 | 7.46 | 7.22 | 6.82 | 6.44 | 6.06 | 5.71 | 5.3 | 4.75 | 4.14 | 3.52 | 2.85 | 2.15 | -3.17 | -7.23 | -9.17
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | System Transformation | Thermal headroom (MW) | 8.36 | 7.64 | 7.33 | 6.98 | 6.52 | 6.11 | 5.81 | 5.45 | 5.07 | 4.56 | 3.91 | 3.13 | 2.32 | 1.11 | -0.17 | -6.26 | -9.35 | -10.35
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | WPD Best View | Thermal headroom (MW) | 8.36 | 6.86 | 5.84 | 4.78 | 3.55 | 2 | 0.64 | -0.78 | -2.25 | -3.9 | -5.92 | -8.08 | -10.21 | -12.29 | -14.24 | -21.47 | -25.16 | -26.91
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Consumer Transformation | Thermal headroom (MW) | 9.424 | 9.124 | 8.754 | 8.274 | 7.544 | 6.574 | 5.594 | 4.524 | 3.384 | 2.144 | -0.326 | -2.926 | -5.606 | -7.866 | -10.046 | -19.326 | -24.356 | -26.866
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Leading the Way | Thermal headroom (MW) | 9.424 | 8.824 | 8.164 | 7.414 | 6.354 | 5.124 | 3.944 | 2.474 | 0.464 | -1.816 | -4.506 | -7.336 | -10.236 | -12.406 | -14.386 | -19.386 | -21.156 | -21.126
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Steady Progression | Thermal headroom (MW) | 9.424 | 9.444 | 9.384 | 9.314 | 9.194 | 8.894 | 8.584 | 8.214 | 7.824 | 7.434 | 6.864 | 6.244 | 5.514 | 4.814 | 4.144 | -0.196 | -4.476 | -6.056
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | System Transformation | Thermal headroom (MW) | 9.424 | 9.304 | 9.114 | 8.904 | 8.594 | 8.234 | 7.834 | 7.344 | 6.774 | 6.154 | 5.304 | 4.334 | 3.334 | 2.584 | 1.904 | -3.516 | -5.866 | -6.016
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | WPD Best View | Thermal headroom (MW) | 9.424 | 8.824 | 8.164 | 7.414 | 6.354 | 5.124 | 3.944 | 2.474 | 0.464 | -1.816 | -4.506 | -7.336 | -10.236 | -12.406 | -14.386 | -19.386 | -21.156 | -21.126
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Consumer Transformation | Thermal headroom (MW) | 22.73 | 23.0417 | 22.742 | 22.1429 | 21.0869 | 18.9364 | 15.6377 | 12.2936 | 9.3595 | 5.9251 | 0.3045 | -6.3825 | -13.6087 | -19.7376 | -25.5746 | -58.2467 | -75.6341 | -83.7579
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Leading the Way | Thermal headroom (MW) | 22.73 | 22.3837 | 21.3644 | 20.0789 | 18.2219 | 14.5233 | 8.8613 | 2.6474 | -2.8287 | -8.9014 | -14.8838 | -21.3593 | -27.7902 | -34.0105 | -39.5624 | -61.4222 | -69.6645 | -73.2641
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Steady Progression | Thermal headroom (MW) | 22.73 | 23.5359 | 23.7861 | 23.9507 | 23.9386 | 23.0793 | 21.5741 | 19.9625 | 18.6042 | 17.1276 | 15 | 12.9086 | 10.6233 | 8.0816 | 5.4281 | -16.0125 | -27.839 | -32.8072
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | System Transformation | Thermal headroom (MW) | 22.73 | 23.3859 | 23.4665 | 23.4018 | 23.0335 | 22.4825 | 20.7386 | 18.8617 | 17.4772 | 15.8435 | 13.5661 | 11.113 | 8.6069 | 5.1272 | 1.3033 | -22.5186 | -35.2967 | -37.9605
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | WPD Best View | Thermal headroom (MW) | 22.73 | 23.3598 | 23.4023 | 23.2808 | 22.8543 | 21.9584 | 19.8843 | 17.7016 | 16.0559 | 14.1041 | 11.4213 | 8.595 | 5.7119 | 1.8344 | -2.43 | -27.0183 | -39.5317 | -42.7663
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Consumer Transformation | Thermal headroom (MW) | 11.6 | 11.75 | 11.8 | 11.84 | 11.86 | 11.74 | 10.85 | 9.89 | 9.29 | 8.73 | 8.04 | 7.34 | 6.61 | 5.88 | 5.12 | 1.85 | 0.85 | 0.62
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Leading the Way | Thermal headroom (MW) | 11.6 | 11.65 | 11.6 | 11.55 | 11.47 | 11.18 | 9.87 | 8.37 | 7.54 | 6.75 | 6 | 5.24 | 4.46 | 3.69 | 2.97 | 1.21 | 1.04 | 1.1
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Steady Progression | Thermal headroom (MW) | 11.6 | 11.77 | 11.85 | 11.92 | 11.98 | 11.96 | 11.55 | 11.09 | 10.85 | 10.63 | 10.33 | 10.03 | 9.68 | 9.28 | 8.88 | 6.93 | 6.62 | 6.76
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | System Transformation | Thermal headroom (MW) | 11.6 | 11.76 | 11.83 | 11.89 | 11.93 | 11.96 | 11.3 | 10.61 | 10.34 | 10.09 | 9.69 | 9.3 | 8.89 | 8.49 | 8.09 | 6.11 | 5.74 | 5.89
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | WPD Best View | Thermal headroom (MW) | 11.6 | 11.76 | 11.83 | 11.89 | 11.93 | 11.96 | 11.3 | 10.61 | 10.34 | 10.09 | 9.69 | 9.3 | 8.89 | 8.49 | 8.09 | 6.11 | 5.74 | 5.89
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Consumer Transformation | Thermal headroom (MW) | 2.98 | 2.99 | 2.97 | 2.93 | 2.86 | 2.75 | 2.65 | 2.52 | 2.37 | 2.22 | 1.99 | 1.71 | 1.31 | 0.9 | 0.53 | -1.95 | -3.21 | -3.81
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Leading the Way | Thermal headroom (MW) | 2.98 | 2.96 | 2.9 | 2.82 | 2.71 | 2.48 | 2.23 | 1.96 | 1.68 | 1.39 | 1.06 | 0.66 | 0.26 | -0.11 | -0.47 | -2.25 | -2.84 | -3.15
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Steady Progression | Thermal headroom (MW) | 2.98 | 3.02 | 3.03 | 3.04 | 3.03 | 2.98 | 2.92 | 2.86 | 2.78 | 2.7 | 2.57 | 2.44 | 2.3 | 2.14 | 1.99 | 0.64 | -0.28 | -0.91
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | System Transformation | Thermal headroom (MW) | 2.98 | 3.02 | 3.02 | 3.02 | 2.99 | 2.96 | 2.92 | 2.87 | 2.81 | 2.71 | 2.58 | 2.43 | 2.29 | 2.15 | 2.02 | 0.34 | -0.73 | -1
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | WPD Best View | Thermal headroom (MW) | 2.98 | 3.02 | 3.02 | 3.02 | 2.99 | 2.96 | 2.92 | 2.87 | 2.81 | 2.71 | 2.58 | 2.43 | 2.29 | 2.15 | 2.02 | 0.34 | -0.73 | -1
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Consumer Transformation | Thermal headroom (MW) | 7.24 | 7.24 | 7.02 | 6.66 | 6.08 | 5.19 | 4.2 | 3.37 | 2.51 | 1.59 | -0.58 | -3.18 | -5.72 | -7.85 | -9.93 | -20.92 | -28.02 | -32.05
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Leading the Way | Thermal headroom (MW) | 7.24 | 7.06 | 6.64 | 6.09 | 5.28 | 3.82 | 2.13 | 0.59 | -1.34 | -3.48 | -5.65 | -8.03 | -10.37 | -12.57 | -14.55 | -22.18 | -26.16 | -28.49
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Steady Progression | Thermal headroom (MW) | 7.24 | 7.47 | 7.5 | 7.5 | 7.44 | 7.08 | 6.65 | 6.28 | 5.86 | 5.4 | 4.78 | 4.16 | 3.5 | 2.81 | 2.11 | -4.48 | -8.56 | -10.19
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | System Transformation | Thermal headroom (MW) | 7.24 | 7.39 | 7.34 | 7.23 | 7.01 | 6.66 | 6.17 | 5.74 | 5.21 | 4.66 | 3.98 | 3.23 | 2.48 | 1.39 | 0.07 | -7.4 | -11.41 | -12.81
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | WPD Best View | Thermal headroom (MW) | 7.24 | 7.4 | 7.34 | 7.22 | 6.99 | 6.58 | 6.03 | 5.55 | 4.99 | 4.41 | 3.7 | 2.95 | 2.2 | 1.08 | -0.53 | -7.91 | -11.72 | -13.07
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Consumer Transformation | Thermal headroom (MW) | 5.12 | 5.13 | 5.08 | 4.96 | 4.75 | 4.46 | 4.01 | 3.52 | 3.16 | 2.58 | 1.59 | 0.26 | -1.13 | -2.1 | -2.99 | -7.71 | -10.31 | -11.33
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Leading the Way | Thermal headroom (MW) | 5.12 | 5.06 | 4.92 | 4.73 | 4.43 | 4.01 | 3.22 | 2.26 | 1.46 | 0.49 | -0.49 | -1.53 | -2.57 | -3.6 | -4.43 | -7.43 | -8.64 | -8.92
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Steady Progression | Thermal headroom (MW) | 5.12 | 5.23 | 5.27 | 5.3 | 5.28 | 5.16 | 4.94 | 4.67 | 4.46 | 4.19 | 3.83 | 3.47 | 3.09 | 2.69 | 2.23 | -1.56 | -3.59 | -4.39
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | System Transformation | Thermal headroom (MW) | 5.12 | 5.19 | 5.2 | 5.18 | 5.09 | 5.02 | 4.78 | 4.46 | 4.25 | 3.95 | 3.6 | 3.24 | 2.85 | 2.08 | 1.16 | -2.93 | -4.94 | -5.22
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | WPD Best View | Thermal headroom (MW) | 5.12 | 5.2 | 5.21 | 5.19 | 5.1 | 5.02 | 4.77 | 4.45 | 4.23 | 3.93 | 3.58 | 3.21 | 2.82 | 1.96 | 1.04 | -3 | -4.94 | -5.21
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Consumer Transformation | Thermal headroom (MW) | 70.8939 | 69.7987 | 69.0594 | 68.0133 | 66.4843 | 64.5271 | 62.4816 | 60.3189 | 57.9475 | 55.492 | 52.2068 | 47.767 | 42.628 | 37.8609 | 33.2959 | 9.2657 | -4.9076 | -11.6632
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Leading the Way | Thermal headroom (MW) | 70.8939 | 69.1226 | 67.779 | 66.1812 | 64.0296 | 61.203 | 58.2325 | 54.7035 | 50.7816 | 46.5493 | 41.8732 | 36.7349 | 31.6745 | 26.7476 | 22.2755 | 6.5151 | 0.1641 | -2.1144
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Steady Progression | Thermal headroom (MW) | 70.8939 | 70.5175 | 70.4789 | 70.3783 | 70.1527 | 69.5165 | 68.7677 | 67.8662 | 66.9318 | 65.8771 | 64.4915 | 63.0028 | 61.4255 | 59.7227 | 57.998 | 46.2986 | 36.6229 | 32.9799
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | System Transformation | Thermal headroom (MW) | 70.8939 | 70.1759 | 69.8815 | 69.4642 | 68.8253 | 68.1748 | 67.4006 | 66.3016 | 64.9916 | 63.5328 | 61.8352 | 59.9403 | 57.9827 | 55.8444 | 53.87 | 40.2583 | 32.7432 | 31.4403
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | WPD Best View | Thermal headroom (MW) | 70.8939 | 69.8131 | 69.2754 | 68.554 | 67.5285 | 66.228 | 64.7936 | 63.0093 | 61.0219 | 58.8849 | 56.3663 | 53.4416 | 50.5449 | 47.4287 | 44.5843 | 31.0073 | 24.6986 | 23.3351
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Consumer Transformation | Thermal headroom (MW) | 14.142 | 14.052 | 13.762 | 13.352 | 12.662 | 11.642 | 10.602 | 9.212 | 7.722 | 6.242 | 3.832 | 0.632 | -2.648 | -5.508 | -8.308 | -22.188 | -31.348 | -35.868
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Leading the Way | Thermal headroom (MW) | 14.142 | 13.692 | 13.032 | 12.272 | 11.172 | 9.532 | 7.982 | 5.752 | 2.962 | 0.202 | -2.678 | -5.768 | -8.838 | -11.828 | -14.658 | -23.938 | -28.238 | -30.078
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Steady Progression | Thermal headroom (MW) | 14.142 | 14.412 | 14.492 | 14.532 | 14.482 | 14.192 | 13.892 | 13.372 | 12.772 | 12.042 | 11.182 | 10.302 | 9.382 | 8.422 | 7.442 | 1.052 | -4.938 | -7.638
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | System Transformation | Thermal headroom (MW) | 14.142 | 14.282 | 14.222 | 14.092 | 13.832 | 13.512 | 13.172 | 12.392 | 11.392 | 10.402 | 9.282 | 8.072 | 6.832 | 5.282 | 3.852 | -3.448 | -7.338 | -8.378
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | WPD Best View | Thermal headroom (MW) | 14.142 | 14.282 | 14.222 | 14.092 | 13.832 | 13.512 | 13.172 | 12.392 | 11.392 | 10.402 | 9.282 | 8.072 | 6.832 | 5.282 | 3.852 | -3.448 | -7.338 | -8.378
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Consumer Transformation | Thermal headroom (MW) | 4.43 | 4.46 | 4.46 | 4.43 | 4.37 | 4.28 | 4.18 | 4.09 | 3.98 | 3.87 | 3.74 | 3.54 | 3.23 | 2.92 | 2.63 | 1.14 | 0.23 | -0.22
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Leading the Way | Thermal headroom (MW) | 4.43 | 4.43 | 4.4 | 4.34 | 4.24 | 4.11 | 3.97 | 3.82 | 3.66 | 3.47 | 3.22 | 2.9 | 2.6 | 2.31 | 2.03 | 1.02 | 0.61 | 0.48
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Steady Progression | Thermal headroom (MW) | 4.43 | 4.49 | 4.52 | 4.54 | 4.55 | 4.53 | 4.5 | 4.47 | 4.42 | 4.37 | 4.28 | 4.19 | 4.09 | 3.98 | 3.87 | 2.96 | 2.29 | 2
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | System Transformation | Thermal headroom (MW) | 4.43 | 4.48 | 4.49 | 4.5 | 4.48 | 4.47 | 4.46 | 4.43 | 4.38 | 4.32 | 4.23 | 4.14 | 4.04 | 3.95 | 3.87 | 2.8 | 2.2 | 2.08
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | WPD Best View | Thermal headroom (MW) | 4.43 | 4.43 | 4.4 | 4.34 | 4.24 | 4.11 | 3.97 | 3.82 | 3.66 | 3.47 | 3.22 | 2.9 | 2.6 | 2.31 | 2.03 | 1.02 | 0.59 | 0.47
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Consumer Transformation | Thermal headroom (MW) | 2.68 | 2.79 | 2.48 | 2.17 | 1.87 | 1.39 | 0.97 | 0.53 | -0.01 | -0.77 | -2.16 | -3.58 | -5.04 | -6.43 | -7.66 | -14.96 | -19.46 | -21.56
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Leading the Way | Thermal headroom (MW) | 2.68 | 2.48 | 1.85 | 1.24 | 0.57 | -0.29 | -1.05 | -1.92 | -2.84 | -3.99 | -5.45 | -6.99 | -8.55 | -10.04 | -11.35 | -15.78 | -17.46 | -17.81
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Steady Progression | Thermal headroom (MW) | 2.68 | 2.96 | 2.91 | 2.89 | 2.91 | 2.84 | 2.74 | 2.64 | 2.53 | 2.33 | 2.06 | 1.71 | 1.36 | 0.89 | 0.39 | -3.89 | -7.27 | -8.23
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | System Transformation | Thermal headroom (MW) | 2.68 | 2.87 | 2.68 | 2.51 | 2.38 | 2.27 | 2.15 | 1.98 | 1.8 | 1.5 | 1.08 | 0.53 | -0.13 | -0.89 | -1.66 | -6.4 | -8.6 | -8.52
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | WPD Best View | Thermal headroom (MW) | 2.68 | 2.87 | 2.68 | 2.51 | 2.38 | 2.27 | 2.15 | 1.98 | 1.8 | 1.5 | 1.08 | 0.53 | -0.13 | -0.89 | -1.66 | -6.4 | -8.6 | -8.52
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Consumer Transformation | Thermal headroom (MW) | 8.07 | 8.02 | 7.77 | 7.46 | 6.99 | 6.61 | 6.15 | 5.73 | 5.29 | 4.81 | 4.1 | 3.01 | 1.7 | 0.43 | -0.82 | -7.84 | -12.17 | -14.23
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Leading the Way | Thermal headroom (MW) | 8.07 | 7.88 | 7.48 | 7.03 | 6.4 | 5.8 | 5.03 | 4.18 | 3.43 | 2.54 | 1.26 | -0.12 | -1.51 | -2.86 | -4.11 | -8.67 | -10.69 | -11.43
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Steady Progression | Thermal headroom (MW) | 8.07 | 8.2 | 8.19 | 8.17 | 8.1 | 7.97 | 7.81 | 7.64 | 7.49 | 7.32 | 7.03 | 6.69 | 6.32 | 5.92 | 5.54 | 2.91 | 0.18 | -0.86
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | System Transformation | Thermal headroom (MW) | 8.07 | 8.15 | 8.07 | 7.96 | 7.78 | 7.63 | 7.44 | 7.22 | 7.01 | 6.71 | 6.26 | 5.76 | 5.25 | 4.77 | 4.35 | 0.96 | -1.07 | -1.48
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | WPD Best View | Thermal headroom (MW) | 8.07 | 8.15 | 8.07 | 7.96 | 7.78 | 7.63 | 7.44 | 7.22 | 7.01 | 6.71 | 6.26 | 5.76 | 5.25 | 4.77 | 4.35 | 0.96 | -1.07 | -1.48
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Consumer Transformation | Thermal headroom (MW) | 0.07 | -0.93 | -1.2 | -1.6 | -2.15 | -2.85 | -3.59 | -4.31 | -5.1 | -5.84 | -6.51 | -7.5 | -8.7 | -9.8 | -10.84 | -16.24 | -18.76 | -19.9
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Leading the Way | Thermal headroom (MW) | 0.07 | -1.13 | -1.49 | -1.98 | -2.58 | -3.43 | -4.38 | -5.43 | -6.6 | -7.83 | -8.93 | -10.1 | -11.24 | -12.38 | -13.33 | -16.89 | -18.02 | -18.45
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Steady Progression | Thermal headroom (MW) | 0.07 | -0.69 | -0.79 | -0.93 | -1.1 | -1.39 | -1.73 | -2.1 | -2.45 | -2.8 | -3.2 | -3.61 | -4.06 | -4.53 | -4.99 | -7.5 | -9.24 | -9.75
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | System Transformation | Thermal headroom (MW) | 0.07 | -0.84 | -0.99 | -1.19 | -1.44 | -1.75 | -2.11 | -2.5 | -2.96 | -3.41 | -3.84 | -4.31 | -4.78 | -5.26 | -5.69 | -8.57 | -10.25 | -10.52
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | WPD Best View | Thermal headroom (MW) | 0.07 | -1.06 | -1.31 | -1.66 | -2.06 | -2.66 | -3.32 | -4.05 | -4.85 | -5.61 | -6.41 | -7.26 | -8.1 | -9 | -9.76 | -12.74 | -13.76 | -14.06
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Consumer Transformation | Thermal headroom (MW) | 24.1 | 24.25 | 24.27 | 24.26 | 24.2 | 24.09 | 23.97 | 23.81 | 23.63 | 23.39 | 22.99 | 22.22 | 21.43 | 20.68 | 19.95 | 16.54 | 14.77 | 13.93
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Leading the Way | Thermal headroom (MW) | 24.1 | 24.19 | 24.14 | 24.08 | 23.94 | 23.69 | 23.41 | 23.07 | 22.74 | 22.03 | 21.18 | 20.3 | 19.42 | 18.6 | 17.86 | 15.84 | 15.41 | 15.46
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Steady Progression | Thermal headroom (MW) | 24.1 | 24.33 | 24.44 | 24.53 | 24.61 | 24.66 | 24.7 | 24.73 | 24.74 | 24.73 | 24.65 | 24.56 | 24.46 | 24.31 | 24.16 | 22.39 | 20.81 | 20.66
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | System Transformation | Thermal headroom (MW) | 24.1 | 24.3 | 24.38 | 24.43 | 24.46 | 24.48 | 24.47 | 24.44 | 24.37 | 24.26 | 24.12 | 23.91 | 23.68 | 23.45 | 23.25 | 20.83 | 20.06 | 20.32
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | WPD Best View | Thermal headroom (MW) | 24.1 | 24.3 | 24.38 | 24.43 | 24.46 | 24.48 | 24.47 | 24.44 | 24.37 | 24.26 | 24.12 | 23.91 | 23.68 | 23.45 | 23.25 | 20.83 | 20.06 | 20.32
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Consumer Transformation | Thermal headroom (MW) | 45.1539 | 40.1622 | 34.333 | 31.7967 | 26.0466 | 22.7937 | 20.175 | 16.7995 | 14.2817 | 11.4369 | 6.7151 | 1.3733 | -4.2152 | -9.7052 | -15.3234 | -44.4878 | -63.085 | -71.6819
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Leading the Way | Thermal headroom (MW) | 45.1539 | 38.8436 | 31.6752 | 28.6131 | 21.6085 | 17.1187 | 13.2524 | 7.6416 | 3.1423 | -2.2182 | -7.3628 | -13.4685 | -19.7322 | -25.8097 | -31.3504 | -49.7829 | -57.6654 | -60.9631
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Steady Progression | Thermal headroom (MW) | 45.1539 | 41.5229 | 37.1373 | 35.8069 | 32.021 | 29.9626 | 28.136 | 26.021 | 24.6008 | 23.06 | 20.9464 | 19.1099 | 17.2202 | 15.4052 | 13.7035 | 2.1348 | -6.152 | -8.2731
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | System Transformation | Thermal headroom (MW) | 45.1539 | 40.6434 | 35.3793 | 33.5951 | 28.8493 | 27.0336 | 25.7546 | 23.6154 | 22.0857 | 20.4074 | 18.0396 | 16.0041 | 13.5235 | 10.8431 | 8.325 | -4.1163 | -12.2271 | -13.3773
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | WPD Best View | Thermal headroom (MW) | 45.1539 | 40.4 | 34.8569 | 32.6611 | 27.3671 | 24.5325 | 22.2921 | 19.3208 | 17.2075 | 14.6112 | 10.9389 | 7.0561 | 2.9077 | -1.0923 | -5.3361 | -29.7802 | -44.5334 | -50.4074
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Consumer Transformation | Thermal headroom (MW) | 2.3 | 1.98 | 1.43 | -0.02 | -1.67 | -2.78 | -4.01 | -5.27 | -6.51 | -7.79 | -9.37 | -11.65 | -14 | -15.96 | -17.86 | -27.52 | -33.39 | -35.84
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Leading the Way | Thermal headroom (MW) | 2.3 | 1.69 | 0.82 | -1.11 | -3.34 | -5.01 | -6.63 | -8.4 | -10.13 | -12.45 | -14.71 | -16.94 | -18.98 | -20.89 | -22.67 | -28.46 | -30.78 | -31.37
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Steady Progression | Thermal headroom (MW) | 2.3 | 2.3 | 2.13 | 1.31 | 0.42 | -0.07 | -0.6 | -1.15 | -1.7 | -2.3 | -3.08 | -3.83 | -4.54 | -5.24 | -5.9 | -9.9 | -13.26 | -14.54
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | System Transformation | Thermal headroom (MW) | 2.3 | 2.19 | 1.88 | 0.81 | -0.37 | -0.87 | -1.47 | -2.12 | -2.85 | -3.65 | -4.49 | -5.29 | -6.03 | -7.1 | -8.08 | -12.7 | -15.42 | -16
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | WPD Best View | Thermal headroom (MW) | 2.3 | 1.98 | 1.43 | -0.02 | -1.67 | -2.78 | -4.01 | -5.27 | -6.51 | -7.79 | -9.37 | -11.65 | -14 | -15.96 | -17.86 | -27.52 | -33.39 | -35.84
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Consumer Transformation | Thermal headroom (MW) | 30.94 | 29.9 | 28.78 | 28.65 | 27.86 | 27.66 | 27.63 | 27.42 | 27.42 | 27.38 | 27.28 | 27.22 | 27.16 | 27.11 | 27.06 | 27.01 | 27.22 | 27.56
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Leading the Way | Thermal headroom (MW) | 30.94 | 29.76 | 28.49 | 28.44 | 27.58 | 27.44 | 27.46 | 27.15 | 27.18 | 27.17 | 27.14 | 27.08 | 27.04 | 27 | 26.96 | 27.17 | 27.54 | 27.98
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Steady Progression | Thermal headroom (MW) | 30.94 | 30.04 | 29.05 | 28.93 | 28.24 | 28 | 27.83 | 27.61 | 27.56 | 27.57 | 27.58 | 27.6 | 27.61 | 27.67 | 27.72 | 27.77 | 27.99 | 28.36
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | System Transformation | Thermal headroom (MW) | 30.94 | 29.91 | 28.78 | 28.66 | 27.86 | 27.68 | 27.66 | 27.46 | 27.47 | 27.48 | 27.48 | 27.53 | 27.54 | 27.51 | 27.48 | 27.52 | 27.83 | 28.28
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | WPD Best View | Thermal headroom (MW) | 30.94 | 29.9 | 28.78 | 28.65 | 27.86 | 27.66 | 27.63 | 27.42 | 27.42 | 27.38 | 27.28 | 27.22 | 27.16 | 27.11 | 27.06 | 27.01 | 27.22 | 27.56
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Consumer Transformation | Thermal headroom (MW) | -0.714 | -1.134 | -1.684 | -2.264 | -3.004 | -3.824 | -4.584 | -5.324 | -6.044 | -6.764 | -7.704 | -8.714 | -9.764 | -10.864 | -12.134 | -20.244 | -25.144 | -27.664
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Leading the Way | Thermal headroom (MW) | -0.714 | -1.354 | -2.134 | -2.904 | -3.844 | -5.024 | -6.304 | -7.584 | -8.924 | -10.344 | -11.454 | -12.954 | -14.574 | -16.174 | -17.584 | -23.314 | -26.304 | -28.224
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Steady Progression | Thermal headroom (MW) | -0.714 | -0.894 | -1.164 | -1.384 | -1.634 | -2.034 | -2.464 | -2.914 | -3.324 | -3.834 | -4.534 | -5.104 | -5.714 | -6.354 | -6.934 | -10.114 | -12.124 | -13.004
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | System Transformation | Thermal headroom (MW) | -0.714 | -1.014 | -1.394 | -1.744 | -2.154 | -2.574 | -3.034 | -3.504 | -4.024 | -4.524 | -5.344 | -6.004 | -6.784 | -7.434 | -8.104 | -11.104 | -14.164 | -15.384
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | WPD Best View | Thermal headroom (MW) | -0.714 | -1.064 | -1.514 | -1.964 | -2.534 | -3.224 | -3.924 | -4.604 | -5.264 | -5.934 | -6.834 | -7.764 | -8.774 | -9.734 | -10.954 | -18.524 | -23.224 | -25.484
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Consumer Transformation | Thermal headroom (MW) | 7.31 | 6.71 | 5.98 | 5.21 | 4.09 | 2.93 | 1.66 | 0.28 | -1.11 | -2.68 | -6.66 | -11.13 | -15.7 | -20.11 | -24.6 | -44.08 | -60.74 | -70.47
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Leading the Way | Thermal headroom (MW) | 7.31 | 6.27 | 5.06 | 3.9 | 2.16 | -0.09 | -2.21 | -4.84 | -8.03 | -11.58 | -15.47 | -19.78 | -24.27 | -28.76 | -33.04 | -46.43 | -53.85 | -58.29
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Steady Progression | Thermal headroom (MW) | 7.31 | 7.21 | 6.96 | 6.74 | 6.34 | 5.83 | 5.31 | 4.76 | 4.22 | 3.22 | 1.87 | 0.81 | -0.32 | -1.57 | -2.75 | -10.7 | -17.64 | -20.53
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | System Transformation | Thermal headroom (MW) | 7.31 | 7.02 | 6.58 | 6.15 | 5.46 | 5.03 | 4.59 | 4 | 3.2 | 2.21 | 0.9 | -0.49 | -2.27 | -4.03 | -5.63 | -15.22 | -20.39 | -22.12
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | WPD Best View | Thermal headroom (MW) | 7.31 | 7.1 | 6.78 | 6.47 | 5.98 | 5.46 | 4.96 | 4.43 | 3.85 | 2.76 | 1.27 | 0.1 | -1.12 | -2.44 | -3.69 | -12.86 | -20.48 | -24.2
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Consumer Transformation | Thermal headroom (MW) | 7.44 | 7.54 | 7.55 | 7.52 | 7.41 | 7.16 | 6.93 | 6.68 | 6.42 | 6.11 | 5.6 | 5.07 | 4.41 | 3.53 | 2.71 | -2.34 | -5.29 | -6.68
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Leading the Way | Thermal headroom (MW) | 7.44 | 7.44 | 7.35 | 7.23 | 6.99 | 6.53 | 6.07 | 5.48 | 4.91 | 4.31 | 3.7 | 2.86 | 1.89 | 0.96 | 0.15 | -3.04 | -4.33 | -4.92
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Steady Progression | Thermal headroom (MW) | 7.44 | 7.65 | 7.75 | 7.84 | 7.9 | 7.83 | 7.74 | 7.63 | 7.5 | 7.34 | 7.08 | 6.82 | 6.53 | 6.22 | 5.92 | 3.79 | 2.06 | 1.53
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | System Transformation | Thermal headroom (MW) | 7.44 | 7.61 | 7.68 | 7.73 | 7.74 | 7.69 | 7.63 | 7.53 | 7.4 | 7.23 | 6.92 | 6.57 | 6.21 | 5.85 | 5.53 | 3.51 | 1.65 | 1.25
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | WPD Best View | Thermal headroom (MW) | 7.44 | 7.54 | 7.55 | 7.52 | 7.41 | 7.16 | 6.93 | 6.68 | 6.42 | 6.1 | 5.6 | 5.09 | 4.47 | 3.69 | 2.86 | -2.27 | -5.28 | -6.68
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Consumer Transformation | Thermal headroom (MW) | 6.39 | 6.34 | 6 | 5.5 | 4.84 | 3.56 | 2.14 | 0.63 | -0.86 | -2.45 | -4.91 | -8 | -12.06 | -15.61 | -19.14 | -38.08 | -50.91 | -57.28
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Leading the Way | Thermal headroom (MW) | 6.39 | 5.81 | 4.88 | 3.86 | 2.65 | 0.48 | -1.79 | -4.3 | -6.69 | -9.69 | -13.49 | -17.43 | -21.43 | -25.32 | -28.97 | -42.13 | -48.14 | -51.44
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Steady Progression | Thermal headroom (MW) | 6.39 | 6.86 | 7.05 | 7.18 | 7.27 | 6.94 | 6.56 | 6.1 | 5.51 | 4.77 | 3.62 | 2.46 | 1.19 | -0.15 | -1.49 | -9.39 | -16.15 | -19.48
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | System Transformation | Thermal headroom (MW) | 6.39 | 6.7 | 6.71 | 6.64 | 6.48 | 6.2 | 5.86 | 5.23 | 4.43 | 3.46 | 2.02 | 0.46 | -1.14 | -3.04 | -4.77 | -13.59 | -19.52 | -21.15
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | WPD Best View | Thermal headroom (MW) | 6.39 | 6.86 | 7.05 | 7.18 | 7.27 | 6.94 | 6.56 | 6.09 | 5.49 | 4.74 | 3.59 | 2.42 | 1.15 | -0.19 | -1.54 | -9.47 | -16.2 | -19.55
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Consumer Transformation | Thermal headroom (MW) | 31.01 | 30.9406 | 30.4777 | 29.8849 | 27.5403 | 24.327 | 22.3835 | 20.7525 | 19.2489 | 17.5272 | 15.1116 | 12.6795 | 10.214 | 7.8227 | 5.5824 | -4.7793 | -9.3307 | -10.8486
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Leading the Way | Thermal headroom (MW) | 31.01 | 30.4883 | 29.5472 | 28.5371 | 25.2511 | 20.5342 | 18.0081 | 15.9649 | 13.9547 | 11.7948 | 9.4869 | 7.0472 | 4.7313 | 2.5076 | 0.55052 | -5.8613 | -7.1501 | -6.4865
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Steady Progression | Thermal headroom (MW) | 31.01 | 31.3046 | 31.3732 | 31.3538 | 29.9758 | 28.1053 | 27.2424 | 26.5787 | 25.9891 | 25.2718 | 24.3175 | 23.2718 | 22.0955 | 20.9361 | 19.7461 | 12.4839 | 8.4792 | 7.2584
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | System Transformation | Thermal headroom (MW) | 31.01 | 31.2454 | 31.1376 | 31.0234 | 29.1989 | 26.8631 | 25.864 | 25.1589 | 24.3949 | 23.5553 | 22.3656 | 21.1821 | 19.8671 | 18.4562 | 17.0108 | 8.9964 | 6.3828 | 6.6105
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | WPD Best View | Thermal headroom (MW) | 31.01 | 31.3046 | 31.3732 | 31.3538 | 29.9758 | 28.1053 | 27.2424 | 26.5787 | 25.9891 | 25.2718 | 24.3175 | 23.2718 | 22.0955 | 20.9361 | 19.7461 | 12.4839 | 8.4792 | 7.2584
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Consumer Transformation | Thermal headroom (MW) | 6.84 | 6.8 | 6.54 | 6.21 | 4.91 | 3.13 | 2.05 | 1.15 | 0.31 | -0.64 | -1.98 | -3.33 | -4.7 | -6.02 | -7.26 | -13.01 | -15.53 | -16.38
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Leading the Way | Thermal headroom (MW) | 6.84 | 6.55 | 6.02 | 5.46 | 3.64 | 1.03 | -0.37 | -1.51 | -2.62 | -3.82 | -5.1 | -6.45 | -7.74 | -8.97 | -10.05 | -13.61 | -14.32 | -13.96
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Steady Progression | Thermal headroom (MW) | 6.84 | 7 | 7.04 | 7.03 | 6.26 | 5.23 | 4.75 | 4.38 | 4.05 | 3.65 | 3.12 | 2.54 | 1.89 | 1.25 | 0.59 | -3.44 | -5.66 | -6.33
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | System Transformation | Thermal headroom (MW) | 6.84 | 6.97 | 6.91 | 6.84 | 5.83 | 4.54 | 3.98 | 3.59 | 3.17 | 2.7 | 2.04 | 1.39 | 0.66 | -0.13 | -0.93 | -5.37 | -6.82 | -6.69
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | WPD Best View | Thermal headroom (MW) | 6.84 | 7 | 7.04 | 7.03 | 6.26 | 5.23 | 4.75 | 4.38 | 4.05 | 3.65 | 3.12 | 2.54 | 1.89 | 1.25 | 0.59 | -3.44 | -5.66 | -6.33
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Consumer Transformation | Thermal headroom (MW) | -51.22 | -50.73 | -51.09 | -51.79 | -53.13 | -54.57 | -56.03 | -57.36 | -58.84 | -60.54 | -63.28 | -66.36 | -69.55 | -72.37 | -75.14 | -88.91 | -96.51 | -99.24
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Leading the Way | Thermal headroom (MW) | -51.22 | -51.29 | -52.28 | -53.7 | -55.94 | -58.38 | -60.71 | -63.01 | -65.28 | -67.78 | -70.74 | -73.84 | -76.91 | -79.91 | -82.8 | -91.36 | -93.83 | -93.71
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Steady Progression | Thermal headroom (MW) | -51.22 | -50.35 | -50.25 | -50.4 | -51 | -51.6 | -52.12 | -52.63 | -53.24 | -53.95 | -54.9 | -55.89 | -57.06 | -58.3 | -59.71 | -67.84 | -72.35 | -73.42
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | System Transformation | Thermal headroom (MW) | -51.22 | -50.49 | -50.61 | -51.03 | -52 | -52.66 | -53.48 | -54.21 | -55.02 | -55.91 | -57.08 | -58.41 | -59.87 | -61.81 | -63.87 | -72.6 | -75.29 | -74.66
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | WPD Best View | Thermal headroom (MW) | -51.22 | -50.73 | -51.09 | -51.79 | -53.13 | -54.57 | -56.03 | -57.36 | -58.84 | -60.54 | -63.28 | -66.36 | -69.55 | -72.37 | -75.14 | -88.91 | -96.51 | -99.24
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Consumer Transformation | Thermal headroom (MW) | 20.17 | 18.4182 | 16.2716 | 13.5867 | 10.2156 | 5.8466 | 1.4642 | -3.0817 | -7.9615 | -13.6495 | -22.9798 | -32.9146 | -43.2363 | -53.3744 | -63.5187 | -110.4806 | -139.1022 | -154.2853
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Leading the Way | Thermal headroom (MW) | 20.17 | 17.0384 | 13.3942 | 9.2547 | 4.2248 | -2.7055 | -9.3417 | -16.7752 | -24.8323 | -34.3738 | -44.2919 | -54.9859 | -65.706 | -76.1723 | -86.1045 | -117.5954 | -128.5859 | -133.4658
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Steady Progression | Thermal headroom (MW) | 20.17 | 19.657 | 18.8128 | 17.7876 | 16.4877 | 14.3942 | 12.3165 | 10.1071 | 7.8462 | 4.8859 | 1.2406 | -2.2787 | -6.2934 | -10.6491 | -15.0098 | -39.7423 | -53.7779 | -59.027
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | System Transformation | Thermal headroom (MW) | 20.17 | 19.1941 | 17.9019 | 16.1974 | 14.1032 | 11.8486 | 9.4831 | 6.9062 | 4.1127 | 0.43894 | -3.607 | -7.9953 | -13.0507 | -18.1862 | -23.3081 | -51.4453 | -61.0901 | -62.9648
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | WPD Best View | Thermal headroom (MW) | 20.17 | 18.4182 | 16.2716 | 13.5867 | 10.2156 | 5.8466 | 1.4642 | -3.0817 | -7.9615 | -13.6495 | -22.9798 | -32.9146 | -43.2363 | -53.3744 | -63.5187 | -110.4806 | -139.1022 | -154.2853
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Consumer Transformation | Thermal headroom (MW) | 15.89 | 15.69 | 15.41 | 15.04 | 14.49 | 13.53 | 12.61 | 11.6 | 10.48 | 9.05 | 6.76 | 4.46 | 2.12 | -0.07 | -2.19 | -12.32 | -17.91 | -20.76
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Leading the Way | Thermal headroom (MW) | 15.89 | 15.32 | 14.63 | 13.86 | 12.85 | 11.46 | 10.01 | 8.37 | 6.62 | 4.56 | 2.19 | -0.31 | -2.78 | -5.08 | -7.24 | -13.38 | -15.03 | -14.73
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Steady Progression | Thermal headroom (MW) | 15.89 | 16.11 | 16.2 | 16.29 | 16.28 | 16.1 | 15.84 | 15.51 | 15.17 | 14.68 | 14.02 | 13.29 | 12.52 | 11.66 | 10.69 | 4.13 | -0.8 | -2.62
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | System Transformation | Thermal headroom (MW) | 15.89 | 15.96 | 15.95 | 15.81 | 15.59 | 15.3 | 14.98 | 14.56 | 14.06 | 13.39 | 12.56 | 11.56 | 10.44 | 9.21 | 7.86 | 0.79 | -1.56 | -1.6
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | WPD Best View | Thermal headroom (MW) | 15.89 | 15.69 | 15.41 | 15.04 | 14.49 | 13.53 | 12.61 | 11.6 | 10.48 | 9.05 | 6.76 | 4.46 | 2.12 | -0.07 | -2.19 | -12.32 | -17.91 | -20.76
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Consumer Transformation | Thermal headroom (MW) | 2.88 | 2.63 | 2.19 | 1.63 | 0.94 | -0.08 | -1.03 | -1.99 | -3.03 | -4.19 | -6.45 | -8.77 | -11.14 | -13.48 | -15.75 | -30.37 | -39.78 | -44.67
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Leading the Way | Thermal headroom (MW) | 2.88 | 1.99 | 0.85 | -0.3 | -1.59 | -3.53 | -5.39 | -7.38 | -9.32 | -11.5 | -13.92 | -16.54 | -19.09 | -21.61 | -23.99 | -33.4 | -37.83 | -40.64
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Steady Progression | Thermal headroom (MW) | 2.88 | 2.97 | 2.92 | 2.83 | 2.7 | 2.19 | 1.69 | 1.21 | 0.71 | 0.16 | -0.68 | -1.69 | -2.84 | -4.05 | -5.26 | -11.47 | -15.81 | -18.01
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | System Transformation | Thermal headroom (MW) | 2.88 | 2.86 | 2.69 | 2.43 | 2.05 | 1.64 | 1.23 | 0.81 | 0.34 | -0.56 | -1.67 | -2.85 | -4.02 | -5.16 | -6.15 | -13.21 | -16.77 | -17.93
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | WPD Best View | Thermal headroom (MW) | 2.88 | 2.63 | 2.19 | 1.63 | 0.94 | -0.08 | -1.03 | -1.99 | -3.03 | -4.19 | -6.45 | -8.77 | -11.14 | -13.48 | -15.75 | -30.37 | -39.78 | -44.67
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Consumer Transformation | Thermal headroom (MW) | 7.85 | 6.88 | 5.81 | 4.5 | 2.9 | 1.09 | -0.8 | -2.75 | -4.8 | -7.15 | -10.79 | -14.81 | -19.06 | -23.29 | -27.63 | -44.47 | -54.76 | -60.38
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Leading the Way | Thermal headroom (MW) | 7.85 | 6.59 | 5.22 | 3.55 | 1.48 | -1.22 | -3.75 | -6.63 | -9.93 | -13.93 | -17.83 | -22.05 | -26.37 | -30.64 | -34.71 | -46.74 | -50.44 | -52.16
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Steady Progression | Thermal headroom (MW) | 7.85 | 7.25 | 6.6 | 5.85 | 4.99 | 3.95 | 2.97 | 1.92 | 0.85 | -0.58 | -2.2 | -3.54 | -5.12 | -6.85 | -8.51 | -17.62 | -21.36 | -22.35
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | System Transformation | Thermal headroom (MW) | 7.85 | 7.09 | 6.27 | 5.3 | 4.19 | 3.03 | 1.81 | 0.5 | -0.86 | -2.44 | -4.03 | -5.71 | -7.8 | -9.9 | -12.01 | -22.66 | -25.52 | -26.02
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | WPD Best View | Thermal headroom (MW) | 7.85 | 6.88 | 5.81 | 4.5 | 2.9 | 1.09 | -0.8 | -2.75 | -4.8 | -7.15 | -10.79 | -14.81 | -19.06 | -23.29 | -27.63 | -44.47 | -54.76 | -60.38
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Consumer Transformation | Thermal headroom (MW) | 13.1 | 12.79 | 12.31 | 11.8 | 11.13 | 10.12 | 9.15 | 8.24 | 7.3 | 6.27 | 4.34 | 1.51 | -1.42 | -3.9 | -6.42 | -18.22 | -28.69 | -34.76
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Leading the Way | Thermal headroom (MW) | 13.1 | 12.52 | 11.71 | 10.94 | 9.86 | 8.41 | 7 | 5.52 | 3.45 | 1.08 | -1.2 | -3.8 | -6.49 | -9.16 | -11.72 | -20.4 | -25.61 | -29.07
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Steady Progression | Thermal headroom (MW) | 13.1 | 13.24 | 13.25 | 13.26 | 13.26 | 13.04 | 12.73 | 12.35 | 11.91 | 11.39 | 10.73 | 10.05 | 9.31 | 8.55 | 7.76 | 2.35 | -2.31 | -4.52
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | System Transformation | Thermal headroom (MW) | 13.1 | 13.08 | 12.91 | 12.74 | 12.52 | 12.38 | 12.1 | 11.75 | 11.3 | 10.75 | 10.1 | 9.38 | 8.66 | 7.59 | 6.45 | 1.05 | -1.8 | -2.91
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | WPD Best View | Thermal headroom (MW) | 13.1 | 12.74 | 12.2 | 11.63 | 10.9 | 9.89 | 8.9 | 7.95 | 7 | 5.89 | 3.48 | 0.66 | -2.21 | -4.65 | -7.13 | -17.77 | -26.81 | -32.2
Ratcliffe 132kV | Nottingham | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Consumer Transformation | Thermal headroom (MW) | 12.38 | 11.94 | 11.36 | 10.76 | 10.08 | 8.93 | 7.99 | 7.12 | 6.17 | 5.18 | 2.94 | 0.72 | -1.54 | -3.7 | -5.88 | -20.45 | -29.74 | -33.59
Ratcliffe 132kV | Nottingham | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Leading the Way | Thermal headroom (MW) | 12.38 | 11.19 | 9.92 | 8.66 | 7.37 | 5.34 | 3.51 | 1.64 | -0.18 | -2.14 | -4.43 | -6.8 | -9.2 | -11.57 | -13.85 | -23.5 | -27.8 | -29.47
Ratcliffe 132kV | Nottingham | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Steady Progression | Thermal headroom (MW) | 12.38 | 12.36 | 12.24 | 12.13 | 12.01 | 11.49 | 11 | 10.53 | 10 | 9.46 | 8.72 | 8 | 7.27 | 6.48 | 5.68 | 0.07 | -3.64 | -5.94
Ratcliffe 132kV | Nottingham | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | System Transformation | Thermal headroom (MW) | 12.38 | 12.24 | 12 | 11.74 | 11.46 | 10.99 | 10.58 | 10.16 | 9.72 | 9.22 | 8.51 | 7.74 | 6.97 | 6.13 | 5.25 | -0.87 | -4.23 | -6.18
Ratcliffe 132kV | Nottingham | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | WPD Best View | Thermal headroom (MW) | 12.38 | 11.21 | 9.95 | 8.7 | 7.43 | 5.43 | 3.63 | 1.79 | 0 | -1.94 | -4.22 | -6.6 | -8.99 | -11.35 | -13.62 | -23.41 | -27.85 | -29.58
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Consumer Transformation | Thermal headroom (MW) | 5.27 | 5.14 | 4.63 | 3.91 | 2.98 | 1.25 | -0.24 | -1.39 | -2.89 | -4.56 | -6.81 | -9.14 | -11.43 | -13.57 | -15.54 | -21.69 | -23.92 | -24.86
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Leading the Way | Thermal headroom (MW) | 5.27 | 4.99 | 4.24 | 3.34 | 2.21 | 0.03 | -1.89 | -3.41 | -5.4 | -7.47 | -9.7 | -12.07 | -14.21 | -16.18 | -17.82 | -20.38 | -19.21 | -16.26
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Steady Progression | Thermal headroom (MW) | 5.27 | 5.53 | 5.55 | 5.51 | 5.44 | 4.77 | 4.15 | 3.68 | 3.05 | 2.32 | 1.47 | 0.5 | -0.59 | -1.84 | -3.21 | -11.61 | -17.44 | -18.94
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | System Transformation | Thermal headroom (MW) | 5.27 | 5.48 | 5.35 | 5.13 | 4.85 | 3.96 | 3.16 | 2.65 | 1.82 | 0.93 | -0.22 | -1.57 | -3.1 | -4.82 | -6.66 | -14.95 | -16.7 | -15.77
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | WPD Best View | Thermal headroom (MW) | 5.27 | 4.99 | 4.24 | 3.34 | 2.21 | 0.03 | -1.89 | -3.41 | -5.4 | -7.47 | -9.7 | -12.07 | -14.21 | -16.18 | -17.82 | -20.38 | -19.21 | -16.26
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Consumer Transformation | Thermal headroom (MW) | 13.16 | 12.76 | 12.07 | 11.33 | 10.56 | 8.58 | 6.48 | 4.38 | 2.34 | 0.42 | -3.78 | -8.23 | -12.68 | -17.05 | -21.35 | -44.86 | -60.43 | -67.83
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Leading the Way | Thermal headroom (MW) | 13.16 | 12.01 | 10.57 | 8.81 | 6.89 | 3.64 | 0.31 | -3.62 | -7.33 | -10.86 | -15.24 | -19.84 | -24.43 | -28.96 | -33.3 | -48.24 | -54.75 | -57.57
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Steady Progression | Thermal headroom (MW) | 13.16 | 13.33 | 13.28 | 13.25 | 13.21 | 12.5 | 11.69 | 10.77 | 9.78 | 8.74 | 7.39 | 6.05 | 4.65 | 3.2 | 1.76 | -8.52 | -17.04 | -21.52
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | System Transformation | Thermal headroom (MW) | 13.16 | 13.11 | 12.8 | 12.49 | 12.16 | 11.43 | 10.49 | 9.32 | 8.08 | 6.87 | 5.29 | 3.62 | 1.94 | 0.34 | -1.08 | -11.8 | -17.22 | -19.27
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | WPD Best View | Thermal headroom (MW) | 13.16 | 12.14 | 10.83 | 9.41 | 7.67 | 4.82 | 1.98 | -0.99 | -4.05 | -7.24 | -11.62 | -16.18 | -20.73 | -25.26 | -29.57 | -47.11 | -55.77 | -59.6
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Consumer Transformation | Thermal headroom (MW) | 3.98 | 3.49 | 3.16 | 2.72 | 2.22 | 1.34 | 0.81 | 0.26 | -0.3 | -1.01 | -1.99 | -3.04 | -4.37 | -5.63 | -6.86 | -15.54 | -20.46 | -22.79
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Leading the Way | Thermal headroom (MW) | 3.98 | 3.28 | 2.77 | 2.13 | 1.4 | -0.27 | -1.29 | -2.31 | -3.3 | -4.72 | -6.1 | -7.6 | -9.03 | -10.39 | -11.67 | -17.15 | -19.44 | -20.63
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Steady Progression | Thermal headroom (MW) | 3.98 | 3.73 | 3.66 | 3.56 | 3.47 | 2.96 | 2.66 | 2.33 | 1.99 | 1.53 | 1.01 | 0.47 | -0.09 | -0.68 | -1.26 | -4.55 | -6.77 | -7.97
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | System Transformation | Thermal headroom (MW) | 3.98 | 3.63 | 3.49 | 3.31 | 3.12 | 2.55 | 2.28 | 1.95 | 1.57 | 1.03 | 0.45 | -0.16 | -0.77 | -1.36 | -1.88 | -5.63 | -7.75 | -8.38
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | WPD Best View | Thermal headroom (MW) | 3.98 | 3.49 | 3.16 | 2.72 | 2.22 | 1.34 | 0.81 | 0.26 | -0.3 | -1.01 | -1.99 | -3.04 | -4.37 | -5.63 | -6.86 | -15.54 | -20.46 | -22.79
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Consumer Transformation | Thermal headroom (MW) | 6.96 | 7.16 | 7.26 | 7.3 | 7.33 | 7.29 | 7.09 | 7 | 6.9 | 6.75 | 6.44 | 6.15 | 5.8 | 5.46 | 5.13 | 3.6 | 2.82 | 2.67
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Leading the Way | Thermal headroom (MW) | 6.96 | 7.04 | 7.02 | 6.96 | 6.88 | 6.73 | 6.36 | 6.2 | 5.95 | 5.69 | 5.33 | 4.97 | 4.61 | 4.3 | 3.95 | 3.26 | 3.42 | 3.87
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Steady Progression | Thermal headroom (MW) | 6.96 | 7.25 | 7.41 | 7.56 | 7.7 | 7.8 | 7.78 | 7.85 | 7.86 | 7.88 | 7.86 | 7.84 | 7.77 | 7.71 | 7.65 | 6.64 | 5.95 | 6.11
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | System Transformation | Thermal headroom (MW) | 6.96 | 7.22 | 7.35 | 7.47 | 7.58 | 7.68 | 7.55 | 7.59 | 7.62 | 7.63 | 7.58 | 7.49 | 7.4 | 7.32 | 7.21 | 6.19 | 5.93 | 6.35
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | WPD Best View | Thermal headroom (MW) | 6.96 | 7.04 | 7.02 | 6.96 | 6.88 | 6.73 | 6.36 | 6.2 | 5.95 | 5.69 | 5.33 | 4.97 | 4.61 | 4.3 | 3.95 | 3.26 | 3.42 | 3.87
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Consumer Transformation | Thermal headroom (MW) | 11.78 | 11.99 | 12.02 | 11.95 | 11.78 | 11 | 10.45 | 9.96 | 8.97 | 8.02 | 5.82 | 3.54 | 1.24 | -0.86 | -2.82 | -11.75 | -16.24 | -18.82
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Leading the Way | Thermal headroom (MW) | 11.78 | 11.76 | 11.51 | 11.2 | 10.74 | 9.61 | 8.82 | 8.03 | 6 | 3.9 | 1.59 | -0.8 | -3.24 | -5.24 | -7.13 | -12.86 | -14.62 | -14.82
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Steady Progression | Thermal headroom (MW) | 11.78 | 12.2 | 12.43 | 12.61 | 12.76 | 12.52 | 12.42 | 12.31 | 11.91 | 11.58 | 11.14 | 10.69 | 10.12 | 9.67 | 9.16 | 3.4 | -0.24 | -1.54
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | System Transformation | Thermal headroom (MW) | 11.78 | 12.13 | 12.29 | 12.38 | 12.4 | 12.15 | 12.08 | 11.97 | 11.28 | 10.85 | 10.34 | 9.78 | 9.06 | 8.11 | 7.09 | 1.47 | -0.72 | -1.23
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | WPD Best View | Thermal headroom (MW) | 11.78 | 11.77 | 11.53 | 11.24 | 10.79 | 9.67 | 8.89 | 8.16 | 6.23 | 4.22 | 1.9 | -0.54 | -2.99 | -5 | -6.86 | -12.74 | -14.79 | -15.26
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Consumer Transformation | Thermal headroom (MW) | 8.16 | 7.61 | 6.79 | 5.67 | 4.09 | 1.96 | 0.26 | -1.58 | -3.26 | -4.86 | -7.16 | -9.39 | -11.61 | -13.8 | -15.89 | -24.38 | -28.49 | -30.27
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Leading the Way | Thermal headroom (MW) | 8.16 | 7.25 | 6.09 | 3.66 | 1.72 | -0.74 | -2.59 | -4.97 | -7.16 | -9.14 | -11.38 | -13.57 | -15.7 | -17.66 | -19.44 | -24.54 | -25.82 | -25.18
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Steady Progression | Thermal headroom (MW) | 8.16 | 8.09 | 7.87 | 7.6 | 7.24 | 6.47 | 5.91 | 5.19 | 4.51 | 3.88 | 3.16 | 2.41 | 1.63 | 0.76 | -0.12 | -6.13 | -10.36 | -12.26
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | System Transformation | Thermal headroom (MW) | 8.16 | 7.91 | 7.48 | 6.95 | 6.27 | 5.37 | 4.71 | 3.76 | 2.85 | 2.07 | 1.25 | 0.29 | -0.7 | -1.79 | -2.9 | -8.69 | -10.63 | -10.66
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | WPD Best View | Thermal headroom (MW) | 8.16 | 7.26 | 6.12 | 4.66 | 2.74 | 0.29 | -1.56 | -3.94 | -6.13 | -8.1 | -10.34 | -12.53 | -14.66 | -16.61 | -18.38 | -23.55 | -24.88 | -24.27
Ratcliffe 132kV | Nottingham | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Consumer Transformation | Thermal headroom (MW) | 27.26 | 27.1 | 26.67 | 26.18 | 25.51 | 24.64 | 23.87 | 22.52 | 20.84 | 18.79 | 15.86 | 12.84 | 9.83 | 6.99 | 4.38 | -4.56 | -8.3 | -10.15
Ratcliffe 132kV | Nottingham | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Leading the Way | Thermal headroom (MW) | 27.26 | 26.84 | 26.12 | 25.38 | 24.44 | 23.4 | 21.68 | 19.77 | 17.59 | 15.1 | 12.26 | 9.27 | 6.39 | 3.74 | 1.47 | -3.08 | -2.49 | 0.16
Ratcliffe 132kV | Nottingham | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Steady Progression | Thermal headroom (MW) | 27.26 | 27.56 | 27.65 | 27.74 | 27.8 | 27.66 | 27.54 | 27.44 | 27.3 | 27.01 | 26.07 | 25.01 | 23.84 | 22.5 | 21.06 | 11.75 | 5.36 | 3.83
Ratcliffe 132kV | Nottingham | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | System Transformation | Thermal headroom (MW) | 27.26 | 27.4 | 27.3 | 27.18 | 27 | 26.92 | 26.85 | 26.81 | 26.69 | 25.8 | 24.58 | 23.15 | 21.44 | 19.56 | 17.55 | 8.27 | 6.07 | 6.65
Ratcliffe 132kV | Nottingham | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | WPD Best View | Thermal headroom (MW) | 27.26 | 26.84 | 26.12 | 25.38 | 24.44 | 23.4 | 21.68 | 19.77 | 17.59 | 15.1 | 12.26 | 9.27 | 6.39 | 3.74 | 1.47 | -3.08 | -2.49 | 0.16
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Consumer Transformation | Thermal headroom (MW) | 7.78 | 7.94 | 8 | 8.01 | 7.92 | 7.82 | 7.73 | 7.44 | 7.31 | 6.51 | 5.54 | 4.47 | 3.43 | 2.46 | 1.56 | -1.04 | -1.86 | -2.27
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Leading the Way | Thermal headroom (MW) | 7.78 | 7.94 | 7.98 | 7.99 | 7.92 | 7.86 | 7.76 | 7.31 | 6.71 | 5.79 | 4.83 | 3.79 | 2.74 | 1.82 | 1.06 | 0.02 | 0.78 | 2.38
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Steady Progression | Thermal headroom (MW) | 7.78 | 8.08 | 8.26 | 8.43 | 8.57 | 8.7 | 8.8 | 8.77 | 8.82 | 8.84 | 8.78 | 8.68 | 8.16 | 7.59 | 6.9 | 2.63 | -0.55 | -1.35
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | System Transformation | Thermal headroom (MW) | 7.78 | 8.03 | 8.17 | 8.29 | 8.36 | 8.51 | 8.65 | 8.55 | 8.61 | 8.61 | 8.39 | 7.77 | 7 | 6.1 | 5.15 | 0.67 | -0.29 | 0.25
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | WPD Best View | Thermal headroom (MW) | 7.78 | 7.94 | 7.98 | 7.99 | 7.92 | 7.86 | 7.76 | 7.31 | 6.71 | 5.79 | 4.83 | 3.79 | 2.74 | 1.82 | 1.06 | 0.02 | 0.78 | 2.38
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Consumer Transformation | Thermal headroom (MW) | 4.04 | 3.56 | 2.77 | 1.82 | 0.2 | -2 | -4.4 | -6.39 | -8.49 | -10.96 | -14.4 | -18.32 | -22.93 | -27.4 | -31.98 | -53.35 | -69.67 | -79.06
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Leading the Way | Thermal headroom (MW) | 4.04 | 3.13 | 1.83 | 0.45 | -1.6 | -4.73 | -8.34 | -11.5 | -15.06 | -19.37 | -24.22 | -28.97 | -33.61 | -38.23 | -42.57 | -56.51 | -63.23 | -67.3
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Steady Progression | Thermal headroom (MW) | 4.04 | 4.23 | 4.14 | 4.03 | 3.76 | 2.91 | 1.8 | 0.64 | -0.66 | -2.54 | -4.63 | -6.33 | -8.1 | -10.02 | -11.84 | -21.72 | -26.74 | -29.53
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | System Transformation | Thermal headroom (MW) | 4.04 | 4.07 | 3.8 | 3.47 | 2.92 | 2.06 | 0.69 | -0.55 | -1.99 | -3.86 | -5.59 | -7.26 | -9.2 | -11.08 | -12.79 | -22.13 | -26.92 | -28.76
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | WPD Best View | Thermal headroom (MW) | 4.04 | 3.56 | 2.77 | 1.82 | 0.2 | -2 | -4.39 | -6.38 | -8.48 | -10.95 | -14.38 | -18.33 | -22.94 | -27.41 | -31.99 | -53.34 | -69.67 | -79.08
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Consumer Transformation | Thermal headroom (MW) | 11.63 | 10.77 | 9.74 | 8.6 | 7.16 | 4.76 | 2.68 | 0.61 | -1.55 | -3.98 | -9.75 | -15.8 | -21.93 | -27.57 | -33.23 | -54.26 | -73.84 | -85.02
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Leading the Way | Thermal headroom (MW) | 11.63 | 9.77 | 7.82 | 5.79 | 3.19 | -0.2 | -3.35 | -6.87 | -11.45 | -16.41 | -20.8 | -25.74 | -31.12 | -36.41 | -41.41 | -54.99 | -61.22 | -62.65
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Steady Progression | Thermal headroom (MW) | 11.63 | 11.65 | 11.54 | 11.37 | 11.16 | 10.35 | 9.54 | 8.73 | 7.8 | 6.09 | 3.87 | 2.56 | 1.08 | -0.71 | -2.32 | -13.55 | -21.95 | -25.88
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | System Transformation | Thermal headroom (MW) | 11.63 | 11.26 | 10.81 | 10.22 | 9.47 | 8.64 | 7.81 | 6.89 | 5.79 | 4.72 | 2.52 | 1.03 | -1.3 | -3.54 | -6.35 | -18.02 | -24.79 | -28.18
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | WPD Best View | Thermal headroom (MW) | 11.63 | 9.77 | 7.82 | 5.79 | 3.19 | -0.2 | -3.35 | -6.87 | -11.45 | -16.41 | -20.8 | -25.74 | -31.12 | -36.41 | -41.41 | -54.99 | -61.22 | -62.65
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Consumer Transformation | Thermal headroom (MW) | 15.45 | 14.2622 | 12.0353 | 9.5868 | 6.3684 | 2.0167 | -2.153 | -6.4399 | -11.2137 | -16.2947 | -23.4205 | -31.3929 | -41.0061 | -49.865 | -58.4968 | -107.5744 | -140.6693 | -157.1678
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Leading the Way | Thermal headroom (MW) | 15.45 | 12.7938 | 8.9611 | 5.0996 | 0.30732 | -6.2744 | -12.7751 | -19.6793 | -27.0717 | -34.9325 | -44.2391 | -54.1958 | -64.179 | -73.9766 | -83.2122 | -118.3458 | -135.9799 | -145.3477
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Steady Progression | Thermal headroom (MW) | 15.45 | 15.8315 | 15.4678 | 15.1382 | 14.5854 | 13.0322 | 11.3537 | 9.344 | 6.9868 | 4.4466 | 1.152 | -2.1629 | -5.7301 | -9.4738 | -13.2709 | -36.8829 | -51.2085 | -59.1551
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | System Transformation | Thermal headroom (MW) | 15.45 | 15.414 | 14.5129 | 13.5488 | 12.3203 | 10.832 | 9.0924 | 6.9161 | 4.1287 | 1.0773 | -2.6453 | -6.7198 | -10.93 | -15.8925 | -20.7263 | -43.7173 | -57.5383 | -62.621
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | WPD Best View | Thermal headroom (MW) | 15.45 | 14.2066 | 11.9169 | 9.4104 | 6.136 | 1.7151 | -2.5253 | -6.8904 | -11.7236 | -16.8569 | -23.9264 | -32.5151 | -42.1644 | -51.0848 | -59.7602 | -108.2286 | -140.6227 | -156.8482
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Consumer Transformation | Thermal headroom (MW) | 0.58 | 0.47 | 0.09 | -0.26 | -0.71 | -1.33 | -1.95 | -2.63 | -3.34 | -4.11 | -4.98 | -5.83 | -7.08 | -8.44 | -9.77 | -17.7 | -22.98 | -25.77
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Leading the Way | Thermal headroom (MW) | 0.58 | 0.3 | -0.29 | -0.81 | -1.43 | -2.34 | -3.31 | -4.38 | -5.45 | -6.6 | -7.94 | -9.52 | -11.1 | -12.66 | -14.16 | -19.8 | -22.6 | -24.27
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Steady Progression | Thermal headroom (MW) | 0.58 | 0.71 | 0.66 | 0.63 | 0.58 | 0.39 | 0.16 | -0.15 | -0.53 | -0.96 | -1.49 | -2.04 | -2.66 | -3.29 | -3.93 | -7.55 | -9.23 | -10.36
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | System Transformation | Thermal headroom (MW) | 0.58 | 0.65 | 0.51 | 0.4 | 0.25 | 0.07 | -0.18 | -0.55 | -1 | -1.55 | -2.16 | -2.81 | -3.47 | -4.1 | -4.65 | -7.58 | -9.74 | -10.5
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | WPD Best View | Thermal headroom (MW) | 0.58 | 0.47 | 0.09 | -0.26 | -0.71 | -1.33 | -1.95 | -2.63 | -3.34 | -4.11 | -4.98 | -5.83 | -7.08 | -8.44 | -9.77 | -17.7 | -22.98 | -25.77
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Consumer Transformation | Thermal headroom (MW) | 15.24 | 14.73 | 14.02 | 13.16 | 11.99 | 10.27 | 8.66 | 6.94 | 5.02 | 2.75 | -1.06 | -5.23 | -9.45 | -13.23 | -16.87 | -36.68 | -50.22 | -56.82
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Leading the Way | Thermal headroom (MW) | 15.24 | 13.89 | 12.34 | 10.68 | 8.65 | 6 | 3.41 | 0.57 | -2.53 | -6 | -10.03 | -14.18 | -18.36 | -22.39 | -26.18 | -40.57 | -47.7 | -51.05
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Steady Progression | Thermal headroom (MW) | 15.24 | 15.39 | 15.34 | 15.28 | 15.09 | 14.46 | 13.78 | 13.09 | 12.32 | 11.47 | 10.21 | 8.99 | 7.69 | 6.29 | 4.82 | -5.76 | -13.42 | -16.9
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | System Transformation | Thermal headroom (MW) | 15.24 | 15.2 | 14.95 | 14.57 | 14.1 | 13.51 | 12.96 | 12.3 | 11.48 | 10.48 | 9.06 | 7.48 | 5.77 | 3.55 | 1.22 | -10.53 | -16.27 | -18.46
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | WPD Best View | Thermal headroom (MW) | 15.24 | 14.73 | 14.02 | 13.16 | 11.99 | 10.27 | 8.66 | 6.94 | 5.02 | 2.75 | -1.06 | -5.23 | -9.45 | -13.23 | -16.87 | -36.68 | -50.22 | -56.82
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Consumer Transformation | Thermal headroom (MW) | 5.11 | 4.66 | 3.84 | 2.92 | 1.72 | 0.24 | -1.18 | -2.54 | -4.09 | -5.56 | -7.39 | -9.7 | -12.81 | -15.49 | -18.12 | -33.26 | -43.42 | -48.38
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Leading the Way | Thermal headroom (MW) | 5.11 | 4.31 | 3.09 | 1.83 | 0.21 | -2.03 | -4.18 | -6.33 | -8.69 | -11.05 | -13.92 | -16.93 | -19.95 | -22.93 | -25.73 | -36.45 | -41.95 | -44.97
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Steady Progression | Thermal headroom (MW) | 5.11 | 5.14 | 4.94 | 4.74 | 4.49 | 3.94 | 3.35 | 2.61 | 1.74 | 0.84 | -0.24 | -1.33 | -2.49 | -3.69 | -4.88 | -11.59 | -15.38 | -17.83
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | System Transformation | Thermal headroom (MW) | 5.11 | 5.01 | 4.64 | 4.27 | 3.81 | 3.25 | 2.54 | 1.72 | 0.62 | -0.43 | -1.64 | -2.96 | -4.27 | -5.87 | -7.38 | -13.57 | -17.81 | -19.36
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | WPD Best View | Thermal headroom (MW) | 5.11 | 4.61 | 3.74 | 2.77 | 1.52 | -0.02 | -1.5 | -2.93 | -4.53 | -6.05 | -7.83 | -10.66 | -13.81 | -16.53 | -19.21 | -33.83 | -43.38 | -48.11
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Consumer Transformation | Thermal headroom (MW) | 22.17 | 19.5106 | 12.2724 | 3.2971 | -6.523 | -20.3481 | -33.64 | -47.681 | -60.84 | -75.4331 | -100.1776 | -124.7802 | -150.895 | -177.0984 | -203.198 | -320.9989 | -408.4714 | -461.3607
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Leading the Way | Thermal headroom (MW) | 22.17 | 17.7547 | 7.561 | -4.9968 | -20.2005 | -42.5471 | -61.3369 | -83.4639 | -106.323 | -131.2527 | -154.8221 | -180.5524 | -207.3863 | -234.2274 | -258.5854 | -337.6137 | -376.6623 | -399.9879
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Steady Progression | Thermal headroom (MW) | 22.17 | 22.032 | 18.0856 | 13.4925 | 9.178 | 2.01 | -4.3299 | -12.0783 | -19.5835 | -29.4583 | -41.3123 | -50.8422 | -60.8463 | -72.0049 | -82.3757 | -144.6435 | -181.0296 | -198.373
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | System Transformation | Thermal headroom (MW) | 22.17 | 21.2049 | 15.9672 | 9.7495 | 3.566 | -5.0357 | -13.5343 | -22.9538 | -31.6281 | -41.5328 | -54.4551 | -67.086 | -80.9188 | -94.7675 | -108.3356 | -176.3951 | -208.9653 | -218.8428
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | WPD Best View | Thermal headroom (MW) | 22.17 | 19.5106 | 12.2724 | 3.2971 | -6.523 | -20.3217 | -33.5806 | -47.5821 | -60.6981 | -75.245 | -99.9665 | -124.5459 | -150.6343 | -176.8146 | -202.8844 | -319.56 | -406.6992 | -459.2421
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Consumer Transformation | Thermal headroom (MW) | 7.42 | 7.19 | 6.62 | 5.91 | 4.99 | 3.84 | 2.82 | 1.64 | 0.77 | -0.32 | -1.54 | -2.66 | -3.99 | -5.65 | -7.22 | -16.62 | -21.47 | -23.7
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Leading the Way | Thermal headroom (MW) | 7.42 | 7.02 | 6.25 | 5.35 | 4.25 | 2.7 | 1.35 | -0.69 | -2.01 | -3.79 | -5.84 | -7.7 | -9.46 | -11.17 | -12.7 | -18.48 | -20.42 | -21.43
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Steady Progression | Thermal headroom (MW) | 7.42 | 7.46 | 7.27 | 7.08 | 6.86 | 6.35 | 5.87 | 5.21 | 4.67 | 4 | 3.19 | 2.47 | 1.71 | 0.93 | 0.16 | -3.63 | -5.41 | -6.41
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | System Transformation | Thermal headroom (MW) | 7.42 | 7.38 | 7.08 | 6.75 | 6.37 | 5.79 | 5.21 | 4.31 | 3.68 | 2.79 | 1.82 | 1.01 | 0.22 | -0.54 | -1.2 | -5.27 | -7.34 | -7.73
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | WPD Best View | Thermal headroom (MW) | 7.42 | 7.19 | 6.62 | 5.91 | 4.99 | 3.84 | 2.82 | 1.64 | 0.77 | -0.32 | -1.54 | -2.66 | -3.99 | -5.65 | -7.22 | -16.62 | -21.47 | -23.7
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Consumer Transformation | Thermal headroom (MW) | 9.67 | 9.63 | 9.41 | 9.14 | 8.79 | 8.47 | 8.19 | 7.87 | 7.54 | 7.13 | 6.29 | 5.51 | 4.59 | 3.66 | 2.72 | -3.3 | -9.44 | -13.5
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Leading the Way | Thermal headroom (MW) | 9.67 | 9.52 | 9.19 | 8.82 | 8.32 | 7.73 | 7.15 | 6.36 | 5.13 | 3.68 | 2.99 | 2.08 | 0.78 | -0.62 | -1.98 | -6.51 | -9.84 | -12.68
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Steady Progression | Thermal headroom (MW) | 9.67 | 9.79 | 9.78 | 9.77 | 9.75 | 9.65 | 9.53 | 9.39 | 9.22 | 9 | 8.73 | 8.46 | 8.16 | 7.85 | 7.55 | 6.14 | 6.05 | 5.87
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | System Transformation | Thermal headroom (MW) | 9.67 | 9.76 | 9.7 | 9.63 | 9.54 | 9.45 | 9.34 | 9.19 | 9.01 | 8.72 | 8.42 | 8.1 | 7.78 | 7.48 | 7.22 | 6.36 | 5.79 | 5.54
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | WPD Best View | Thermal headroom (MW) | 9.67 | 9.63 | 9.41 | 9.14 | 8.79 | 8.47 | 8.19 | 7.87 | 7.54 | 7.13 | 6.29 | 5.51 | 4.59 | 3.66 | 2.72 | -3.3 | -9.44 | -13.5
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Consumer Transformation | Thermal headroom (MW) | 3.65 | 3.44 | 2.99 | 2.46 | 1.74 | 0.94 | 0.02 | -0.98 | -2.05 | -3.12 | -4.29 | -5.38 | -6.58 | -7.85 | -9.06 | -16.17 | -19.79 | -21.6
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Leading the Way | Thermal headroom (MW) | 3.65 | 3.31 | 2.73 | 2.08 | 1.24 | 0.22 | -0.96 | -2.36 | -3.81 | -5.32 | -6.7 | -8.4 | -10.17 | -11.88 | -13.05 | -17.55 | -19.41 | -20.62
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Steady Progression | Thermal headroom (MW) | 3.65 | 3.64 | 3.49 | 3.34 | 3.13 | 2.79 | 2.39 | 1.95 | 1.45 | 0.94 | 0.33 | -0.33 | -1.06 | -1.86 | -2.56 | -5.58 | -7.43 | -8.68
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | System Transformation | Thermal headroom (MW) | 3.65 | 3.58 | 3.36 | 3.12 | 2.79 | 2.44 | 1.97 | 1.43 | 0.79 | 0.09 | -0.69 | -1.52 | -2.34 | -3.16 | -3.72 | -6.54 | -7.81 | -8.34
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | WPD Best View | Thermal headroom (MW) | 3.65 | 3.44 | 2.99 | 2.46 | 1.74 | 0.94 | 0.02 | -0.98 | -2.05 | -3.12 | -4.29 | -5.38 | -6.58 | -7.85 | -9.06 | -16.17 | -19.79 | -21.6
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Consumer Transformation | Thermal headroom (MW) | 7.18 | 6.1 | 5.59 | 3.55 | 1.87 | -0.54 | -3.37 | -6.13 | -7.86 | -9.54 | -12.64 | -16.08 | -20.13 | -24.1 | -28.04 | -44.11 | -57.92 | -66.67
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Leading the Way | Thermal headroom (MW) | 7.18 | 5.73 | 4.92 | 2.33 | 0.15 | -3.2 | -6.81 | -10.7 | -13.91 | -17.28 | -20.61 | -24.35 | -28.22 | -31.9 | -35.3 | -45.1 | -50.92 | -54.73
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Steady Progression | Thermal headroom (MW) | 7.18 | 6.54 | 6.38 | 5.28 | 4.68 | 3.56 | 2.33 | 1.1 | 0.15 | -1.11 | -2.62 | -3.79 | -4.97 | -6.29 | -7.51 | -13.95 | -17.75 | -19.99
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | System Transformation | Thermal headroom (MW) | 7.18 | 6.35 | 6.06 | 4.64 | 3.76 | 2.44 | 0.77 | -0.95 | -2.13 | -3.34 | -4.65 | -6.05 | -7.83 | -9.58 | -11.16 | -17.85 | -21.56 | -22.93
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | WPD Best View | Thermal headroom (MW) | 7.18 | 6.1 | 5.59 | 3.55 | 1.87 | -0.54 | -3.37 | -6.13 | -7.86 | -9.54 | -12.64 | -16.08 | -20.13 | -24.1 | -28.04 | -44.11 | -57.92 | -66.67
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Consumer Transformation | Thermal headroom (MW) | 3.32 | 3.34 | 3.33 | 3.29 | 3.22 | 3.04 | 2.84 | 2.62 | 2.4 | 2.14 | 1.94 | 1.68 | 1.32 | 0.96 | 0.59 | -1.87 | -3.04 | -3.82
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Leading the Way | Thermal headroom (MW) | 3.32 | 3.31 | 3.27 | 3.2 | 3.08 | 2.78 | 2.45 | 2.02 | 1.44 | 0.81 | 0.5 | 0.04 | -0.48 | -1.01 | -1.52 | -3.64 | -4.96 | -5.86
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Steady Progression | Thermal headroom (MW) | 3.32 | 3.36 | 3.36 | 3.36 | 3.34 | 3.27 | 3.19 | 3.1 | 3 | 2.82 | 2.59 | 2.44 | 2.29 | 2.09 | 1.9 | 0.69 | -0.16 | -0.41
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | System Transformation | Thermal headroom (MW) | 3.32 | 3.32 | 3.31 | 3.27 | 3.2 | 3.1 | 2.98 | 2.83 | 2.65 | 2.47 | 2.16 | 2 | 1.7 | 1.51 | 1.25 | -0.34 | -1.78 | -2.49
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | WPD Best View | Thermal headroom (MW) | 3.32 | 3.34 | 3.33 | 3.29 | 3.22 | 3.05 | 2.86 | 2.65 | 2.44 | 2.2 | 2 | 1.75 | 1.4 | 1.05 | 0.69 | -1.42 | -2.49 | -3.16
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Consumer Transformation | Thermal headroom (MW) | 17.2 | 16.8 | 15.53 | 14.16 | 12.71 | 10.6 | 8.68 | 6.65 | 4.69 | 2.49 | -1.71 | -5.82 | -9.93 | -14.02 | -18.1 | -34.52 | -47.47 | -55.36
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Leading the Way | Thermal headroom (MW) | 17.2 | 16.58 | 14.83 | 12.85 | 10.42 | 6.84 | 4.14 | 1.02 | -2.18 | -5.62 | -9.28 | -13.08 | -16.95 | -20.83 | -24.36 | -35.07 | -40.08 | -42.75
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Steady Progression | Thermal headroom (MW) | 17.2 | 17.13 | 16.31 | 15.48 | 14.69 | 13.49 | 12.52 | 11.3 | 10.11 | 8.54 | 6.67 | 5.22 | 3.7 | 2.01 | 0.45 | -9.43 | -15.39 | -18.13
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | System Transformation | Thermal headroom (MW) | 17.2 | 17.04 | 16.02 | 14.97 | 13.92 | 12.44 | 11.1 | 9.66 | 8.36 | 6.88 | 4.87 | 2.84 | 0.68 | -1.59 | -3.86 | -14.85 | -19.4 | -20.6
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | WPD Best View | Thermal headroom (MW) | 17.2 | 16.8 | 15.53 | 14.16 | 12.71 | 10.6 | 8.68 | 6.65 | 4.69 | 2.49 | -1.71 | -5.82 | -9.93 | -14.02 | -18.1 | -34.52 | -47.47 | -55.36
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Consumer Transformation | Thermal headroom (MW) | 5.19 | 5.23 | 5.17 | 5.05 | 4.85 | 4.55 | 4.24 | 3.9 | 3.54 | 3.15 | 2.77 | 2.31 | 1.45 | 0.63 | -0.16 | -4.54 | -6.62 | -7.68
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Leading the Way | Thermal headroom (MW) | 5.19 | 5.18 | 5.06 | 4.89 | 4.6 | 4.15 | 3.68 | 3.17 | 2.59 | 1.95 | 1.39 | 0.65 | -0.13 | -0.93 | -1.64 | -4.84 | -5.97 | -6.42
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Steady Progression | Thermal headroom (MW) | 5.19 | 5.31 | 5.34 | 5.35 | 5.33 | 5.17 | 5 | 4.81 | 4.59 | 4.34 | 4.04 | 3.73 | 3.39 | 3.02 | 2.65 | -0.07 | -1.93 | -2.88
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | System Transformation | Thermal headroom (MW) | 5.19 | 5.29 | 5.3 | 5.28 | 5.2 | 5.1 | 4.97 | 4.8 | 4.61 | 4.36 | 4.05 | 3.72 | 3.39 | 3.07 | 2.77 | -0.43 | -2.43 | -2.84
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | WPD Best View | Thermal headroom (MW) | 5.19 | 5.23 | 5.17 | 5.05 | 4.85 | 4.55 | 4.24 | 3.9 | 3.54 | 3.15 | 2.77 | 2.31 | 1.45 | 0.63 | -0.16 | -4.54 | -6.62 | -7.68
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Consumer Transformation | Thermal headroom (MW) | 8.52 | 8.56 | 8.58 | 8.6 | 8.61 | 8.47 | 8.35 | 8.18 | 8.01 | 7.81 | 7.52 | 7.24 | 6.94 | 6.68 | 6.45 | 5.63 | 5.32 | 5.19
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Leading the Way | Thermal headroom (MW) | 8.52 | 8.54 | 8.53 | 8.52 | 8.49 | 8.27 | 8.07 | 7.8 | 7.54 | 7.27 | 7.06 | 6.84 | 6.62 | 6.4 | 6.24 | 5.6 | 5.48 | 5.46
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Steady Progression | Thermal headroom (MW) | 8.52 | 8.54 | 8.53 | 8.53 | 8.51 | 8.43 | 8.34 | 8.26 | 8.18 | 8.1 | 7.95 | 7.81 | 7.67 | 7.49 | 7.31 | 5.78 | 5.05 | 4.98
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | System Transformation | Thermal headroom (MW) | 8.52 | 8.55 | 8.55 | 8.54 | 8.53 | 8.53 | 8.53 | 8.53 | 8.51 | 8.49 | 8.36 | 8.24 | 8.06 | 7.86 | 7.68 | 6.26 | 5.21 | 5.07
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | WPD Best View | Thermal headroom (MW) | 8.52 | 8.56 | 8.58 | 8.6 | 8.61 | 8.47 | 8.35 | 8.18 | 8.01 | 7.81 | 7.52 | 7.24 | 6.94 | 6.68 | 6.45 | 5.63 | 5.32 | 5.19
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Consumer Transformation | Thermal headroom (MW) | -18.635 | -18.625 | -18.675 | -18.835 | -19.025 | -19.545 | -20.035 | -20.565 | -21.185 | -21.965 | -24.615 | -27.245 | -29.935 | -32.525 | -35.255 | -41.895 | -55.795 | -67.135
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Leading the Way | Thermal headroom (MW) | -18.635 | -18.735 | -18.895 | -19.125 | -19.715 | -20.735 | -21.795 | -23.335 | -27.245 | -31.555 | -32.785 | -35.195 | -38.435 | -41.865 | -45.095 | -53.215 | -62.405 | -71.645
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Steady Progression | Thermal headroom (MW) | -18.635 | -18.485 | -18.405 | -18.385 | -18.375 | -18.435 | -18.475 | -18.505 | -18.585 | -18.965 | -19.385 | -19.625 | -19.855 | -20.265 | -20.605 | -23.765 | -25.505 | -25.295
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | System Transformation | Thermal headroom (MW) | -18.635 | -18.555 | -18.555 | -18.595 | -18.665 | -18.665 | -18.765 | -18.995 | -19.255 | -19.485 | -20.085 | -20.515 | -21.225 | -21.815 | -22.575 | -26.535 | -28.845 | -28.845
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | WPD Best View | Thermal headroom (MW) | -18.635 | -18.595 | -18.625 | -18.775 | -18.935 | -19.325 | -19.675 | -20.035 | -20.495 | -21.175 | -23.585 | -25.935 | -28.305 | -30.755 | -33.375 | -40.725 | -55.775 | -67.305
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Consumer Transformation | Thermal headroom (MW) | 107.1588 | 107.256 | 107.4306 | 107.7261 | 108.123 | 108.8364 | 109.6147 | 110.4196 | 111.3543 | 112.4522 | 114.7951 | 117.3116 | 119.7867 | 122.0037 | 124.2355 | 132.2038 | 138.0818 | 141.7584
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Leading the Way | Thermal headroom (MW) | 107.1588 | 107.3565 | 107.6513 | 108.1002 | 108.7114 | 109.9547 | 111.1971 | 112.6389 | 114.4665 | 116.4749 | 118.5059 | 120.8584 | 123.1944 | 125.2495 | 127.1628 | 133.0356 | 135.6833 | 137.0867
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Steady Progression | Thermal headroom (MW) | 107.1588 | 107.1646 | 107.2403 | 107.3968 | 107.5591 | 107.9219 | 108.2795 | 108.6997 | 109.1774 | 109.9379 | 111.0482 | 111.9031 | 112.8768 | 113.8211 | 114.6913 | 120.7323 | 123.5958 | 124.6415
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | System Transformation | Thermal headroom (MW) | 107.1588 | 107.2123 | 107.3318 | 107.5613 | 107.8247 | 108.0722 | 108.3672 | 108.7533 | 109.2288 | 109.7381 | 110.8018 | 111.873 | 113.237 | 114.4769 | 115.8551 | 122.6698 | 126.3404 | 127.4035
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | WPD Best View | Thermal headroom (MW) | 107.1588 | 107.2511 | 107.4179 | 107.7044 | 108.0866 | 108.7872 | 109.5521 | 110.3361 | 111.2503 | 112.3188 | 114.6251 | 117.1041 | 119.5351 | 121.7286 | 123.9391 | 131.8795 | 137.8016 | 141.4762
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Consumer Transformation | Thermal headroom (MW) | 19.29 | 19.29 | 19.26 | 19.2 | 19.07 | 18.83 | 18.6 | 18.36 | 18.13 | 17.72 | 16.2 | 14.65 | 13.13 | 11.57 | 9.95 | 5.85 | 0.62 | -3.14
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Leading the Way | Thermal headroom (MW) | 19.29 | 19.26 | 19.19 | 19.12 | 18.88 | 18.52 | 18.08 | 17.43 | 16.33 | 15.15 | 14.22 | 13.1 | 11.81 | 10.47 | 9.2 | 6.26 | 4.02 | 2.46
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Steady Progression | Thermal headroom (MW) | 19.29 | 19.32 | 19.32 | 19.32 | 19.3 | 19.19 | 19.08 | 18.97 | 18.83 | 18.32 | 17.65 | 17.43 | 17.14 | 16.73 | 16.44 | 13.58 | 11.93 | 11.21
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | System Transformation | Thermal headroom (MW) | 19.29 | 19.29 | 19.28 | 19.24 | 19.16 | 19.09 | 19.02 | 18.91 | 18.76 | 18.63 | 18.27 | 18.04 | 17.32 | 16.72 | 15.86 | 12.04 | 9.57 | 8.58
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | WPD Best View | Thermal headroom (MW) | 19.29 | 19.29 | 19.26 | 19.2 | 19.07 | 18.83 | 18.6 | 18.36 | 18.13 | 17.72 | 16.2 | 14.65 | 13.13 | 11.57 | 9.95 | 5.85 | 0.62 | -3.14
Staythorpe 132kV | Checkerhouse | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Consumer Transformation | Thermal headroom (MW) | 4.95 | 5.02 | 5.02 | 5.02 | 4.96 | 4.5 | 4.07 | 3.67 | 3.23 | 2.77 | 2.14 | 1.13 | 0.15 | -0.44 | -1.06 | -3.46 | -4.64 | -5
Staythorpe 132kV | Checkerhouse | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Leading the Way | Thermal headroom (MW) | 4.95 | 4.97 | 4.93 | 4.88 | 4.73 | 4.01 | 3.28 | 2.48 | 1.42 | 0.32 | -0.13 | -0.76 | -1.51 | -2.28 | -2.97 | -5.77 | -7.59 | -8.75
Staythorpe 132kV | Checkerhouse | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Steady Progression | Thermal headroom (MW) | 4.95 | 5.01 | 5 | 4.98 | 4.96 | 4.7 | 4.45 | 4.2 | 3.9 | 3.44 | 2.78 | 2.36 | 1.93 | 1.46 | 1.03 | -2.57 | -4.01 | -4.64
Staythorpe 132kV | Checkerhouse | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | System Transformation | Thermal headroom (MW) | 4.95 | 4.96 | 4.93 | 4.88 | 4.79 | 4.73 | 4.62 | 4.48 | 4.28 | 4.1 | 3.47 | 3.13 | 2.52 | 1.73 | 0.72 | -3.49 | -7.11 | -8.26
Staythorpe 132kV | Checkerhouse | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | WPD Best View | Thermal headroom (MW) | 4.95 | 5.02 | 5.02 | 5.02 | 4.96 | 4.5 | 4.07 | 3.67 | 3.23 | 2.77 | 2.14 | 1.13 | 0.15 | -0.44 | -1.06 | -3.46 | -4.64 | -5
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Consumer Transformation | Thermal headroom (MW) | 6.26 | 6.3 | 6.31 | 6.32 | 6.32 | 6.14 | 5.97 | 5.81 | 5.55 | 5.24 | 4.17 | 3.04 | 1.82 | 1.09 | 0.34 | -3.2 | -4.85 | -6.15
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Leading the Way | Thermal headroom (MW) | 6.26 | 6.27 | 6.24 | 6.22 | 6.18 | 5.82 | 5.48 | 5.15 | 4.67 | 4.15 | 2.71 | 1.19 | -0.4 | -1.18 | -1.95 | -5.23 | -6.59 | -7.92
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Steady Progression | Thermal headroom (MW) | 6.26 | 6.29 | 6.3 | 6.3 | 6.3 | 6.23 | 6.16 | 6.09 | 6 | 5.91 | 5.44 | 4.89 | 4.02 | 3.63 | 3.25 | 1.14 | 0.88 | 0.96
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | System Transformation | Thermal headroom (MW) | 6.26 | 6.3 | 6.3 | 6.31 | 6.31 | 6.29 | 6.28 | 6.23 | 6.1 | 6.03 | 5.29 | 4.44 | 3.51 | 3.08 | 2.65 | 0.5 | -0.6 | -1.29
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | WPD Best View | Thermal headroom (MW) | 6.26 | 6.3 | 6.31 | 6.32 | 6.32 | 6.14 | 5.97 | 5.81 | 5.55 | 5.24 | 4.17 | 3.04 | 1.82 | 1.09 | 0.34 | -3.2 | -4.85 | -6.15
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Consumer Transformation | Thermal headroom (MW) | 2.98 | 2.86 | 2.6 | 1.41 | 0.8 | 0.04 | -0.87 | -1.87 | -2.98 | -4.23 | -7.03 | -9.86 | -12.74 | -15.57 | -18.43 | -29.82 | -39.72 | -45.67
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Leading the Way | Thermal headroom (MW) | 2.98 | 2.69 | 2.24 | 0.43 | -0.73 | -2.36 | -3.79 | -5.43 | -7.34 | -9.47 | -11.77 | -14.3 | -16.93 | -19.54 | -21.99 | -29.23 | -33.14 | -35.06
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Steady Progression | Thermal headroom (MW) | 2.98 | 3.06 | 3.02 | 2.23 | 2.07 | 1.77 | 1.43 | 1.06 | 0.66 | -0.07 | -1.15 | -1.92 | -2.61 | -3.47 | -4.25 | -9.98 | -13.91 | -15.72
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | System Transformation | Thermal headroom (MW) | 2.98 | 3 | 2.91 | 1.92 | 1.64 | 1.34 | 1.01 | 0.59 | 0.11 | -0.47 | -1.2 | -1.98 | -3.24 | -4.61 | -6.04 | -12.91 | -16.2 | -17.4
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | WPD Best View | Thermal headroom (MW) | 2.98 | 2.86 | 2.6 | 1.41 | 0.8 | 0.04 | -0.87 | -1.87 | -2.98 | -4.23 | -7.03 | -9.86 | -12.74 | -15.57 | -18.43 | -29.82 | -39.72 | -45.67
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Consumer Transformation | Thermal headroom (MW) | 18.48 | 17.87 | 17.68 | 17.45 | 17.03 | 16.39 | 15.76 | 15.1 | 14.32 | 13.48 | 12.34 | 11.23 | 10.04 | 8.94 | 7.91 | 3.38 | 1.67 | 0.94
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Leading the Way | Thermal headroom (MW) | 18.48 | 17.75 | 17.45 | 17.14 | 16.7 | 15.81 | 14.92 | 13.93 | 12.92 | 11.7 | 10.75 | 9.66 | 8.58 | 7.55 | 6.66 | 3.34 | 2.61 | 2.85
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Steady Progression | Thermal headroom (MW) | 18.48 | 17.96 | 17.85 | 17.69 | 17.45 | 17.08 | 16.73 | 16.39 | 15.99 | 15.6 | 15.04 | 14.53 | 13.97 | 13.29 | 12.63 | 8.21 | 5.83 | 4.9
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | System Transformation | Thermal headroom (MW) | 18.48 | 17.91 | 17.79 | 17.63 | 17.37 | 17.15 | 16.89 | 16.58 | 16.21 | 15.83 | 15.24 | 14.58 | 13.91 | 13.1 | 12.34 | 7.44 | 5.22 | 5.06
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | WPD Best View | Thermal headroom (MW) | 18.48 | 17.9 | 17.75 | 17.58 | 17.25 | 16.68 | 16.12 | 15.59 | 14.92 | 14.25 | 13.33 | 12.44 | 11.51 | 10.55 | 9.65 | 5.24 | 3.26 | 2.52
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Consumer Transformation | Thermal headroom (MW) | 3.35 | 3.37 | 3.33 | 3.28 | 3.09 | 2.91 | 2.79 | 2.66 | 2.52 | 2.38 | 2.15 | 1.8 | 1.38 | 1.01 | 0.65 | -1.67 | -3 | -3.62
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Leading the Way | Thermal headroom (MW) | 3.35 | 3.34 | 3.25 | 3.16 | 2.93 | 2.62 | 2.36 | 2.09 | 1.82 | 1.55 | 1.17 | 0.73 | 0.3 | -0.12 | -0.47 | -1.88 | -2.47 | -2.72
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Steady Progression | Thermal headroom (MW) | 3.35 | 3.41 | 3.43 | 3.44 | 3.4 | 3.33 | 3.28 | 3.22 | 3.15 | 3.08 | 2.95 | 2.82 | 2.68 | 2.54 | 2.4 | 1.58 | 0.94 | 0.65
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | System Transformation | Thermal headroom (MW) | 3.35 | 3.4 | 3.4 | 3.4 | 3.32 | 3.25 | 3.21 | 3.14 | 3.06 | 2.95 | 2.79 | 2.63 | 2.47 | 2.31 | 2.17 | 1.28 | 0.67 | 0.48
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | WPD Best View | Thermal headroom (MW) | 3.35 | 3.37 | 3.33 | 3.28 | 3.09 | 2.91 | 2.79 | 2.66 | 2.52 | 2.38 | 2.15 | 1.8 | 1.38 | 1.01 | 0.65 | -1.67 | -3 | -3.62
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Consumer Transformation | Thermal headroom (MW) | 2.29 | 2.22 | 2.1 | 1.97 | 1.77 | 1.31 | 0.59 | -0.22 | -1.1 | -2.24 | -4.61 | -6.99 | -9.4 | -11.65 | -13.93 | -19.71 | -25.09 | -28.63
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Leading the Way | Thermal headroom (MW) | 2.29 | 2.2 | 2.04 | 1.88 | 1.57 | 0.71 | -0.23 | -1.41 | -2.97 | -4.71 | -6.38 | -8.3 | -10.29 | -12.18 | -13.93 | -17.56 | -18.9 | -18.78
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Steady Progression | Thermal headroom (MW) | 2.29 | 2.3 | 2.26 | 2.23 | 2.17 | 2.01 | 1.86 | 1.46 | 1.07 | 0.27 | -0.64 | -1.28 | -2 | -2.81 | -3.59 | -9.13 | -12.39 | -13.4
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | System Transformation | Thermal headroom (MW) | 2.29 | 2.27 | 2.2 | 2.13 | 2.01 | 1.93 | 1.77 | 1.41 | 1 | 0.49 | -0.2 | -1.02 | -2.28 | -3.64 | -5.08 | -11.55 | -14.07 | -14.26
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | WPD Best View | Thermal headroom (MW) | 2.29 | 2.22 | 2.1 | 1.97 | 1.77 | 1.31 | 0.59 | -0.22 | -1.1 | -2.24 | -4.61 | -6.99 | -9.4 | -11.65 | -13.93 | -19.71 | -25.09 | -28.63
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Consumer Transformation | Thermal headroom (MW) | 14.74 | 14.62 | 14.38 | 14.16 | 13.85 | 13.38 | 12.85 | 12.28 | 11.42 | 10.49 | 7.86 | 5.25 | 2.63 | 0.05 | -2.56 | -11.58 | -20.82 | -26.83
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Leading the Way | Thermal headroom (MW) | 14.74 | 14.47 | 14.06 | 13.69 | 13.1 | 12.12 | 10.93 | 9.6 | 7.87 | 5.96 | 4.02 | 1.84 | -0.53 | -2.86 | -5.02 | -10.58 | -13.35 | -14.81
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Steady Progression | Thermal headroom (MW) | 14.74 | 14.79 | 14.76 | 14.75 | 14.72 | 14.58 | 14.41 | 14.22 | 14 | 13.39 | 12.57 | 12.19 | 11.74 | 11.02 | 10.43 | 5.47 | 1.88 | 0.23
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | System Transformation | Thermal headroom (MW) | 14.74 | 14.75 | 14.65 | 14.57 | 14.45 | 14.29 | 14.09 | 13.84 | 13.55 | 13.2 | 12.37 | 11.45 | 10.35 | 9.19 | 8.02 | 2.03 | -0.63 | -1.32
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | WPD Best View | Thermal headroom (MW) | 14.74 | 14.62 | 14.38 | 14.16 | 13.85 | 13.38 | 12.85 | 12.28 | 11.42 | 10.49 | 7.86 | 5.25 | 2.63 | 0.05 | -2.56 | -11.58 | -20.82 | -26.83
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Consumer Transformation | Thermal headroom (MW) | 0.42 | 0.54 | -0.04 | -0.6 | -1.59 | -2.81 | -4.24 | -5.65 | -7.19 | -8.76 | -10.6 | -12.24 | -13.55 | -14.82 | -16.05 | -20.48 | -21.33 | -21.32
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Leading the Way | Thermal headroom (MW) | 0.42 | 0.5 | -0.19 | -0.92 | -2.25 | -4.44 | -6.38 | -8.48 | -10.94 | -13.45 | -15.3 | -17.06 | -18.28 | -19.47 | -20.58 | -24.44 | -25.47 | -26.1
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Steady Progression | Thermal headroom (MW) | 0.42 | 0.56 | 0.07 | -0.37 | -1.14 | -2.11 | -3.08 | -4.13 | -5.29 | -6.6 | -8.16 | -9.46 | -10.56 | -11.65 | -12.67 | -18.48 | -19.38 | -19.21
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | System Transformation | Thermal headroom (MW) | 0.42 | 0.48 | -0.12 | -0.71 | -1.71 | -2.64 | -3.67 | -4.74 | -5.9 | -7.1 | -8.86 | -10.1 | -11.33 | -12.31 | -13.52 | -19.21 | -22.41 | -23.12
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | WPD Best View | Thermal headroom (MW) | 0.42 | 0.54 | -0.04 | -0.6 | -1.59 | -2.8 | -4.23 | -5.63 | -7.17 | -8.73 | -10.57 | -12.21 | -13.51 | -14.78 | -16.01 | -20.37 | -21.2 | -21.17
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Consumer Transformation | Thermal headroom (MW) | -2.83 | -2.78 | -2.76 | -2.77 | -2.82 | -3.04 | -3.27 | -3.49 | -3.71 | -4.03 | -4.55 | -5.54 | -6.21 | -6.88 | -7.55 | -10.24 | -11.14 | -11.58
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Leading the Way | Thermal headroom (MW) | -2.83 | -2.81 | -2.82 | -2.86 | -2.94 | -3.25 | -3.61 | -4.06 | -4.61 | -5.3 | -5.78 | -6.81 | -7.41 | -7.96 | -8.51 | -10.76 | -11.31 | -11.47
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Steady Progression | Thermal headroom (MW) | -2.83 | -2.76 | -2.74 | -2.72 | -2.71 | -2.83 | -2.95 | -3.12 | -3.31 | -3.51 | -3.82 | -4.27 | -4.71 | -5.15 | -5.6 | -8.25 | -8.93 | -9.15
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | System Transformation | Thermal headroom (MW) | -2.83 | -2.77 | -2.76 | -2.76 | -2.78 | -2.82 | -2.87 | -2.94 | -3.02 | -3.16 | -3.41 | -3.89 | -4.2 | -4.49 | -4.86 | -7.31 | -8.88 | -9.27
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | WPD Best View | Thermal headroom (MW) | -2.83 | -2.78 | -2.76 | -2.77 | -2.82 | -3.04 | -3.27 | -3.49 | -3.71 | -4.03 | -4.55 | -5.54 | -6.21 | -6.88 | -7.55 | -10.24 | -11.14 | -11.58
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Consumer Transformation | Thermal headroom (MW) | 27.73 | 27.71 | 27.57 | 27.31 | 26.9 | 26.35 | 25.77 | 25.13 | 24.46 | 23.77 | 22.99 | 22.31 | 21.53 | 20.8 | 19.87 | 14.3 | 11.24 | 9.53
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Leading the Way | Thermal headroom (MW) | 27.73 | 27.6 | 27.35 | 26.98 | 26.44 | 25.7 | 24.92 | 23.94 | 22.96 | 21.95 | 21.03 | 20.02 | 18.81 | 17.82 | 16.93 | 13.16 | 11.56 | 10.36
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Steady Progression | Thermal headroom (MW) | 27.73 | 27.84 | 27.86 | 27.84 | 27.77 | 27.56 | 27.33 | 27.06 | 26.77 | 26.45 | 26.02 | 25.57 | 25.08 | 24.6 | 24.13 | 21.78 | 20.87 | 19.94
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | System Transformation | Thermal headroom (MW) | 27.73 | 27.8 | 27.77 | 27.69 | 27.52 | 27.32 | 27.06 | 26.75 | 26.38 | 25.94 | 25.4 | 24.83 | 24.26 | 23.77 | 23.35 | 21 | 19.54 | 19.08
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | WPD Best View | Thermal headroom (MW) | 27.73 | 27.71 | 27.57 | 27.31 | 26.9 | 26.35 | 25.77 | 25.13 | 24.46 | 23.77 | 22.99 | 22.31 | 21.53 | 20.8 | 19.87 | 14.3 | 11.24 | 9.53
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Consumer Transformation | Thermal headroom (MW) | -20.89 | -20.85 | -21.03 | -21.32 | -22.54 | -24.54 | -27.18 | -31.2 | -34.71 | -37.83 | -41.83 | -45.84 | -49.92 | -53.56 | -57.15 | -74.27 | -83.3 | -88.09
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Leading the Way | Thermal headroom (MW) | -20.89 | -21.17 | -21.68 | -22.26 | -24.09 | -27.47 | -32.25 | -38.56 | -43.39 | -47.49 | -51.6 | -55.33 | -58.96 | -62.47 | -65.85 | -76.46 | -80.58 | -82.51
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Steady Progression | Thermal headroom (MW) | -20.89 | -20.55 | -20.42 | -20.31 | -20.88 | -21.88 | -23.07 | -24.72 | -26.16 | -27.88 | -29.89 | -31.75 | -33.66 | -35.51 | -37.47 | -49.22 | -55.06 | -56.96
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | System Transformation | Thermal headroom (MW) | -20.89 | -20.68 | -20.7 | -20.76 | -21.67 | -22.87 | -24.77 | -27.4 | -30.11 | -32.27 | -34.51 | -36.49 | -38.57 | -41.12 | -43.75 | -55.81 | -60.38 | -61.19
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | WPD Best View | Thermal headroom (MW) | -20.89 | -20.85 | -21.03 | -21.32 | -22.54 | -24.54 | -27.18 | -31.2 | -34.71 | -37.83 | -41.83 | -45.84 | -49.92 | -53.56 | -57.15 | -74.27 | -83.3 | -88.09
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Consumer Transformation | Thermal headroom (MW) | 60.9696 | 59.9559 | 58.4652 | 56.7813 | 54.5264 | 50.7157 | 46.9203 | 42.9512 | 38.9585 | 34.5384 | 28.9242 | 22.3053 | 15.3646 | 9.124 | 2.9407 | -31.5328 | -51.2358 | -63.4043
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Leading the Way | Thermal headroom (MW) | 60.9696 | 59.2534 | 57.0362 | 54.7113 | 51.7099 | 45.9324 | 40.0247 | 33.312 | 26.3393 | 18.6728 | 12.0544 | 5.0865 | -2.1233 | -8.9652 | -15.1468 | -41.4734 | -54.9892 | -64.9244
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Steady Progression | Thermal headroom (MW) | 60.9696 | 60.5877 | 59.8231 | 59.1226 | 58.2699 | 56.5035 | 54.7501 | 52.9124 | 51.0413 | 48.8657 | 45.9912 | 43.3697 | 40.4711 | 37.4528 | 34.4625 | 14.8729 | 4.7339 | 0.69114
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | System Transformation | Thermal headroom (MW) | 60.9696 | 60.3133 | 59.2586 | 58.2082 | 56.8898 | 55.4934 | 53.9495 | 51.9596 | 49.6573 | 47.3445 | 44.1769 | 41.2198 | 37.9426 | 34.2136 | 30.4568 | 9.4944 | -5.6244 | -11.7188
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | WPD Best View | Thermal headroom (MW) | 60.9696 | 59.9192 | 58.389 | 56.6673 | 54.3913 | 50.6464 | 46.9063 | 43.0313 | 39.1237 | 34.8485 | 29.3855 | 22.9307 | 16.0956 | 9.9582 | 3.8144 | -31.2325 | -50.8819 | -62.9672
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Consumer Transformation | Thermal headroom (MW) | 3.16 | 2.98 | 2.81 | 2.66 | 2.42 | 1.95 | 1.47 | 0.98 | 0.48 | -0.04 | -0.55 | -1.15 | -1.89 | -2.61 | -3.31 | -8.07 | -11.16 | -13.49
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Leading the Way | Thermal headroom (MW) | 3.16 | 2.89 | 2.65 | 2.43 | 2.11 | 1.33 | 0.49 | -0.42 | -1.45 | -2.59 | -3.47 | -4.41 | -5.42 | -6.43 | -7.34 | -11.29 | -14.03 | -16.61
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Steady Progression | Thermal headroom (MW) | 3.16 | 3.08 | 3.03 | 3 | 2.94 | 2.77 | 2.58 | 2.37 | 2.16 | 1.86 | 1.48 | 1.21 | 0.92 | 0.6 | 0.29 | -1.69 | -2.95 | -3.38
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | System Transformation | Thermal headroom (MW) | 3.16 | 3.02 | 2.92 | 2.84 | 2.71 | 2.51 | 2.27 | 1.95 | 1.57 | 1.26 | 0.78 | 0.48 | 0.03 | -0.3 | -0.71 | -3.03 | -5.6 | -7.09
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | WPD Best View | Thermal headroom (MW) | 3.16 | 2.98 | 2.81 | 2.66 | 2.42 | 1.95 | 1.47 | 0.98 | 0.48 | -0.04 | -0.55 | -1.15 | -1.89 | -2.61 | -3.31 | -8.07 | -11.16 | -13.49
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Consumer Transformation | Thermal headroom (MW) | 12.1 | 12.1 | 11.92 | 11.7 | 11.43 | 11.08 | 10.71 | 10.3 | 9.87 | 9.38 | 8.89 | 8.48 | 8.03 | 7.37 | 6.6 | 1.14 | -1.8 | -3.32
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Leading the Way | Thermal headroom (MW) | 12.1 | 12.02 | 11.73 | 11.43 | 11.06 | 10.5 | 9.92 | 9.28 | 8.6 | 7.84 | 7.22 | 6.48 | 5.54 | 4.65 | 3.82 | 0.03 | -1.48 | -2.43
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Steady Progression | Thermal headroom (MW) | 12.1 | 12.24 | 12.25 | 12.26 | 12.25 | 12.11 | 11.94 | 11.74 | 11.51 | 11.24 | 10.89 | 10.52 | 10.11 | 9.67 | 9.24 | 6.55 | 5.12 | 4.28
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | System Transformation | Thermal headroom (MW) | 12.1 | 12.21 | 12.18 | 12.14 | 12.06 | 11.95 | 11.82 | 11.62 | 11.36 | 11.04 | 10.67 | 10.27 | 9.86 | 9.47 | 9.13 | 6.55 | 4.57 | 4.17
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | WPD Best View | Thermal headroom (MW) | 12.1 | 12.1 | 11.92 | 11.7 | 11.43 | 11.08 | 10.71 | 10.3 | 9.87 | 9.38 | 8.89 | 8.48 | 8.03 | 7.37 | 6.6 | 1.14 | -1.8 | -3.32
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Consumer Transformation | Thermal headroom (MW) | 19.61 | 19.09 | 18.63 | 18.09 | 17.48 | 16.89 | 16.28 | 15.63 | 14.95 | 14.21 | 13.36 | 12.55 | 11.71 | 10.95 | 10.25 | 6.76 | 5.82 | 5.47
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Leading the Way | Thermal headroom (MW) | 19.61 | 19.01 | 18.46 | 17.85 | 17.22 | 16.5 | 15.81 | 14.96 | 14.01 | 12.96 | 11.84 | 10.87 | 9.91 | 9.09 | 8.46 | 6.15 | 5.9 | 5.92
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Steady Progression | Thermal headroom (MW) | 19.61 | 19.22 | 18.9 | 18.57 | 18.26 | 17.94 | 17.63 | 17.34 | 17.05 | 16.77 | 16.42 | 16.07 | 15.69 | 15.3 | 14.98 | 13.62 | 13.26 | 13.16
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | System Transformation | Thermal headroom (MW) | 19.61 | 19.15 | 18.76 | 18.36 | 17.97 | 17.63 | 17.28 | 16.91 | 16.48 | 16.01 | 15.56 | 15.15 | 14.74 | 14.34 | 14.01 | 12.52 | 12.3 | 12.34
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | WPD Best View | Thermal headroom (MW) | 19.61 | 19.09 | 18.63 | 18.09 | 17.48 | 16.89 | 16.28 | 15.63 | 14.95 | 14.21 | 13.36 | 12.55 | 11.71 | 10.95 | 10.25 | 6.76 | 5.82 | 5.47
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Consumer Transformation | Thermal headroom (MW) | 3.1 | 2.96 | 2.04 | 1.4 | 0.54 | -0.72 | -2.12 | -3.56 | -4.99 | -6.68 | -9.72 | -13.17 | -16.67 | -19.8 | -22.87 | -39.82 | -50.29 | -56.04
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Leading the Way | Thermal headroom (MW) | 3.1 | 2.65 | 1.31 | 0.3 | -1.18 | -3.3 | -5.39 | -8.03 | -10.69 | -13.64 | -16.99 | -20.5 | -24.05 | -27.48 | -30.74 | -44.04 | -50.04 | -53.86
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Steady Progression | Thermal headroom (MW) | 3.1 | 3.29 | 2.79 | 2.63 | 2.41 | 1.97 | 1.5 | 0.96 | 0.41 | -0.25 | -1.17 | -2.13 | -3.19 | -4.3 | -5.43 | -12.53 | -17.32 | -19.41
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | System Transformation | Thermal headroom (MW) | 3.1 | 3.2 | 2.51 | 2.21 | 1.8 | 1.34 | 0.82 | 0.14 | -0.74 | -1.64 | -2.88 | -4.23 | -5.59 | -7.28 | -8.88 | -17.26 | -21.81 | -24.01
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | WPD Best View | Thermal headroom (MW) | 3.1 | 2.96 | 2.04 | 1.4 | 0.54 | -0.72 | -2.12 | -3.56 | -4.99 | -6.68 | -9.72 | -13.17 | -16.67 | -19.8 | -22.87 | -39.82 | -50.29 | -56.04
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Consumer Transformation | Thermal headroom (MW) | 16.99 | 15.79 | 14.87 | 13.77 | 12.4 | 10.57 | 8.85 | 6.82 | 4.76 | 2.47 | -0.98 | -4.77 | -8.52 | -11.8 | -14.94 | -29.82 | -38.99 | -43.92
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Leading the Way | Thermal headroom (MW) | 16.99 | 15.12 | 13.6 | 11.95 | 9.99 | 7.3 | 4.67 | 1.5 | -1.61 | -4.93 | -8.56 | -12.38 | -16 | -19.42 | -22.55 | -32.13 | -36.38 | -38.36
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Steady Progression | Thermal headroom (MW) | 16.99 | 16.33 | 15.88 | 15.36 | 14.76 | 13.87 | 13.03 | 12.13 | 11.34 | 10.44 | 9.29 | 8.15 | 6.95 | 5.63 | 4.27 | -4.52 | -9.98 | -11.91
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | System Transformation | Thermal headroom (MW) | 16.99 | 16.08 | 15.36 | 14.59 | 13.7 | 12.93 | 12.14 | 11.02 | 9.87 | 8.74 | 7.41 | 5.84 | 4.22 | 2.1 | -0.06 | -9.66 | -13.82 | -14.98
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | WPD Best View | Thermal headroom (MW) | 16.99 | 15.79 | 14.87 | 13.77 | 12.4 | 10.57 | 8.85 | 6.82 | 4.76 | 2.47 | -0.98 | -4.77 | -8.52 | -11.8 | -14.94 | -29.82 | -38.99 | -43.92
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Consumer Transformation | Thermal headroom (MW) | 1.91 | 1.92 | 1.9 | 1.86 | 1.75 | 1.4 | 1.08 | 0.78 | 0.48 | 0.15 | -0.21 | -0.62 | -1.09 | -1.57 | -2.07 | -5.07 | -7.4 | -9.62
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Leading the Way | Thermal headroom (MW) | 1.91 | 1.9 | 1.85 | 1.79 | 1.65 | 1.14 | 0.63 | 0.1 | -0.42 | -0.97 | -1.41 | -1.96 | -2.55 | -3.1 | -3.6 | -6.34 | -8.53 | -10.75
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Steady Progression | Thermal headroom (MW) | 1.91 | 1.94 | 1.95 | 1.95 | 1.92 | 1.81 | 1.7 | 1.6 | 1.48 | 1.35 | 1.19 | 1.02 | 0.85 | 0.66 | 0.48 | -1.07 | -2.04 | -2.27
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | System Transformation | Thermal headroom (MW) | 1.91 | 1.94 | 1.94 | 1.92 | 1.87 | 1.78 | 1.69 | 1.54 | 1.34 | 1.19 | 1.01 | 0.83 | 0.63 | 0.43 | 0.24 | -1.25 | -3.14 | -4.33
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | WPD Best View | Thermal headroom (MW) | 1.91 | 1.92 | 1.9 | 1.86 | 1.75 | 1.4 | 1.08 | 0.78 | 0.48 | 0.15 | -0.21 | -0.62 | -1.09 | -1.57 | -2.07 | -5.07 | -7.4 | -9.62
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Consumer Transformation | Thermal headroom (MW) | 4.66 | 4.62 | 4.4 | 4.12 | 3.74 | 3.25 | 2.78 | 2.28 | 1.77 | 1.23 | 0.59 | -0.4 | -1.45 | -2.43 | -3.43 | -9.47 | -13.88 | -17.25
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Leading the Way | Thermal headroom (MW) | 4.66 | 4.55 | 4.23 | 3.84 | 3.34 | 2.55 | 1.74 | 0.89 | 0.03 | -1.02 | -2.15 | -3.38 | -4.6 | -5.78 | -6.83 | -11.42 | -14.6 | -17.59
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Steady Progression | Thermal headroom (MW) | 4.66 | 4.74 | 4.67 | 4.59 | 4.46 | 4.28 | 4.09 | 3.88 | 3.64 | 3.38 | 3.05 | 2.7 | 2.34 | 1.97 | 1.6 | -0.64 | -2.28 | -2.78
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | System Transformation | Thermal headroom (MW) | 4.66 | 4.71 | 4.6 | 4.46 | 4.24 | 4.1 | 3.93 | 3.66 | 3.3 | 2.98 | 2.61 | 2.23 | 1.84 | 1.44 | 1.1 | -1.58 | -3.99 | -5.42
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | WPD Best View | Thermal headroom (MW) | 4.66 | 4.62 | 4.4 | 4.12 | 3.74 | 3.25 | 2.78 | 2.28 | 1.77 | 1.23 | 0.59 | -0.4 | -1.45 | -2.43 | -3.43 | -9.47 | -13.88 | -17.25
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Consumer Transformation | Thermal headroom (MW) | 79.14 | 79.16 | 79.13 | 79.09 | 79.01 | 78.68 | 78.36 | 78.01 | 77.68 | 77.29 | 76.67 | 76.06 | 75.44 | 74.83 | 74.23 | 71.31 | 69.69 | 68.86
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Leading the Way | Thermal headroom (MW) | 79.14 | 79.07 | 78.94 | 78.83 | 78.67 | 78.08 | 77.46 | 76.84 | 76.24 | 75.61 | 75.16 | 74.66 | 74.14 | 73.63 | 73.13 | 70.98 | 70.01 | 69.42
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Steady Progression | Thermal headroom (MW) | 79.14 | 79.14 | 79.1 | 79.04 | 78.98 | 78.75 | 78.53 | 78.31 | 78.1 | 77.89 | 77.57 | 77.28 | 76.89 | 76.51 | 76.08 | 73.56 | 72.66 | 72.24
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | System Transformation | Thermal headroom (MW) | 79.14 | 79.15 | 79.11 | 79.06 | 78.99 | 78.93 | 78.89 | 78.84 | 78.78 | 78.72 | 78.43 | 78.1 | 77.75 | 77.41 | 77.04 | 74.71 | 73.1 | 72.57
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | WPD Best View | Thermal headroom (MW) | 79.14 | 79.14 | 79.08 | 79.01 | 78.92 | 78.64 | 78.35 | 78.07 | 77.79 | 77.5 | 76.98 | 76.49 | 75.94 | 75.4 | 74.83 | 71.51 | 69.93 | 69.16
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Consumer Transformation | Thermal headroom (MW) | 5.09 | 5.04 | 4.94 | 4.81 | 4.63 | 4.22 | 3.79 | 3.34 | 2.88 | 2.37 | 1.82 | 0.77 | -0.29 | -0.96 | -1.65 | -6.03 | -8.2 | -9.14
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Leading the Way | Thermal headroom (MW) | 5.09 | 4.98 | 4.82 | 4.65 | 4.41 | 3.79 | 3.05 | 2.23 | 1.26 | 0.23 | -0.37 | -1.03 | -1.75 | -2.4 | -3.02 | -6.28 | -7.67 | -8.09
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Steady Progression | Thermal headroom (MW) | 5.09 | 5.11 | 5.09 | 5.07 | 5.04 | 4.89 | 4.73 | 4.56 | 4.37 | 4.14 | 3.85 | 3.56 | 3.26 | 2.94 | 2.61 | -0.57 | -2.43 | -3.29
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | System Transformation | Thermal headroom (MW) | 5.09 | 5.09 | 5.05 | 5.01 | 4.92 | 4.76 | 4.55 | 4.3 | 4.03 | 3.71 | 3.45 | 3.17 | 2.88 | 2.24 | 1.61 | -1.91 | -4.19 | -4.68
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | WPD Best View | Thermal headroom (MW) | 5.09 | 5.04 | 4.94 | 4.81 | 4.63 | 4.22 | 3.79 | 3.34 | 2.88 | 2.37 | 1.82 | 0.77 | -0.29 | -0.96 | -1.65 | -6.03 | -8.2 | -9.14
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Consumer Transformation | Thermal headroom (MW) | 9.7309 | 8.6698 | 7.1964 | 6.51 | 3.3269 | 0.34944 | -2.4744 | -5.5243 | -8.8844 | -13.1483 | -20.4691 | -27.8161 | -35.337 | -42.7575 | -50.3055 | -87.3577 | -106.2353 | -114.3924
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Leading the Way | Thermal headroom (MW) | 9.7309 | 7.8324 | 5.5676 | 4.3395 | -0.31537 | -5.55 | -10.3916 | -16.0661 | -22.188 | -28.8754 | -36.194 | -44.1405 | -52.0153 | -59.9889 | -67.6602 | -96.3838 | -102.823 | -103.8372
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Steady Progression | Thermal headroom (MW) | 9.7309 | 9.3501 | 8.5999 | 8.6005 | 6.6234 | 4.8524 | 3.372 | 1.814 | 0.14546 | -2.1252 | -5.0067 | -7.703 | -11.164 | -14.7757 | -18.4917 | -42.4327 | -50.7434 | -52.1787
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | System Transformation | Thermal headroom (MW) | 9.7309 | 9.0524 | 7.9831 | 7.77 | 5.1777 | 3.3549 | 1.5944 | -0.38384 | -2.6315 | -5.1537 | -8.4011 | -11.9285 | -16.0036 | -20.3123 | -24.6614 | -49.7148 | -55.6014 | -55.7084
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | WPD Best View | Thermal headroom (MW) | 9.7309 | 8.6698 | 7.1964 | 6.51 | 3.3269 | 0.34944 | -2.4744 | -5.5243 | -8.8844 | -13.1483 | -20.4691 | -27.8161 | -35.337 | -42.7575 | -50.3055 | -87.3577 | -106.2353 | -114.3924
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Consumer Transformation | Thermal headroom (MW) | 5.6 | 5.46 | 5.15 | 4.8 | 4.27 | 3.44 | 2.52 | 1.58 | 0.52 | -1 | -4.59 | -8.24 | -11.92 | -15.5 | -19.1 | -34.2 | -47.21 | -54.68
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Leading the Way | Thermal headroom (MW) | 5.6 | 5.15 | 4.51 | 3.83 | 2.66 | 1 | -0.81 | -2.94 | -5.44 | -8.16 | -11.28 | -14.7 | -18.23 | -21.76 | -25.09 | -35.19 | -40.56 | -43.3
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Steady Progression | Thermal headroom (MW) | 5.6 | 5.76 | 5.77 | 5.78 | 5.74 | 5.44 | 5.12 | 4.81 | 4.43 | 3.67 | 2.63 | 1.91 | 1.14 | 0.25 | -0.55 | -7.44 | -12.7 | -15.16
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | System Transformation | Thermal headroom (MW) | 5.6 | 5.69 | 5.59 | 5.5 | 5.29 | 5.07 | 4.81 | 4.43 | 3.92 | 3.29 | 2.36 | 1.35 | -0.05 | -1.41 | -2.67 | -10.75 | -14.56 | -16.3
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | WPD Best View | Thermal headroom (MW) | 5.6 | 5.46 | 5.15 | 4.8 | 4.27 | 3.44 | 2.52 | 1.58 | 0.52 | -1 | -4.59 | -8.24 | -11.92 | -15.5 | -19.1 | -34.2 | -47.21 | -54.68
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Consumer Transformation | Thermal headroom (MW) | 8.68 | 7.89 | 7.79 | 7.65 | 5.75 | 4.3 | 2.99 | 1.52 | -0.05 | -1.96 | -4.4 | -6.82 | -9.31 | -11.83 | -14.45 | -28.27 | -31.2 | -31.14
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Leading the Way | Thermal headroom (MW) | 8.68 | 7.65 | 7.41 | 7.21 | 4.77 | 2.37 | 0.35 | -2.03 | -4.45 | -7.07 | -9.83 | -12.78 | -15.61 | -18.49 | -21.36 | -33.9 | -34.03 | -32.54
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Steady Progression | Thermal headroom (MW) | 8.68 | 8.1 | 8.1 | 8.09 | 6.59 | 5.51 | 4.68 | 3.79 | 2.85 | 1.73 | 0.4 | -1.04 | -3.01 | -4.95 | -7.03 | -18.96 | -20.56 | -19.71
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | System Transformation | Thermal headroom (MW) | 8.68 | 7.96 | 7.9 | 7.84 | 6.03 | 4.81 | 3.74 | 2.54 | 1.25 | -0.17 | -1.84 | -3.63 | -5.55 | -7.62 | -9.82 | -21.52 | -22.47 | -21.22
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | WPD Best View | Thermal headroom (MW) | 8.68 | 7.89 | 7.79 | 7.65 | 5.75 | 4.3 | 2.99 | 1.52 | -0.05 | -1.96 | -4.4 | -6.82 | -9.31 | -11.83 | -14.45 | -28.27 | -31.2 | -31.14
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Consumer Transformation | Thermal headroom (MW) | 5.93 | 6 | 4.94 | 4.76 | 4.53 | 4.21 | 3.94 | 3.69 | 3.35 | 2.98 | 2.22 | 1.46 | 0.64 | -0.13 | -0.87 | -5.82 | -8.58 | -9.71
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Leading the Way | Thermal headroom (MW) | 5.93 | 5.77 | 4.39 | 4.07 | 3.66 | 3.09 | 2.57 | 1.98 | 1.36 | 0.63 | -0.17 | -1.08 | -1.95 | -2.86 | -3.68 | -6.67 | -7.84 | -8.16
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Steady Progression | Thermal headroom (MW) | 5.93 | 6.14 | 5.36 | 5.36 | 5.36 | 5.26 | 5.16 | 5.05 | 4.94 | 4.84 | 4.66 | 4.5 | 4.32 | 4.05 | 3.78 | 1.75 | 0.49 | 0.3
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | System Transformation | Thermal headroom (MW) | 5.93 | 6.1 | 5.16 | 5.12 | 5.05 | 5.01 | 4.89 | 4.81 | 4.72 | 4.62 | 4.41 | 4.14 | 3.88 | 3.54 | 3.22 | 0.89 | -0.15 | -0.22
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | WPD Best View | Thermal headroom (MW) | 5.93 | 6 | 4.94 | 4.76 | 4.53 | 4.21 | 3.94 | 3.69 | 3.35 | 2.98 | 2.22 | 1.46 | 0.64 | -0.13 | -0.87 | -5.82 | -8.58 | -9.71
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Consumer Transformation | Thermal headroom (MW) | 44.65 | 43.7489 | 41.964 | 39.3213 | 35.956 | 31.2485 | 27.1762 | 22.3735 | 16.9868 | 11.0035 | 1.0208 | -9.4274 | -20.1857 | -30.7656 | -40.8316 | -88.594 | -118.1984 | -132.7144
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Leading the Way | Thermal headroom (MW) | 44.65 | 41.969 | 38.2652 | 33.7002 | 28.1737 | 21.3072 | 14.3415 | 6.6274 | -1.731 | -10.966 | -21.3751 | -32.5247 | -43.5818 | -54.1616 | -63.9827 | -95.6434 | -106.7494 | -109.8242
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Steady Progression | Thermal headroom (MW) | 44.65 | 45.5091 | 45.7058 | 45.4097 | 44.8669 | 43.4678 | 42.1776 | 40.6968 | 38.9658 | 36.934 | 33.4518 | 29.8786 | 26.0804 | 21.9103 | 17.6194 | -10.2708 | -30.7742 | -38.7958
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | System Transformation | Thermal headroom (MW) | 44.65 | 44.9832 | 44.5609 | 43.4968 | 42.0876 | 40.9232 | 39.8379 | 38.4322 | 36.4988 | 33.5686 | 29.6862 | 25.0841 | 20.1225 | 15.0583 | 10.0424 | -18.7732 | -30.9894 | -34.4916
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | WPD Best View | Thermal headroom (MW) | 44.65 | 43.1244 | 40.6668 | 37.2658 | 32.9432 | 27.7781 | 22.4546 | 16.7102 | 10.3246 | 3.3079 | -6.8005 | -17.2792 | -27.9246 | -38.276 | -47.9211 | -88.0093 | -109.0879 | -116.2004
Stoke Bardolph 132kV | Nottingham East | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Consumer Transformation | Thermal headroom (MW) | -10.166 | -10.096 | -10.306 | -10.666 | -11.106 | -12.036 | -13.086 | -14.246 | -15.426 | -16.706 | -18.796 | -21.126 | -23.436 | -26.236 | -28.946 | -42.376 | -51.566 | -55.866
Stoke Bardolph 132kV | Nottingham East | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Leading the Way | Thermal headroom (MW) | -10.166 | -10.536 | -11.226 | -12.016 | -12.916 | -14.486 | -16.226 | -18.126 | -20.036 | -22.086 | -24.396 | -27.416 | -30.436 | -33.356 | -36.066 | -45.566 | -49.896 | -51.706
Stoke Bardolph 132kV | Nottingham East | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Steady Progression | Thermal headroom (MW) | -10.166 | -9.706 | -9.516 | -9.386 | -9.276 | -9.496 | -9.776 | -10.106 | -10.486 | -11.006 | -11.806 | -12.656 | -13.556 | -14.506 | -15.456 | -20.526 | -24.326 | -26.336
Stoke Bardolph 132kV | Nottingham East | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | System Transformation | Thermal headroom (MW) | -10.166 | -9.816 | -9.776 | -9.806 | -9.866 | -10.026 | -10.266 | -10.596 | -11.176 | -11.916 | -12.976 | -14.116 | -15.246 | -16.326 | -17.256 | -21.486 | -24.336 | -25.366
Stoke Bardolph 132kV | Nottingham East | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | WPD Best View | Thermal headroom (MW) | -10.166 | -10.176 | -10.496 | -10.936 | -11.466 | -12.476 | -13.606 | -14.846 | -16.106 | -17.466 | -19.646 | -21.986 | -24.386 | -27.186 | -29.876 | -42.436 | -50.846 | -54.496
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Consumer Transformation | Thermal headroom (MW) | 9.412 | 9.052 | 8.392 | 7.552 | 6.462 | 4.512 | 2.692 | 0.962 | -0.948 | -2.948 | -6.088 | -9.988 | -13.918 | -17.718 | -21.408 | -40.548 | -53.458 | -59.738
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Leading the Way | Thermal headroom (MW) | 9.412 | 8.442 | 7.122 | 5.692 | 3.722 | 0.762 | -1.838 | -4.668 | -8.138 | -11.948 | -15.918 | -20.088 | -24.258 | -28.318 | -32.108 | -44.968 | -50.448 | -53.108
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Steady Progression | Thermal headroom (MW) | 9.412 | 9.692 | 9.722 | 9.702 | 9.612 | 8.982 | 8.412 | 7.782 | 6.872 | 5.842 | 4.562 | 3.272 | 1.892 | 0.452 | -0.978 | -9.208 | -16.108 | -18.948
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | System Transformation | Thermal headroom (MW) | 9.412 | 9.492 | 9.292 | 9.032 | 8.632 | 7.972 | 7.362 | 6.552 | 5.422 | 4.172 | 2.792 | 1.282 | -0.268 | -1.768 | -3.148 | -12.078 | -17.248 | -19.468
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | WPD Best View | Thermal headroom (MW) | 9.412 | 8.932 | 8.142 | 7.192 | 5.982 | 4.012 | 2.172 | 0.382 | -1.578 | -3.728 | -7.478 | -11.438 | -15.438 | -19.308 | -23.058 | -41.208 | -52.868 | -58.478
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Consumer Transformation | Thermal headroom (MW) | 10.074 | 9.734 | 9.194 | 8.574 | 7.774 | 6.534 | 5.614 | 4.654 | 3.604 | 2.484 | 0.374 | -1.736 | -4.016 | -6.266 | -8.436 | -20.936 | -29.086 | -32.996
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Leading the Way | Thermal headroom (MW) | 10.074 | 9.154 | 7.994 | 6.814 | 5.504 | 3.514 | 1.854 | 0.054 | -1.736 | -3.706 | -5.926 | -8.266 | -10.626 | -12.926 | -15.186 | -24.186 | -28.356 | -30.876
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Steady Progression | Thermal headroom (MW) | 10.074 | 10.124 | 10.074 | 10.014 | 9.864 | 9.374 | 8.964 | 8.504 | 8.054 | 7.594 | 6.864 | 6.194 | 5.484 | 4.674 | 3.864 | -2.056 | -6.166 | -8.236
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | System Transformation | Thermal headroom (MW) | 10.074 | 10.034 | 9.874 | 9.674 | 9.374 | 8.964 | 8.654 | 8.264 | 7.784 | 7.304 | 6.574 | 5.564 | 4.534 | 3.554 | 2.664 | -4.226 | -7.566 | -8.976
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | WPD Best View | Thermal headroom (MW) | 10.074 | 9.734 | 9.194 | 8.574 | 7.774 | 6.534 | 5.614 | 4.654 | 3.604 | 2.484 | 0.374 | -1.736 | -4.016 | -6.266 | -8.436 | -20.936 | -29.086 | -32.996
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Consumer Transformation | Thermal headroom (MW) | 17.35 | 17.09 | 16.67 | 15.23 | 13.48 | 11.76 | 10.17 | 8.52 | 6.83 | 5.07 | 1.63 | -1.79 | -5.34 | -8.77 | -12.1 | -27.63 | -38.51 | -44.23
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Leading the Way | Thermal headroom (MW) | 17.35 | 16.55 | 15.52 | 13.14 | 10.22 | 7.92 | 5.79 | 3.32 | 0.68 | -2.15 | -5.53 | -9.06 | -12.61 | -16.03 | -19.3 | -30.08 | -34.39 | -35.94
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Steady Progression | Thermal headroom (MW) | 17.35 | 17.7 | 17.87 | 17.23 | 16.48 | 16.03 | 15.53 | 14.83 | 14.02 | 13.12 | 11.91 | 10.69 | 9.44 | 8.2 | 6.94 | -1.33 | -8.2 | -11.25
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | System Transformation | Thermal headroom (MW) | 17.35 | 17.5 | 17.46 | 16.46 | 15.31 | 14.99 | 14.51 | 13.81 | 12.93 | 11.95 | 10.82 | 9.65 | 8.44 | 7.19 | 5.9 | -1.7 | -5.61 | -7.38
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | WPD Best View | Thermal headroom (MW) | 17.35 | 16.62 | 15.69 | 13.49 | 10.69 | 8.53 | 6.62 | 4.45 | 2.02 | -0.57 | -3.92 | -7.39 | -10.88 | -14.23 | -17.43 | -29 | -34.39 | -36.48
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Consumer Transformation | Thermal headroom (MW) | 20.48 | 19.5 | 18.37 | 17.04 | 15.26 | 12.31 | 9.74 | 7.21 | 4.47 | 1.29 | -4.87 | -11.08 | -17.31 | -23.38 | -29.39 | -52.46 | -69.46 | -78.73
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Leading the Way | Thermal headroom (MW) | 20.48 | 18.44 | 16.23 | 13.9 | 11.02 | 7.27 | 3.81 | 0.12 | -4.15 | -8.95 | -14.38 | -20.19 | -26.13 | -31.84 | -37.16 | -51.86 | -57.86 | -58.45
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Steady Progression | Thermal headroom (MW) | 20.48 | 20.48 | 20.33 | 20.16 | 19.84 | 18.88 | 17.88 | 16.83 | 15.67 | 14.06 | 12.1 | 10.48 | 8.76 | 6.8 | 4.86 | -9.07 | -20.02 | -25.1
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | System Transformation | Thermal headroom (MW) | 20.48 | 20.21 | 19.75 | 19.22 | 18.41 | 17.45 | 16.49 | 15.49 | 14.29 | 12.79 | 11.1 | 9.17 | 6.7 | 4.06 | 1.36 | -11.96 | -17.89 | -20.17
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | WPD Best View | Thermal headroom (MW) | 20.48 | 18.44 | 16.23 | 13.9 | 11.02 | 7.27 | 3.81 | 0.12 | -4.15 | -8.95 | -14.38 | -20.19 | -26.13 | -31.84 | -37.16 | -51.86 | -57.86 | -58.45
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Consumer Transformation | Thermal headroom (MW) | 34.66 | 32.7516 | 29.3148 | 25.6654 | 20.7229 | 12.8646 | 6.001 | -0.66444 | -7.2196 | -14.6268 | -30.5124 | -46.731 | -63.1122 | -78.9815 | -94.8194 | -177.6153 | -235.7699 | -265.0095
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Leading the Way | Thermal headroom (MW) | 34.66 | 29.4997 | 22.366 | 14.789 | 5.6959 | -6.8837 | -18.2218 | -30.2077 | -42.4386 | -55.8791 | -70.8718 | -87.2548 | -104.1297 | -120.5462 | -136.0981 | -191.6874 | -217.6229 | -229.8025
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Steady Progression | Thermal headroom (MW) | 34.66 | 34.9347 | 33.9443 | 33.1276 | 31.8916 | 28.9962 | 26.2836 | 23.3924 | 20.3644 | 16.3635 | 10.9856 | 6.3213 | 1.3175 | -3.8657 | -8.9836 | -45.4592 | -73.2254 | -88.3497
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | System Transformation | Thermal headroom (MW) | 34.66 | 34.086 | 32.1296 | 30.2047 | 27.66 | 24.6776 | 21.94 | 18.8927 | 15.5763 | 11.7265 | 5.7228 | 0.1385 | -6.3257 | -12.5804 | -19.5157 | -58.9491 | -80.7893 | -90.469
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | WPD Best View | Thermal headroom (MW) | 34.66 | 30.187 | 24.0371 | 17.3757 | 9.3942 | -1.6987 | -11.9167 | -22.7684 | -33.9881 | -46.3074 | -61.2077 | -77.0409 | -93.4396 | -109.5995 | -125.0495 | -186.8439 | -218.9622 | -233.7887
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Consumer Transformation | Thermal headroom (MW) | 14.92 | 14.04 | 12.14 | 10.49 | 8.13 | 5.23 | 2.95 | 1.05 | -0.85 | -3.18 | -7.29 | -11.77 | -16.22 | -20.12 | -23.94 | -42.89 | -54.54 | -59.75
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Leading the Way | Thermal headroom (MW) | 14.92 | 13.37 | 10.6 | 7.74 | 3.83 | -0.45 | -3.51 | -6.28 | -9 | -12.31 | -16.46 | -20.78 | -25.02 | -28.93 | -32.55 | -44.35 | -49.14 | -50.11
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Steady Progression | Thermal headroom (MW) | 14.92 | 14.55 | 13.31 | 12.41 | 11.17 | 9.97 | 9.08 | 8.2 | 7.27 | 6.11 | 4.68 | 3.23 | 1.65 | 0.29 | -1.15 | -11.52 | -19.2 | -22.81
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | System Transformation | Thermal headroom (MW) | 14.92 | 14.29 | 12.67 | 11.39 | 9.73 | 8.3 | 7.31 | 6.33 | 5.35 | 4.05 | 2.47 | 0.87 | -0.87 | -2.9 | -5.06 | -15.31 | -19.89 | -21
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | WPD Best View | Thermal headroom (MW) | 14.92 | 13.49 | 10.95 | 8.42 | 5.07 | 1.19 | -1.85 | -4.76 | -7.6 | -11.03 | -15.25 | -19.57 | -23.88 | -27.9 | -31.67 | -44.38 | -49.61 | -50.87
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Consumer Transformation | Thermal headroom (MW) | 5.82 | 5.64 | 5.3 | 4.78 | 3.9 | 2.26 | 0.76 | -0.86 | -2.27 | -3.83 | -7.26 | -10.65 | -14.11 | -17.5 | -20.82 | -38.83 | -50.56 | -56.63
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Leading the Way | Thermal headroom (MW) | 5.82 | 5.13 | 4.01 | 2.64 | 1.05 | -1.42 | -3.92 | -6.78 | -9.27 | -11.88 | -15.21 | -18.7 | -22.33 | -25.84 | -29.17 | -41.68 | -47.64 | -51.01
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Steady Progression | Thermal headroom (MW) | 5.82 | 6 | 6.04 | 6.05 | 5.99 | 5.52 | 5.02 | 4.38 | 3.75 | 3.07 | 2.12 | 1.16 | 0.15 | -0.89 | -1.94 | -9.77 | -16.7 | -20.81
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | System Transformation | Thermal headroom (MW) | 5.82 | 5.87 | 5.75 | 5.56 | 5.25 | 4.78 | 4.19 | 3.44 | 2.7 | 1.85 | 0.61 | -0.7 | -2.03 | -3.3 | -4.63 | -13.38 | -18.21 | -20.29
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | WPD Best View | Thermal headroom (MW) | 5.82 | 5.19 | 4.27 | 3.02 | 1.56 | -0.6 | -2.81 | -5.37 | -7.63 | -9.98 | -13.28 | -16.76 | -20.33 | -23.76 | -27.03 | -40.72 | -47.63 | -51.35
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Consumer Transformation | Thermal headroom (MW) | 0.49 | 0.07 | -0.55 | -1.23 | -2.06 | -3.53 | -4.89 | -6.26 | -7.67 | -9.3 | -13.75 | -18.18 | -22.67 | -27.04 | -31.58 | -49.87 | -67.53 | -78.48
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Leading the Way | Thermal headroom (MW) | 0.49 | -0.75 | -2.2 | -3.66 | -5.49 | -8 | -10.39 | -13.1 | -16.8 | -20.84 | -24.11 | -28 | -32.3 | -36.67 | -40.85 | -53.3 | -60 | -64.27
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Steady Progression | Thermal headroom (MW) | 0.49 | 0.63 | 0.62 | 0.61 | 0.53 | 0.01 | -0.56 | -1.13 | -1.71 | -3.03 | -4.8 | -5.68 | -6.71 | -7.98 | -9.08 | -17.43 | -23.58 | -26.49
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | System Transformation | Thermal headroom (MW) | 0.49 | 0.34 | 0.11 | -0.21 | -0.67 | -1.2 | -1.74 | -2.34 | -3.06 | -3.77 | -5.57 | -6.61 | -8.54 | -9.93 | -11.94 | -22.16 | -28.58 | -31.68
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | WPD Best View | Thermal headroom (MW) | 0.49 | -0.39 | -1.45 | -2.56 | -4.04 | -6.05 | -7.99 | -10.14 | -13.34 | -16.83 | -20.05 | -23.75 | -27.9 | -32.09 | -36.14 | -51.1 | -60.47 | -65.82
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Consumer Transformation | Thermal headroom (MW) | 51.7176 | 50.7576 | 49.8756 | 48.5333 | 45.7959 | 40.7909 | 35.0434 | 29.8396 | 24.5314 | 18.244 | 7.6444 | -3.6948 | -15.3803 | -26.478 | -37.6107 | -89.1095 | -121.9364 | -141.3566
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Leading the Way | Thermal headroom (MW) | 51.7176 | 49.7893 | 47.9473 | 45.7214 | 41.5899 | 32.933 | 23.6126 | 14.1392 | 3.7429 | -8.341 | -17.6507 | -27.8147 | -38.3027 | -48.4936 | -58.0862 | -94.3998 | -110.5542 | -120.028
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Steady Progression | Thermal headroom (MW) | 51.7176 | 51.5571 | 51.4578 | 51.213 | 50.2514 | 47.827 | 45.1505 | 42.7876 | 40.3504 | 36.917 | 32.1798 | 28.3461 | 24.2133 | 19.6337 | 15.1984 | -17.0942 | -32.6491 | -39.4736
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | System Transformation | Thermal headroom (MW) | 51.7176 | 51.1471 | 50.6613 | 49.9896 | 48.3352 | 46.4639 | 43.8743 | 41.652 | 39.1044 | 36.1245 | 32.0937 | 28.0009 | 22.8967 | 17.4335 | 11.7353 | -22.3579 | -44.5648 | -52.1151
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | WPD Best View | Thermal headroom (MW) | 51.7176 | 51.5148 | 51.3597 | 51.0505 | 50.0006 | 47.6873 | 45.0496 | 42.7442 | 40.4148 | 37.0485 | 32.5712 | 28.8038 | 24.805 | 20.3751 | 16.0629 | -15.9635 | -33.768 | -40.8629
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Consumer Transformation | Thermal headroom (MW) | 2.99 | 2.93 | 2.77 | 2.56 | 2.24 | 1.61 | 0.99 | 0.32 | -0.28 | -0.88 | -1.99 | -3.28 | -4.58 | -5.77 | -6.94 | -13.47 | -17.04 | -18.76
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Leading the Way | Thermal headroom (MW) | 2.99 | 2.8 | 2.5 | 2.17 | 1.73 | 0.63 | -0.46 | -1.71 | -3.02 | -4.3 | -5.39 | -6.58 | -7.77 | -8.92 | -9.92 | -14.38 | -16.21 | -17.14
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Steady Progression | Thermal headroom (MW) | 2.99 | 3.05 | 3.03 | 3.01 | 2.94 | 2.63 | 2.31 | 1.93 | 1.52 | 1.13 | 0.54 | -0.02 | -0.59 | -1.17 | -1.75 | -6.46 | -8.53 | -9.34
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | System Transformation | Thermal headroom (MW) | 2.99 | 3.02 | 2.95 | 2.87 | 2.73 | 2.52 | 2.3 | 1.97 | 1.66 | 1.34 | 0.82 | 0.26 | -0.28 | -0.82 | -1.3 | -5.44 | -8.64 | -9.63
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | WPD Best View | Thermal headroom (MW) | 2.99 | 3.03 | 2.98 | 2.91 | 2.8 | 2.55 | 2.28 | 1.92 | 1.6 | 1.26 | 0.75 | 0.21 | -0.33 | -0.86 | -1.43 | -6.04 | -8.67 | -9.57
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Consumer Transformation | Thermal headroom (MW) | 5.41 | 4.64 | 4.38 | 4.05 | 3.64 | 2.98 | 2.33 | 1.73 | 1.11 | 0.33 | -0.89 | -2.04 | -3.23 | -4.42 | -5.59 | -11.84 | -15.61 | -18.19
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Leading the Way | Thermal headroom (MW) | 5.41 | 4.45 | 4.09 | 3.71 | 3.24 | 2.1 | 1.03 | -0.23 | -1.46 | -2.83 | -3.92 | -5 | -6.07 | -7.07 | -8.05 | -12.92 | -15.54 | -17.65
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Steady Progression | Thermal headroom (MW) | 5.41 | 4.8 | 4.66 | 4.5 | 4.32 | 3.88 | 3.44 | 3.06 | 2.72 | 2.36 | 1.86 | 1.4 | 0.82 | 0.19 | -0.43 | -4.45 | -6.1 | -7.15
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | System Transformation | Thermal headroom (MW) | 5.41 | 4.68 | 4.49 | 4.28 | 4.03 | 3.83 | 3.66 | 3.43 | 3.15 | 2.91 | 2.47 | 2.02 | 1.57 | 1.11 | 0.52 | -3.78 | -7.12 | -8.66
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | WPD Best View | Thermal headroom (MW) | 5.41 | 4.8 | 4.66 | 4.5 | 4.32 | 3.88 | 3.43 | 3.03 | 2.68 | 2.32 | 1.82 | 1.36 | 0.77 | 0.15 | -0.47 | -4.5 | -6.15 | -7.21
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Consumer Transformation | Thermal headroom (MW) | 1.71 | 1.75 | 1.76 | 1.74 | 1.61 | 1.17 | 0.69 | 0.2 | -0.31 | -0.91 | -2.55 | -4.26 | -5.99 | -7.73 | -9.56 | -14.54 | -19.37 | -22.9
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Leading the Way | Thermal headroom (MW) | 1.71 | 1.75 | 1.74 | 1.72 | 1.51 | 0.9 | 0.21 | -0.68 | -1.91 | -3.42 | -4.4 | -5.53 | -6.84 | -8.17 | -9.48 | -13.13 | -14.78 | -15.74
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Steady Progression | Thermal headroom (MW) | 1.71 | 1.77 | 1.78 | 1.8 | 1.77 | 1.6 | 1.43 | 1.22 | 1 | 0.48 | -0.19 | -0.49 | -0.85 | -1.29 | -1.67 | -5.08 | -6.56 | -7.2
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | System Transformation | Thermal headroom (MW) | 1.71 | 1.76 | 1.77 | 1.77 | 1.71 | 1.56 | 1.38 | 1.17 | 0.93 | 0.67 | 0.4 | 0.09 | -0.59 | -1.25 | -1.92 | -5.81 | -8.09 | -8.87
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | WPD Best View | Thermal headroom (MW) | 1.71 | 1.76 | 1.77 | 1.78 | 1.74 | 1.53 | 1.3 | 1.06 | 0.8 | 0.24 | -0.39 | -0.69 | -1.04 | -1.48 | -1.85 | -5.22 | -6.96 | -7.69
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Consumer Transformation | Thermal headroom (MW) | 10.64 | 10.55 | 10.36 | 10.05 | 9.01 | 7.68 | 5.75 | 4.7 | 3.64 | 2.41 | 0.61 | -1.18 | -2.98 | -4.68 | -6.3 | -15.19 | -20.37 | -23.43
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Leading the Way | Thermal headroom (MW) | 10.64 | 10.25 | 9.76 | 9.17 | 7.61 | 5.51 | 2.71 | 1.15 | -0.42 | -2.16 | -4.05 | -6.01 | -7.88 | -9.59 | -11.2 | -16.56 | -19.17 | -20.72
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Steady Progression | Thermal headroom (MW) | 10.64 | 10.74 | 10.77 | 10.73 | 10.15 | 9.43 | 8.48 | 7.99 | 7.53 | 6.98 | 6.33 | 5.63 | 4.95 | 4.19 | 3.42 | -1.33 | -4.11 | -4.94
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | System Transformation | Thermal headroom (MW) | 10.64 | 10.65 | 10.52 | 10.35 | 9.53 | 8.75 | 7.32 | 6.72 | 6.09 | 5.43 | 4.6 | 3.74 | 2.82 | 1.88 | 0.95 | -4.21 | -6.57 | -7.4
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | WPD Best View | Thermal headroom (MW) | 10.64 | 10.74 | 10.77 | 10.73 | 10.15 | 9.43 | 8.48 | 7.99 | 7.53 | 6.98 | 6.33 | 5.63 | 4.95 | 4.19 | 3.42 | -1.33 | -4.11 | -4.94
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Consumer Transformation | Thermal headroom (MW) | 7.4025 | 7.3725 | 7.1525 | 6.7725 | 6.1625 | 5.2425 | 4.2925 | 3.3825 | 2.4425 | 1.5025 | 0.1925 | -1.6175 | -3.6275 | -5.4175 | -7.1875 | -19.2275 | -26.6075 | -30.1275
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Leading the Way | Thermal headroom (MW) | 7.4025 | 7.1325 | 6.6725 | 6.0625 | 5.0825 | 3.4125 | 1.7825 | 0.0925 | -1.5575 | -3.3775 | -5.2475 | -7.2775 | -9.3175 | -11.2675 | -13.0775 | -20.8675 | -24.6675 | -26.5975
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Steady Progression | Thermal headroom (MW) | 7.4025 | 7.5925 | 7.6125 | 7.5925 | 7.5125 | 7.1825 | 6.8325 | 6.4725 | 6.0825 | 5.6725 | 5.0425 | 4.4125 | 3.7525 | 3.0625 | 2.3825 | -2.2875 | -5.7775 | -7.4675
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | System Transformation | Thermal headroom (MW) | 7.4025 | 7.5225 | 7.4825 | 7.3725 | 7.1325 | 6.7625 | 6.3225 | 5.8325 | 5.2825 | 4.6825 | 3.9125 | 3.0925 | 2.2625 | 1.0825 | 0.0025 | -5.0975 | -8.9075 | -10.0475
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | WPD Best View | Thermal headroom (MW) | 7.4025 | 7.5925 | 7.6125 | 7.5925 | 7.5125 | 7.1725 | 6.8025 | 6.4225 | 6.0125 | 5.5825 | 4.9525 | 4.3125 | 3.6525 | 2.9525 | 2.2625 | -2.3975 | -5.9175 | -7.5875
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Consumer Transformation | Thermal headroom (MW) | 11.23 | 11.02 | 10.68 | 10.25 | 9.73 | 8.99 | 7.93 | 6.72 | 5.42 | 3.53 | 1.01 | -1.91 | -4.86 | -7.34 | -9.76 | -23.11 | -31.01 | -34.67
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Leading the Way | Thermal headroom (MW) | 11.23 | 10.75 | 10.1 | 9.34 | 8.37 | 6.49 | 4.42 | 2.38 | 0.35 | -2.63 | -5.33 | -8.17 | -10.92 | -13.61 | -16.09 | -24.47 | -27.49 | -28.48
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Steady Progression | Thermal headroom (MW) | 11.23 | 11.29 | 11.24 | 11.18 | 11.08 | 10.8 | 10.41 | 10.08 | 9.75 | 9.11 | 8.22 | 7.28 | 6.35 | 5.32 | 4.24 | -3.07 | -7.8 | -9.73
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | System Transformation | Thermal headroom (MW) | 11.23 | 11.2 | 11.05 | 10.87 | 10.63 | 10.35 | 9.88 | 9.48 | 8.99 | 8.01 | 6.98 | 5.78 | 4.49 | 2.8 | 1.02 | -7.33 | -10.74 | -11.59
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | WPD Best View | Thermal headroom (MW) | 11.23 | 11.29 | 11.24 | 11.18 | 11.08 | 10.8 | 10.42 | 10.11 | 9.77 | 9.17 | 8.3 | 7.37 | 6.45 | 5.43 | 4.36 | -2.94 | -7.73 | -9.65
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Consumer Transformation | Thermal headroom (MW) | -5.1 | -4.94 | -4.89 | -4.85 | -5.03 | -5.72 | -6.42 | -7.16 | -7.92 | -8.71 | -9.45 | -10.17 | -10.88 | -11.59 | -12.3 | -16.81 | -18.08 | -18.71
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Leading the Way | Thermal headroom (MW) | -5.1 | -5 | -5.06 | -5.13 | -5.44 | -6.62 | -7.84 | -9.15 | -10.69 | -12.35 | -12.93 | -13.6 | -14.32 | -15.05 | -15.75 | -19.68 | -20.99 | -21.84
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Steady Progression | Thermal headroom (MW) | -5.1 | -4.96 | -4.94 | -4.93 | -5.06 | -5.34 | -5.61 | -5.89 | -6.16 | -6.51 | -7.06 | -7.46 | -7.94 | -8.45 | -8.94 | -12.13 | -13.15 | -13.63
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | System Transformation | Thermal headroom (MW) | -5.1 | -4.98 | -4.98 | -4.99 | -5.19 | -5.4 | -5.65 | -5.9 | -6.25 | -6.61 | -7.15 | -7.5 | -7.98 | -8.38 | -8.89 | -12.74 | -15.64 | -16.48
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | WPD Best View | Thermal headroom (MW) | -5.1 | -4.96 | -4.94 | -4.94 | -5.09 | -5.25 | -5.42 | -5.59 | -5.82 | -6.17 | -6.66 | -7.03 | -7.41 | -7.83 | -8.23 | -11.67 | -13.75 | -14.1
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Consumer Transformation | Thermal headroom (MW) | 46.31 | 46.2464 | 45.9034 | 45.3812 | 44.6218 | 42.4384 | 40.2499 | 37.8807 | 35.8661 | 33.6545 | 30.9436 | 27.885 | 24.5038 | 21.1699 | 17.8348 | -2.7548 | -13.8456 | -19.8616
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Leading the Way | Thermal headroom (MW) | 46.31 | 45.7746 | 44.9299 | 43.967 | 42.6709 | 39.1889 | 35.448 | 31.0934 | 27.3508 | 23.0927 | 19.9228 | 16.4291 | 12.748 | 9.1018 | 5.6897 | -8.7818 | -15.5353 | -19.9671
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Steady Progression | Thermal headroom (MW) | 46.31 | 46.6386 | 46.6943 | 46.7185 | 46.6557 | 45.6769 | 44.7493 | 43.5732 | 42.5645 | 41.3928 | 39.7927 | 38.3233 | 36.7587 | 35.1016 | 33.422 | 22.045 | 16.2859 | 14.2609
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | System Transformation | Thermal headroom (MW) | 46.31 | 46.4919 | 46.3977 | 46.2339 | 45.8873 | 44.9112 | 43.8309 | 42.4206 | 41.2622 | 40.0216 | 38.4383 | 36.9361 | 35.2675 | 33.6662 | 32.0257 | 20.7324 | 11.9297 | 8.8318
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | WPD Best View | Thermal headroom (MW) | 46.31 | 46.2192 | 45.8513 | 45.3025 | 44.5273 | 42.6261 | 40.7492 | 38.6813 | 36.9455 | 35.0925 | 32.4588 | 29.7523 | 26.6338 | 23.5922 | 20.3176 | 0.038807 | -12.7228 | -19.0188
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Consumer Transformation | Thermal headroom (MW) | 8.35 | 8.07 | 7.69 | 7.17 | 6.56 | 5.23 | 4.01 | 2.92 | 1.82 | 0.59 | -1.46 | -3.54 | -5.64 | -7.71 | -9.73 | -22.57 | -31.44 | -37.19
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Leading the Way | Thermal headroom (MW) | 8.35 | 7.57 | 6.72 | 5.77 | 4.67 | 2.49 | 0.42 | -1.59 | -3.57 | -5.71 | -7.77 | -9.98 | -12.24 | -14.43 | -16.48 | -25.77 | -31.45 | -36.11
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Steady Progression | Thermal headroom (MW) | 8.35 | 8.36 | 8.27 | 8.16 | 8.03 | 7.46 | 6.9 | 6.32 | 5.75 | 5.18 | 4.37 | 3.54 | 2.71 | 1.86 | 0.98 | -5.02 | -8.12 | -9.59
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | System Transformation | Thermal headroom (MW) | 8.35 | 8.28 | 8.11 | 7.88 | 7.57 | 7.18 | 6.77 | 6.34 | 5.83 | 5.33 | 4.6 | 3.77 | 2.94 | 2 | 1.02 | -5.2 | -10.09 | -12.78
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | WPD Best View | Thermal headroom (MW) | 8.35 | 8.07 | 7.69 | 7.17 | 6.56 | 5.23 | 4.01 | 2.92 | 1.82 | 0.59 | -1.46 | -3.54 | -5.64 | -7.71 | -9.73 | -22.57 | -31.44 | -37.19
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Consumer Transformation | Thermal headroom (MW) | 0.47 | 0.48 | 0.44 | 0.36 | 0.25 | -0.25 | -0.78 | -1.33 | -1.89 | -2.5 | -3.04 | -3.64 | -4.36 | -5 | -5.66 | -9.72 | -11.37 | -12.29
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Leading the Way | Thermal headroom (MW) | 0.47 | 0.42 | 0.3 | 0.16 | -0.03 | -0.77 | -1.72 | -2.74 | -3.94 | -5.32 | -5.9 | -6.58 | -7.34 | -8.1 | -8.83 | -12.27 | -13.75 | -14.8
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Steady Progression | Thermal headroom (MW) | 0.47 | 0.53 | 0.54 | 0.54 | 0.53 | 0.36 | 0.18 | -0.04 | -0.28 | -0.6 | -1.06 | -1.41 | -1.78 | -2.18 | -2.58 | -5.67 | -6.92 | -7.29
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | System Transformation | Thermal headroom (MW) | 0.47 | 0.48 | 0.44 | 0.39 | 0.31 | 0.1 | -0.16 | -0.44 | -0.79 | -1.15 | -1.6 | -1.88 | -2.3 | -2.61 | -3 | -5.96 | -8.77 | -9.77
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | WPD Best View | Thermal headroom (MW) | 0.47 | 0.46 | 0.4 | 0.29 | 0.18 | -0.09 | -0.38 | -0.67 | -1 | -1.32 | -1.81 | -2.12 | -2.63 | -3.04 | -3.65 | -7.47 | -10.5 | -11.65
Walpole 132kV | Bourne | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Consumer Transformation | Thermal headroom (MW) | 10.45 | 10.34 | 10.11 | 9.82 | 9.4 | 8.77 | 7.72 | 6.45 | 5.63 | 4.75 | 3.65 | 2.23 | 0.58 | -1 | -2.56 | -11.86 | -16.75 | -19.1
Walpole 132kV | Bourne | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Leading the Way | Thermal headroom (MW) | 10.45 | 10.18 | 9.77 | 9.34 | 8.72 | 7.74 | 5.99 | 3.7 | 2.35 | 0.71 | -1 | -2.75 | -4.55 | -6.33 | -7.99 | -13.63 | -15.9 | -17.11
Walpole 132kV | Bourne | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Steady Progression | Thermal headroom (MW) | 10.45 | 10.56 | 10.56 | 10.56 | 10.5 | 10.26 | 9.77 | 9.08 | 8.61 | 8.11 | 7.48 | 6.82 | 6.13 | 5.4 | 4.67 | 0.18 | -2.76 | -3.65
Walpole 132kV | Bourne | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | System Transformation | Thermal headroom (MW) | 10.45 | 10.51 | 10.45 | 10.37 | 10.2 | 9.95 | 9.27 | 8.3 | 7.76 | 7.16 | 6.45 | 5.7 | 4.93 | 4.18 | 3.49 | -1.62 | -4.54 | -5.26
Walpole 132kV | Bourne | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | WPD Best View | Thermal headroom (MW) | 10.45 | 10.34 | 10.11 | 9.82 | 9.4 | 8.78 | 7.72 | 6.46 | 5.64 | 4.76 | 3.69 | 2.29 | 0.65 | -0.92 | -2.47 | -11.81 | -16.74 | -19.1
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Consumer Transformation | Thermal headroom (MW) | 12.16 | 12.31 | 12.37 | 12.42 | 12.44 | 11.74 | 11.43 | 10.97 | 10.71 | 10.4 | 9.98 | 9.57 | 9.16 | 8.74 | 8.33 | 5.8 | 4.8 | 4.53
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Leading the Way | Thermal headroom (MW) | 12.16 | 12.22 | 12.2 | 12.18 | 12.1 | 10.91 | 10.41 | 9.64 | 9.26 | 8.81 | 8.41 | 7.97 | 7.59 | 7.22 | 6.89 | 5.54 | 5.23 | 5.4
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Steady Progression | Thermal headroom (MW) | 12.16 | 12.34 | 12.42 | 12.5 | 12.57 | 12.13 | 12.03 | 11.83 | 11.75 | 11.62 | 11.46 | 11.31 | 11.12 | 10.9 | 10.68 | 9.12 | 8.37 | 8.37
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | System Transformation | Thermal headroom (MW) | 12.16 | 12.33 | 12.41 | 12.48 | 12.53 | 11.94 | 11.74 | 11.38 | 11.24 | 11.1 | 10.93 | 10.72 | 10.52 | 10.26 | 10.02 | 8.43 | 7.78 | 7.96
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | WPD Best View | Thermal headroom (MW) | 12.16 | 12.31 | 12.37 | 12.42 | 12.44 | 11.74 | 11.44 | 10.99 | 10.73 | 10.42 | 10.01 | 9.6 | 9.19 | 8.78 | 8.37 | 5.92 | 4.93 | 4.67
Walpole 132kV | Bourne | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Consumer Transformation | Thermal headroom (MW) | -7.84 | -7.82 | -7.86 | -7.95 | -8.11 | -8.37 | -8.63 | -8.9 | -9.18 | -9.47 | -9.82 | -10.26 | -10.74 | -11.34 | -11.98 | -15.92 | -18.14 | -19.24
Walpole 132kV | Bourne | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Leading the Way | Thermal headroom (MW) | -7.84 | -7.86 | -7.97 | -8.11 | -8.34 | -8.75 | -9.23 | -9.78 | -10.3 | -10.85 | -11.27 | -11.8 | -12.44 | -13.08 | -13.67 | -16.39 | -17.64 | -18.33
Walpole 132kV | Bourne | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Steady Progression | Thermal headroom (MW) | -7.84 | -7.74 | -7.7 | -7.68 | -7.69 | -7.82 | -7.97 | -8.13 | -8.32 | -8.53 | -8.81 | -9.1 | -9.39 | -9.7 | -10 | -11.86 | -12.78 | -13.3
Walpole 132kV | Bourne | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | System Transformation | Thermal headroom (MW) | -7.84 | -7.76 | -7.75 | -7.76 | -7.82 | -7.88 | -7.96 | -8.07 | -8.22 | -8.41 | -8.67 | -8.96 | -9.25 | -9.53 | -9.77 | -11.13 | -12.62 | -13.15
Walpole 132kV | Bourne | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | WPD Best View | Thermal headroom (MW) | -7.84 | -7.82 | -7.86 | -7.95 | -8.11 | -8.37 | -8.63 | -8.9 | -9.18 | -9.47 | -9.82 | -10.26 | -10.74 | -11.34 | -11.98 | -15.92 | -18.14 | -19.24
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Consumer Transformation | Thermal headroom (MW) | -1.53 | -1.79 | -2.01 | -2.29 | -2.7 | -3.45 | -4.18 | -4.99 | -5.85 | -6.9 | -8.27 | -9.62 | -11.05 | -12.41 | -13.59 | -19.64 | -22.24 | -23.51
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Leading the Way | Thermal headroom (MW) | -1.53 | -1.89 | -2.19 | -2.55 | -3.03 | -4.08 | -5.21 | -6.61 | -8.3 | -10.18 | -11.51 | -12.86 | -14.21 | -15.57 | -16.54 | -20.55 | -21.92 | -22.5
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Steady Progression | Thermal headroom (MW) | -1.53 | -1.63 | -1.71 | -1.8 | -1.91 | -2.25 | -2.57 | -2.94 | -3.35 | -3.79 | -4.35 | -4.9 | -5.5 | -6.11 | -6.7 | -11.02 | -12.95 | -13.54
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | System Transformation | Thermal headroom (MW) | -1.53 | -1.68 | -1.8 | -1.94 | -2.13 | -2.47 | -2.82 | -3.29 | -3.82 | -4.42 | -5 | -5.61 | -6.23 | -6.86 | -7.34 | -11.72 | -14.27 | -14.93
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | WPD Best View | Thermal headroom (MW) | -1.53 | -1.7 | -1.84 | -1.98 | -2.21 | -2.63 | -3.06 | -3.59 | -4.2 | -4.89 | -5.52 | -6.18 | -7.11 | -8.04 | -8.88 | -13.62 | -15.95 | -16.85
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Consumer Transformation | Thermal headroom (MW) | -14.68 | -14.95 | -15.28 | -15.76 | -16.38 | -17.93 | -19.31 | -20.66 | -22.04 | -24.53 | -28.51 | -32.17 | -35.87 | -39.57 | -43.17 | -57.67 | -69.54 | -77.02
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Leading the Way | Thermal headroom (MW) | -14.68 | -15.38 | -16.14 | -16.98 | -18.08 | -20.48 | -22.64 | -24.99 | -28.12 | -32.43 | -35.64 | -38.61 | -41.79 | -44.95 | -47.74 | -57.13 | -61.56 | -64.25
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Steady Progression | Thermal headroom (MW) | -14.68 | -14.75 | -14.88 | -15.08 | -15.3 | -16.06 | -16.72 | -17.44 | -18.15 | -19.69 | -21.53 | -22.69 | -23.89 | -25.27 | -26.87 | -35.44 | -39.37 | -41.08
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | System Transformation | Thermal headroom (MW) | -14.68 | -14.77 | -14.99 | -15.24 | -15.54 | -16.07 | -16.49 | -16.97 | -17.49 | -18.74 | -20.52 | -22.05 | -23.64 | -25.31 | -26.91 | -36.28 | -41.37 | -43.05
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | WPD Best View | Thermal headroom (MW) | -14.68 | -14.77 | -14.99 | -15.24 | -15.54 | -16.07 | -16.49 | -16.97 | -17.49 | -18.74 | -20.52 | -22.05 | -23.64 | -25.31 | -26.91 | -36.28 | -41.36 | -43.04
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Consumer Transformation | Thermal headroom (MW) | 5.43 | 5.43 | 5.33 | 5.15 | 4.82 | 3.89 | 2.63 | 0.88 | -1.13 | -3.56 | -7.42 | -11.3 | -15.23 | -19.06 | -22.94 | -38.23 | -51.28 | -60.6
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Leading the Way | Thermal headroom (MW) | 5.43 | 5.27 | 5 | 4.68 | 4.08 | 2.37 | -0.24 | -3.8 | -7.71 | -11.64 | -14.57 | -17.79 | -21.22 | -24.56 | -27.68 | -38.37 | -44.28 | -48.69
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Steady Progression | Thermal headroom (MW) | 5.43 | 5.59 | 5.63 | 5.65 | 5.63 | 5.29 | 4.74 | 3.94 | 3.15 | 1.86 | 0.1 | -1.11 | -2.39 | -3.89 | -5.62 | -15.67 | -20.95 | -22.86
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | System Transformation | Thermal headroom (MW) | 5.43 | 5.54 | 5.52 | 5.47 | 5.34 | 5.09 | 4.47 | 3.57 | 2.71 | 1.79 | 0.2 | -1.51 | -3.32 | -5.22 | -7.16 | -18.3 | -24.62 | -26.96
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | WPD Best View | Thermal headroom (MW) | 5.43 | 5.54 | 5.52 | 5.47 | 5.34 | 5.12 | 4.53 | 3.66 | 2.84 | 1.98 | 0.39 | -1.32 | -3.13 | -5.02 | -6.94 | -18.02 | -24.38 | -26.73
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Consumer Transformation | Thermal headroom (MW) | 7.6 | 7.65 | 7.59 | 7.47 | 7.23 | 6.44 | 5.67 | 4.87 | 4.08 | 2.41 | 0.93 | -0.5 | -2.03 | -3.7 | -5.28 | -14.98 | -20.44 | -23.63
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Leading the Way | Thermal headroom (MW) | 7.6 | 7.51 | 7.3 | 7.04 | 6.64 | 5.2 | 3.64 | 2.06 | 0.66 | -2.08 | -3.93 | -5.92 | -7.61 | -9.24 | -10.86 | -17.87 | -21.01 | -23.39
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Steady Progression | Thermal headroom (MW) | 7.6 | 7.8 | 7.88 | 7.94 | 7.98 | 7.62 | 7.27 | 6.89 | 6.49 | 5.63 | 4.88 | 4.12 | 3.39 | 2.64 | 1.88 | -2.82 | -4.93 | -5.92
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | System Transformation | Thermal headroom (MW) | 7.6 | 7.75 | 7.78 | 7.79 | 7.74 | 7.36 | 6.94 | 6.47 | 5.93 | 4.64 | 3.82 | 2.95 | 2.18 | 1.44 | 0.77 | -4.3 | -7.29 | -8.56
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | WPD Best View | Thermal headroom (MW) | 7.6 | 7.75 | 7.78 | 7.79 | 7.74 | 7.36 | 6.94 | 6.47 | 5.93 | 4.64 | 3.82 | 2.95 | 2.18 | 1.44 | 0.77 | -4.3 | -7.29 | -8.56
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Consumer Transformation | Thermal headroom (MW) | 6.288 | 5.988 | 5.528 | 4.958 | 4.208 | 2.468 | 0.558 | -1.612 | -4.092 | -6.242 | -9.412 | -12.432 | -15.442 | -18.292 | -20.942 | -36.292 | -44.122 | -47.592
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Leading the Way | Thermal headroom (MW) | 6.288 | 5.408 | 4.348 | 3.228 | 1.888 | -0.982 | -3.982 | -7.622 | -11.542 | -14.872 | -18.352 | -21.702 | -25.042 | -28.102 | -30.812 | -39.852 | -42.862 | -44.192
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Steady Progression | Thermal headroom (MW) | 6.288 | 6.388 | 6.348 | 6.308 | 6.238 | 5.418 | 4.588 | 3.528 | 2.268 | 1.268 | -0.032 | -1.242 | -2.512 | -3.872 | -5.222 | -13.092 | -16.762 | -17.602
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | System Transformation | Thermal headroom (MW) | 6.288 | 6.298 | 6.168 | 5.998 | 5.668 | 4.698 | 3.488 | 1.978 | 0.278 | -1.012 | -2.582 | -4.102 | -5.692 | -7.342 | -8.922 | -17.432 | -20.222 | -20.762
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | WPD Best View | Thermal headroom (MW) | 6.288 | 6.298 | 6.168 | 5.998 | 5.668 | 4.688 | 3.458 | 1.918 | 0.188 | -1.132 | -2.712 | -4.232 | -5.832 | -7.492 | -9.072 | -17.932 | -20.762 | -21.342
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Consumer Transformation | Thermal headroom (MW) | 7.91 | 7.98 | 8.08 | 8.16 | 8.19 | 7.77 | 7.57 | 7.52 | 7.46 | 7.29 | 7.04 | 6.54 | 5.81 | 5.36 | 4.9 | 2.51 | 1.65 | 1.77
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Leading the Way | Thermal headroom (MW) | 7.91 | 7.93 | 8.01 | 8.07 | 8.07 | 7.37 | 7.03 | 6.92 | 6.82 | 6.48 | 6.09 | 5.77 | 5.33 | 4.91 | 4.56 | 3.12 | 2.84 | 3.44
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Steady Progression | Thermal headroom (MW) | 7.91 | 8.05 | 8.18 | 8.31 | 8.42 | 8.16 | 8.09 | 8.08 | 8.06 | 7.98 | 7.85 | 7.78 | 7.71 | 7.63 | 7.54 | 5.95 | 4.77 | 4.58
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | System Transformation | Thermal headroom (MW) | 7.91 | 8.01 | 8.14 | 8.26 | 8.35 | 8 | 7.86 | 7.88 | 7.88 | 7.77 | 7.58 | 7.49 | 7.39 | 6.93 | 6.47 | 4.15 | 3.14 | 3.56
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | WPD Best View | Thermal headroom (MW) | 7.91 | 8.01 | 8.14 | 8.26 | 8.35 | 8 | 7.86 | 7.88 | 7.88 | 7.77 | 7.58 | 7.49 | 7.39 | 6.93 | 6.47 | 4.15 | 3.14 | 3.56
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Consumer Transformation | Thermal headroom (MW) | 1.5064 | 1.5564 | 1.5764 | 1.5764 | 1.5364 | 1.2764 | 0.9964 | 0.7164 | 0.4064 | 0.0564 | -0.4736 | -1.0336 | -1.6036 | -2.0736 | -2.5536 | -4.5236 | -5.2436 | -5.6136
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Leading the Way | Thermal headroom (MW) | 1.5064 | 1.5364 | 1.5164 | 1.4864 | 1.4164 | 1.0264 | 0.5464 | 0.0064 | -0.6036 | -1.3036 | -1.6536 | -2.0136 | -2.4036 | -2.7736 | -3.0736 | -4.7636 | -5.2636 | -5.4536
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Steady Progression | Thermal headroom (MW) | 1.5064 | 1.5564 | 1.5664 | 1.5764 | 1.5764 | 1.4364 | 1.2564 | 1.0764 | 0.8864 | 0.6964 | 0.4064 | 0.1364 | -0.1736 | -0.5636 | -0.9536 | -3.6336 | -4.6236 | -4.9036
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | System Transformation | Thermal headroom (MW) | 1.5064 | 1.5464 | 1.5464 | 1.5464 | 1.5164 | 1.4464 | 1.3664 | 1.2764 | 1.1564 | 1.0164 | 0.8164 | 0.6164 | 0.4064 | 0.1964 | 0.0064 | -2.3536 | -4.3336 | -4.7936
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | WPD Best View | Thermal headroom (MW) | 1.5064 | 1.5464 | 1.5464 | 1.5464 | 1.5164 | 1.4464 | 1.3464 | 1.2464 | 1.1164 | 0.9764 | 0.7664 | 0.5664 | 0.3564 | 0.1364 | -0.0536 | -2.5636 | -4.5436 | -5.0236
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Consumer Transformation | Thermal headroom (MW) | 27.4106 | 27.0836 | 26.2422 | 24.9749 | 23.1295 | 19.4878 | 15.1777 | 10.9285 | 6.8333 | 1.8312 | -15.7927 | -34.629 | -54.1478 | -72.9983 | -93.2377 | -157.5625 | -265.2474 | -349.127
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Leading the Way | Thermal headroom (MW) | 27.4106 | 26.3957 | 24.6155 | 22.4443 | 18.0782 | 10.7874 | 1.8623 | -9.8237 | -33.9624 | -60.114 | -69.774 | -85.893 | -107.4915 | -130.4644 | -152.4406 | -217.9074 | -283.3576 | -347.5665
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Steady Progression | Thermal headroom (MW) | 27.4106 | 28.0604 | 28.1578 | 28.0901 | 27.8642 | 26.5947 | 24.8901 | 23.0405 | 21.2205 | 19.2165 | 16.53 | 13.7749 | 10.8194 | 7.3538 | 3.8342 | -20.5207 | -35.3335 | -42.7143
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | System Transformation | Thermal headroom (MW) | 27.4106 | 27.8222 | 27.6244 | 27.1826 | 26.4427 | 25.4401 | 23.6367 | 21.667 | 19.8076 | 17.589 | 14.8294 | 11.8794 | 8.8333 | 4.6506 | 0.74974 | -25.4159 | -41.3569 | -45.2103
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | WPD Best View | Thermal headroom (MW) | 27.4106 | 27.4557 | 26.9005 | 25.9896 | 24.594 | 22.4321 | 19.5223 | 16.6337 | 13.9539 | 10.9723 | 6.8414 | 1.5134 | -4.4668 | -10.7993 | -16.9928 | -54.8658 | -76.637 | -85.1396
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Consumer Transformation | Thermal headroom (MW) | 4.93 | 4.83 | 4.52 | 4.08 | 3.33 | 1.77 | -0.08 | -1.61 | -3.18 | -4.87 | -7.83 | -11.1 | -14.51 | -17.84 | -21.12 | -38.35 | -48.73 | -54.04
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Leading the Way | Thermal headroom (MW) | 4.93 | 4.45 | 3.74 | 2.94 | 1.57 | -1.15 | -4.11 | -6.89 | -9.7 | -12.8 | -16.13 | -19.61 | -23.11 | -26.56 | -29.83 | -41.28 | -46.25 | -48.8
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Steady Progression | Thermal headroom (MW) | 4.93 | 5.18 | 5.22 | 5.22 | 5.13 | 4.46 | 3.68 | 3.01 | 2.2 | 1.3 | 0.16 | -1.02 | -2.29 | -3.6 | -4.95 | -13.22 | -19.23 | -22.36
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | System Transformation | Thermal headroom (MW) | 4.93 | 5.06 | 4.96 | 4.79 | 4.47 | 3.72 | 2.64 | 1.76 | 0.77 | -0.35 | -1.61 | -2.96 | -4.37 | -5.74 | -7 | -16.25 | -21.12 | -22.86
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | WPD Best View | Thermal headroom (MW) | 4.93 | 4.86 | 4.57 | 4.17 | 3.49 | 2.02 | 0.26 | -1.19 | -2.69 | -4.31 | -6.95 | -9.99 | -13.25 | -16.42 | -19.55 | -36 | -45.92 | -50.84
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Consumer Transformation | Thermal headroom (MW) | 6.13 | 6.05 | 5.93 | 5.77 | 5.56 | 5.08 | 4.58 | 4.08 | 3.53 | 2.76 | -1.54 | -5.81 | -10.11 | -14.36 | -19.05 | -30.4 | -58.4 | -81.63
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Leading the Way | Thermal headroom (MW) | 6.13 | 5.99 | 5.75 | 5.46 | 4.7 | 3.5 | 2.09 | -0.02 | -6.16 | -12.75 | -14.34 | -17.72 | -22.71 | -28.16 | -33.4 | -47.88 | -65.42 | -83.83
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Steady Progression | Thermal headroom (MW) | 6.13 | 6.17 | 6.17 | 6.14 | 6.1 | 5.98 | 5.82 | 5.66 | 5.49 | 5.31 | 5.04 | 4.78 | 4.48 | 4.06 | 3.63 | 0.65 | -0.95 | -1.88
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | System Transformation | Thermal headroom (MW) | 6.13 | 6.16 | 6.12 | 6.06 | 5.97 | 5.9 | 5.78 | 5.66 | 5.5 | 5.31 | 5.06 | 4.79 | 4.51 | 4.04 | 3.59 | 0.29 | -1.52 | -1.89
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | WPD Best View | Thermal headroom (MW) | 6.13 | 6.16 | 6.12 | 6.06 | 5.97 | 5.9 | 5.78 | 5.66 | 5.5 | 5.31 | 5.06 | 4.79 | 4.51 | 4.03 | 3.57 | 0.24 | -1.6 | -1.98
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Consumer Transformation | Thermal headroom (MW) | 3.3 | 3.36 | 3.35 | 3.26 | 3.16 | 2.96 | 2.75 | 2.56 | 2.36 | 2.13 | 1.85 | 1.12 | 0.17 | -0.39 | -0.91 | -3.57 | -5.33 | -6.05
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Leading the Way | Thermal headroom (MW) | 3.3 | 3.31 | 3.25 | 3.11 | 2.96 | 2.68 | 2.39 | 2.1 | 1.76 | 1.37 | 1.04 | 0.51 | -0.02 | -0.51 | -0.96 | -2.93 | -3.88 | -4.11
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Steady Progression | Thermal headroom (MW) | 3.3 | 3.4 | 3.44 | 3.43 | 3.45 | 3.38 | 3.3 | 3.22 | 3.12 | 3.01 | 2.84 | 2.66 | 2.48 | 2.27 | 2.07 | -0.3 | -1.89 | -2.63
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | System Transformation | Thermal headroom (MW) | 3.3 | 3.38 | 3.39 | 3.35 | 3.33 | 3.29 | 3.24 | 3.19 | 3.13 | 3.02 | 2.85 | 2.66 | 2.47 | 1.92 | 1.4 | -1.18 | -3.02 | -3.24
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | WPD Best View | Thermal headroom (MW) | 3.3 | 3.36 | 3.35 | 3.28 | 3.19 | 3.04 | 2.89 | 2.75 | 2.6 | 2.42 | 2.15 | 1.55 | 0.79 | 0.26 | -0.23 | -3.09 | -5.03 | -5.67
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Consumer Transformation | Thermal headroom (MW) | -13.78 | -13.58 | -13.96 | -14.36 | -15.11 | -17.08 | -18.78 | -20.99 | -22.91 | -25.07 | -28.39 | -32.18 | -35.96 | -39.21 | -42.42 | -55.9 | -61.33 | -62.94
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Leading the Way | Thermal headroom (MW) | -13.78 | -14.13 | -15.1 | -15.96 | -17.23 | -20.03 | -22.24 | -25.55 | -28.35 | -31.26 | -34.8 | -38.55 | -42.19 | -45.61 | -48.65 | -55.89 | -56.11 | -54.05
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Steady Progression | Thermal headroom (MW) | -13.78 | -13.03 | -12.79 | -12.55 | -12.38 | -13.02 | -13.41 | -14.04 | -14.54 | -15.07 | -15.87 | -16.71 | -17.64 | -18.7 | -19.85 | -28.63 | -33.78 | -34.41
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | System Transformation | Thermal headroom (MW) | -13.78 | -13.23 | -13.23 | -13.23 | -13.37 | -14.14 | -14.67 | -15.76 | -16.51 | -17.32 | -18.46 | -19.74 | -21.12 | -23.04 | -25.07 | -33.98 | -36.1 | -34.77
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | WPD Best View | Thermal headroom (MW) | -13.78 | -13.21 | -13.18 | -13.14 | -13.24 | -13.86 | -14.28 | -15.03 | -15.66 | -16.35 | -17.38 | -18.53 | -19.8 | -21.59 | -23.44 | -32.27 | -34.31 | -32.86
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Consumer Transformation | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Leading the Way | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Steady Progression | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | System Transformation | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | WPD Best View | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Consumer Transformation | Thermal headroom (MW) | 9.23 | 8.92 | 8.24 | 7.67 | 6.74 | 5.45 | 4.23 | 3.1 | 1.98 | 0.87 | -0.92 | -3.6 | -6.37 | -8.73 | -11.05 | -23.72 | -32.32 | -36.59
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Leading the Way | Thermal headroom (MW) | 9.23 | 8.59 | 7.53 | 6.58 | 5.15 | 3.21 | 1.39 | -0.54 | -2.6 | -4.75 | -7.23 | -9.82 | -12.46 | -15 | -17.36 | -25.74 | -30 | -32.15
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Steady Progression | Thermal headroom (MW) | 9.23 | 9.26 | 8.97 | 8.85 | 8.62 | 8.16 | 7.69 | 7.24 | 6.69 | 6.11 | 5.34 | 4.56 | 3.74 | 2.88 | 2.02 | -3.12 | -7.31 | -9.58
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | System Transformation | Thermal headroom (MW) | 9.23 | 9.16 | 8.72 | 8.47 | 8.05 | 7.57 | 7.04 | 6.41 | 5.72 | 4.98 | 4.03 | 3 | 1.95 | 0.6 | -0.66 | -6.07 | -9.51 | -10.67
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | WPD Best View | Thermal headroom (MW) | 9.23 | 9.17 | 8.76 | 8.54 | 8.15 | 7.69 | 7.2 | 6.61 | 5.95 | 5.25 | 4.33 | 3.33 | 2.31 | 0.96 | -0.32 | -5.63 | -9.1 | -10.24
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Consumer Transformation | Thermal headroom (MW) | 14.23 | 14.05 | 13.79 | 13.45 | 13.02 | 12.44 | 12.07 | 11.68 | 11.11 | 10.34 | 9.1 | 7.88 | 6.6 | 5.37 | 4.21 | -0.78 | -3.24 | -4.55
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Leading the Way | Thermal headroom (MW) | 14.23 | 13.91 | 13.49 | 13.01 | 12.58 | 12.09 | 11.43 | 10.54 | 9.64 | 8.64 | 7.36 | 6.05 | 4.76 | 3.54 | 2.43 | -0.36 | -0.74 | -0.26
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Steady Progression | Thermal headroom (MW) | 14.23 | 14.23 | 14.16 | 14.1 | 14.02 | 13.85 | 13.69 | 13.5 | 13.38 | 13.18 | 12.9 | 12.61 | 12.29 | 11.96 | 11.63 | 8.04 | 5.26 | 4.07
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | System Transformation | Thermal headroom (MW) | 14.23 | 14.16 | 14.02 | 13.88 | 13.7 | 13.53 | 13.46 | 13.35 | 13.15 | 12.91 | 12.61 | 12.26 | 11.77 | 11.12 | 10.45 | 6.72 | 5.61 | 5.68
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | WPD Best View | Thermal headroom (MW) | 14.23 | 14.16 | 14.02 | 13.88 | 13.7 | 13.53 | 13.46 | 13.35 | 13.15 | 12.91 | 12.61 | 12.26 | 11.77 | 11.12 | 10.45 | 6.72 | 5.61 | 5.68
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Consumer Transformation | Thermal headroom (MW) | 6.48 | 6.44 | 6.22 | 5.94 | 5.51 | 4.79 | 4.07 | 3.33 | 2.55 | 1.66 | 0.2 | -1.78 | -3.89 | -5.86 | -7.78 | -19.63 | -26.95 | -30.57
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Leading the Way | Thermal headroom (MW) | 6.48 | 6.19 | 5.71 | 5.18 | 4.37 | 2.94 | 1.6 | 0.19 | -1.41 | -3.28 | -5.33 | -7.51 | -9.69 | -11.89 | -13.9 | -21.91 | -25.5 | -27.35
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Steady Progression | Thermal headroom (MW) | 6.48 | 6.69 | 6.73 | 6.75 | 6.73 | 6.47 | 6.18 | 5.87 | 5.5 | 5.03 | 4.38 | 3.71 | 3.01 | 2.28 | 1.55 | -3.74 | -7.8 | -9.77
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | System Transformation | Thermal headroom (MW) | 6.48 | 6.63 | 6.6 | 6.53 | 6.38 | 6.17 | 5.93 | 5.58 | 5.11 | 4.55 | 3.78 | 2.94 | 2.07 | 1.23 | 0.49 | -5.22 | -9.07 | -10.36
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | WPD Best View | Thermal headroom (MW) | 6.48 | 6.65 | 6.64 | 6.6 | 6.49 | 6.24 | 5.95 | 5.59 | 5.11 | 4.56 | 3.79 | 2.98 | 2.15 | 1.33 | 0.6 | -5.1 | -8.76 | -10.13
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Consumer Transformation | Thermal headroom (MW) | 10.26 | 10.16 | 9.85 | 9.38 | 8.76 | 7.92 | 7.06 | 6.24 | 5.37 | 4.41 | 3.32 | 2.18 | 0.81 | -0.78 | -2.31 | -11.85 | -17.32 | -20.07
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Leading the Way | Thermal headroom (MW) | 10.26 | 9.98 | 9.49 | 8.83 | 8.01 | 6.56 | 5.18 | 3.72 | 2.3 | 0.77 | -0.79 | -2.57 | -4.32 | -6 | -7.57 | -13.72 | -16.57 | -18.56
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Steady Progression | Thermal headroom (MW) | 10.26 | 10.38 | 10.34 | 10.24 | 10.1 | 9.72 | 9.32 | 8.9 | 8.41 | 7.9 | 7.23 | 6.53 | 5.81 | 5.07 | 4.33 | 0.59 | -1.7 | -2.76
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | System Transformation | Thermal headroom (MW) | 10.26 | 10.32 | 10.2 | 10 | 9.72 | 9.39 | 8.98 | 8.53 | 8 | 7.37 | 6.61 | 5.8 | 5 | 4.24 | 3.55 | 0.03 | -2.97 | -4.03
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | WPD Best View | Thermal headroom (MW) | 10.26 | 10.38 | 10.34 | 10.24 | 10.1 | 9.72 | 9.32 | 8.9 | 8.41 | 7.9 | 7.23 | 6.53 | 5.81 | 5.07 | 4.33 | 0.59 | -1.7 | -2.76
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Consumer Transformation | Thermal headroom (MW) | 11.59 | 11.55 | 11.4 | 11.17 | 10.84 | 10.17 | 9.5 | 8.83 | 8.15 | 7.35 | 6.09 | 4.67 | 3.21 | 1.82 | 0.48 | -6.44 | -10.35 | -12.44
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Leading the Way | Thermal headroom (MW) | 11.59 | 11.43 | 11.16 | 10.82 | 10.34 | 9.21 | 8 | 6.67 | 5.23 | 3.7 | 2.48 | 1.25 | 0 | -1.21 | -2.28 | -7.38 | -9.66 | -11.14
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Steady Progression | Thermal headroom (MW) | 11.59 | 11.64 | 11.62 | 11.58 | 11.48 | 11.1 | 10.65 | 10.16 | 9.66 | 9.11 | 8.37 | 7.66 | 6.93 | 6.1 | 5.22 | -0.49 | -2.74 | -3.76
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | System Transformation | Thermal headroom (MW) | 11.59 | 11.62 | 11.56 | 11.45 | 11.26 | 11.06 | 10.81 | 10.51 | 10.15 | 9.73 | 9.11 | 8.47 | 7.81 | 7.18 | 6.61 | 1.72 | -2.24 | -3.63
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | WPD Best View | Thermal headroom (MW) | 11.59 | 11.64 | 11.62 | 11.58 | 11.48 | 11.1 | 10.65 | 10.16 | 9.66 | 9.11 | 8.37 | 7.66 | 6.93 | 6.1 | 5.22 | -0.49 | -2.74 | -3.76
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Consumer Transformation | Thermal headroom (MW) | 12.25 | 11.98 | 11.51 | 10.86 | 9.88 | 8.57 | 7.24 | 5.84 | 4.22 | 2.07 | -1.1 | -4.64 | -8.17 | -11.22 | -14.05 | -30.55 | -39.85 | -44.39
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Leading the Way | Thermal headroom (MW) | 12.25 | 11.73 | 10.98 | 9.94 | 8.44 | 6.22 | 3.68 | 0.86 | -2.05 | -5.29 | -8.67 | -12.07 | -15.44 | -18.66 | -21.37 | -31.78 | -36.61 | -38.67
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Steady Progression | Thermal headroom (MW) | 12.25 | 12.3 | 12.19 | 12.02 | 11.77 | 11.21 | 10.62 | 9.95 | 9.19 | 8.37 | 7.25 | 6.13 | 4.94 | 3.71 | 2.37 | -7.21 | -13.01 | -15.65
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | System Transformation | Thermal headroom (MW) | 12.25 | 12.21 | 11.99 | 11.69 | 11.26 | 10.76 | 10.17 | 9.4 | 8.5 | 7.48 | 6.14 | 4.78 | 3.46 | 1.77 | -0.12 | -10.68 | -16.43 | -18.2
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | WPD Best View | Thermal headroom (MW) | 12.25 | 12.3 | 12.18 | 12 | 11.74 | 11.19 | 10.61 | 9.92 | 9.15 | 8.31 | 7.16 | 6 | 4.79 | 3.53 | 2.28 | -7.42 | -13.2 | -15.87
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Consumer Transformation | Thermal headroom (MW) | 6.9 | 6.67 | 6.37 | 5.88 | 4.33 | 2.04 | 0.03 | -1.59 | -3.15 | -4.84 | -7.24 | -9.71 | -12.6 | -15.47 | -18.36 | -32.07 | -39.69 | -43.57
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Leading the Way | Thermal headroom (MW) | 6.9 | 6.38 | 5.78 | 5 | 2.76 | -0.69 | -3.51 | -5.76 | -7.94 | -10.51 | -13.53 | -16.66 | -19.74 | -22.74 | -25.57 | -34.97 | -38.55 | -40.78
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Steady Progression | Thermal headroom (MW) | 6.9 | 6.98 | 6.99 | 6.93 | 6.1 | 4.97 | 4.06 | 3.34 | 2.61 | 1.81 | 0.74 | -0.38 | -1.59 | -2.81 | -4.03 | -9.94 | -12.62 | -14.17
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | System Transformation | Thermal headroom (MW) | 6.9 | 6.88 | 6.79 | 6.6 | 5.49 | 4.1 | 2.86 | 1.96 | 0.96 | -0.14 | -1.57 | -3.04 | -4.54 | -6.01 | -7.37 | -12.91 | -15.67 | -16.5
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | WPD Best View | Thermal headroom (MW) | 6.9 | 6.89 | 6.8 | 6.61 | 5.5 | 4.12 | 2.88 | 1.98 | 0.99 | -0.11 | -1.52 | -2.97 | -4.44 | -5.89 | -7.24 | -12.69 | -15.48 | -16.37
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Consumer Transformation | Thermal headroom (MW) | 16.01 | 16.07 | 16.1 | 16.13 | 16.15 | 16.18 | 16.21 | 16.24 | 16.27 | 16.22 | 16.17 | 16.12 | 16.08 | 16.03 | 15.99 | 15.94 | 16 | 16.1
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Leading the Way | Thermal headroom (MW) | 16.01 | 16.07 | 16.1 | 16.13 | 16.15 | 16.18 | 16.21 | 16.24 | 16.22 | 16.2 | 16.15 | 16.1 | 16.06 | 16.02 | 15.98 | 16 | 16.1 | 16.28
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Steady Progression | Thermal headroom (MW) | 16.01 | 16.07 | 16.1 | 16.13 | 16.16 | 16.19 | 16.22 | 16.24 | 16.27 | 16.3 | 16.33 | 16.36 | 16.38 | 16.41 | 16.44 | 16.32 | 16.27 | 16.33
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | System Transformation | Thermal headroom (MW) | 16.01 | 16.07 | 16.1 | 16.13 | 16.15 | 16.18 | 16.21 | 16.24 | 16.27 | 16.3 | 16.33 | 16.31 | 16.26 | 16.21 | 16.17 | 16.05 | 16.08 | 16.23
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | WPD Best View | Thermal headroom (MW) | 16.01 | 16.07 | 16.1 | 16.13 | 16.15 | 16.18 | 16.21 | 16.24 | 16.27 | 16.3 | 16.33 | 16.31 | 16.26 | 16.21 | 16.17 | 16.05 | 16.08 | 16.23
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Consumer Transformation | Thermal headroom (MW) | 8.238 | 7.948 | 7.608 | 7.228 | 6.688 | 5.978 | 5.288 | 4.548 | 3.838 | 2.938 | 1.318 | -0.312 | -1.992 | -3.592 | -5.152 | -14.152 | -20.002 | -23.702
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Leading the Way | Thermal headroom (MW) | 8.238 | 7.788 | 7.298 | 6.748 | 5.958 | 4.688 | 3.268 | 1.708 | 0.038 | -1.762 | -3.372 | -5.152 | -7.022 | -8.872 | -10.582 | -17.352 | -21.522 | -24.732
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Steady Progression | Thermal headroom (MW) | 8.238 | 8.138 | 8.038 | 7.928 | 7.758 | 7.428 | 7.078 | 6.678 | 6.258 | 5.728 | 5.068 | 4.498 | 3.898 | 3.258 | 2.498 | -2.722 | -5.722 | -7.012
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | System Transformation | Thermal headroom (MW) | 8.238 | 8.058 | 7.868 | 7.668 | 7.348 | 7.058 | 6.728 | 6.278 | 5.748 | 5.268 | 4.478 | 3.838 | 3.048 | 2.398 | 1.478 | -4.302 | -8.522 | -10.612
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | WPD Best View | Thermal headroom (MW) | 8.238 | 8.148 | 8.038 | 7.928 | 7.758 | 7.428 | 7.078 | 6.678 | 6.268 | 5.818 | 5.248 | 4.678 | 4.088 | 3.448 | 2.658 | -2.452 | -5.482 | -6.792
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Consumer Transformation | Thermal headroom (MW) | 10.27 | 10.03 | 9.71 | 9.29 | 8.71 | 7.87 | 7.15 | 6.42 | 5.65 | 4.76 | 1.23 | -2.53 | -6.58 | -10.63 | -14.91 | -29.68 | -49.24 | -63.24
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Leading the Way | Thermal headroom (MW) | 10.27 | 9.71 | 9.1 | 8.35 | 6.65 | 4.28 | 1.93 | -1.23 | -9.6 | -18.6 | -21.83 | -27.54 | -35.42 | -43.89 | -52 | -75.19 | -100.97 | -126.81
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Steady Progression | Thermal headroom (MW) | 10.27 | 10.25 | 10.18 | 10.1 | 10.01 | 9.65 | 9.27 | 8.86 | 8.41 | 4.92 | 0.61 | 0.03 | -0.71 | -2.39 | -3.04 | -7.58 | -11.24 | -13.21
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | System Transformation | Thermal headroom (MW) | 10.27 | 10.07 | 9.89 | 9.62 | 9.22 | 8.73 | 8.18 | 7.51 | 6.66 | 5.98 | 3.4 | 2.32 | 0.02 | -1.3 | -3.37 | -12.15 | -21.73 | -27.23
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | WPD Best View | Thermal headroom (MW) | 10.27 | 10.25 | 10.18 | 10.1 | 10.01 | 9.65 | 9.27 | 8.86 | 8.41 | 4.92 | 0.61 | 0.03 | -0.71 | -2.4 | -3.06 | -7.61 | -11.25 | -13.21
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Consumer Transformation | Thermal headroom (MW) | 2.54 | 2.59 | 2.58 | 2.53 | 2.45 | 2.14 | 1.82 | 1.52 | 1.25 | 0.96 | 0.19 | -0.71 | -1.61 | -2.51 | -3.45 | -6.48 | -10.28 | -13.13
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Leading the Way | Thermal headroom (MW) | 2.54 | 2.53 | 2.46 | 2.35 | 2.17 | 1.74 | 1.24 | 0.59 | -0.37 | -1.5 | -2.01 | -2.69 | -3.55 | -4.44 | -5.3 | -8.26 | -10.53 | -12.68
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Steady Progression | Thermal headroom (MW) | 2.54 | 2.64 | 2.67 | 2.69 | 2.71 | 2.57 | 2.44 | 2.29 | 2.15 | 1.98 | 1.7 | 1.43 | 1.14 | 0.83 | 0.44 | -2.05 | -2.83 | -3.16
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | System Transformation | Thermal headroom (MW) | 2.54 | 2.61 | 2.62 | 2.61 | 2.58 | 2.54 | 2.49 | 2.43 | 2.36 | 2.28 | 2.04 | 1.79 | 1.53 | 1.3 | 1.09 | -1.05 | -2.75 | -3.24
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | WPD Best View | Thermal headroom (MW) | 2.54 | 2.62 | 2.65 | 2.65 | 2.64 | 2.57 | 2.5 | 2.41 | 2.33 | 2.23 | 2.01 | 1.79 | 1.54 | 1.3 | 1.08 | -1.18 | -2.61 | -3.07
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Consumer Transformation | Thermal headroom (MW) | 26.04 | 25.35 | 24.68 | 23.77 | 22.37 | 20.29 | 18.07 | 15.03 | 11.36 | 7 | -0.4 | -7.89 | -15.42 | -22.65 | -29.73 | -55.62 | -76.19 | -88.88
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Leading the Way | Thermal headroom (MW) | 26.04 | 25.05 | 23.3 | 21.72 | 19.53 | 15.95 | 11.9 | 7.11 | 1.47 | -4.95 | -11.4 | -18.43 | -25.53 | -32.31 | -38.49 | -54.63 | -60.42 | -61.39
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Steady Progression | Thermal headroom (MW) | 26.04 | 26.45 | 26.55 | 26.58 | 26.46 | 25.93 | 25.35 | 24.76 | 24.15 | 22.81 | 20.82 | 18.85 | 16.69 | 13.79 | 10.89 | -6.74 | -19.88 | -24.87
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | System Transformation | Thermal headroom (MW) | 26.04 | 26.21 | 26.05 | 25.77 | 25.24 | 24.76 | 24.23 | 23.61 | 22.75 | 21.59 | 19 | 16.02 | 12.68 | 9.07 | 5.31 | -13.18 | -20.39 | -22.24
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | WPD Best View | Thermal headroom (MW) | 26.04 | 25.35 | 24.68 | 23.77 | 22.37 | 20.29 | 18.07 | 15.03 | 11.36 | 7 | -0.4 | -7.89 | -15.42 | -22.65 | -29.73 | -55.62 | -76.19 | -88.88
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Consumer Transformation | Thermal headroom (MW) | 78.54 | 78.0209 | 77.1775 | 76.1242 | 74.4172 | 71.8381 | 69.4953 | 66.9907 | 64.3174 | 61.0899 | 54.4702 | 46.7757 | 38.8058 | 31.1973 | 23.5371 | -8.0222 | -35.0072 | -51.8982
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Leading the Way | Thermal headroom (MW) | 78.54 | 77.268 | 75.6192 | 73.7228 | 70.4739 | 66.337 | 62.5349 | 58.1282 | 52.2805 | 44.596 | 37.9502 | 30.8536 | 23.0395 | 15.2511 | 8.2261 | -12.0816 | -21.6415 | -27.1289
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Steady Progression | Thermal headroom (MW) | 78.54 | 78.9049 | 78.9459 | 78.9284 | 78.6714 | 77.8953 | 77.1414 | 76.1729 | 75.0319 | 72.4479 | 69.0884 | 67.078 | 64.8602 | 62.225 | 59.9932 | 45.7847 | 35.5501 | 31.3197
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | System Transformation | Thermal headroom (MW) | 78.54 | 78.4685 | 78.1523 | 77.6534 | 76.7149 | 75.8512 | 74.7887 | 73.3183 | 71.533 | 69.3877 | 65.7131 | 63.2226 | 59.6072 | 56.6007 | 52.9746 | 36.2378 | 25.7002 | 21.7625
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | WPD Best View | Thermal headroom (MW) | 78.54 | 78.0209 | 77.1775 | 76.1242 | 74.4172 | 71.8381 | 69.4953 | 66.9907 | 64.3174 | 61.0899 | 54.4702 | 46.7757 | 38.8058 | 31.1973 | 23.5371 | -8.0222 | -35.0072 | -51.8982
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Consumer Transformation | Thermal headroom (MW) | 6.84 | 6.8 | 6.58 | 6.27 | 5.83 | 4.98 | 4.1 | 3.19 | 2.23 | 0.82 | -1.65 | -4.43 | -7.25 | -10.07 | -12.68 | -28.13 | -37.71 | -42.56
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Leading the Way | Thermal headroom (MW) | 6.84 | 6.45 | 5.85 | 5.13 | 4.03 | 2.39 | 0.83 | -0.85 | -2.49 | -5.47 | -8.99 | -12.18 | -15.48 | -18.73 | -21.5 | -32.24 | -36.84 | -39.82
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Steady Progression | Thermal headroom (MW) | 6.84 | 7.11 | 7.22 | 7.28 | 7.3 | 7.09 | 6.84 | 6.55 | 6.14 | 5.46 | 4.42 | 3.44 | 2.35 | 1.22 | 0.18 | -6.3 | -11.09 | -13.35
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | System Transformation | Thermal headroom (MW) | 6.84 | 7.03 | 7.03 | 6.97 | 6.84 | 6.63 | 6.37 | 5.91 | 5.34 | 4.3 | 2.86 | 1.52 | 0.15 | -1.19 | -2.44 | -10.55 | -14.5 | -15.73
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | WPD Best View | Thermal headroom (MW) | 6.84 | 6.8 | 6.58 | 6.27 | 5.83 | 4.98 | 4.1 | 3.19 | 2.23 | 0.82 | -1.65 | -4.43 | -7.25 | -10.07 | -12.68 | -28.13 | -37.71 | -42.56
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Consumer Transformation | Thermal headroom (MW) | 6.21 | 6.15 | 5.9 | 5.55 | 4.98 | 4.1 | 3.18 | 2.2 | 1.17 | 0.05 | -1.29 | -3.53 | -6.12 | -8.28 | -10.46 | -24.49 | -33.78 | -38.55
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Leading the Way | Thermal headroom (MW) | 6.21 | 5.89 | 5.34 | 4.71 | 3.66 | 2.06 | 0.5 | -1.21 | -2.89 | -5.07 | -7.42 | -9.88 | -12.42 | -14.94 | -17.3 | -26.96 | -31.97 | -34.55
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Steady Progression | Thermal headroom (MW) | 6.21 | 6.48 | 6.57 | 6.62 | 6.62 | 6.36 | 6.05 | 5.59 | 5.06 | 4.44 | 3.64 | 2.79 | 1.88 | 0.93 | -0.03 | -5.83 | -9.86 | -12.12
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | System Transformation | Thermal headroom (MW) | 6.21 | 6.41 | 6.41 | 6.34 | 6.18 | 5.94 | 5.53 | 4.99 | 4.33 | 3.53 | 2.67 | 1.71 | 0.73 | -0.55 | -1.88 | -7.65 | -11.46 | -12.93
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | WPD Best View | Thermal headroom (MW) | 6.21 | 6.15 | 5.9 | 5.55 | 4.98 | 4.1 | 3.18 | 2.2 | 1.17 | 0.05 | -1.29 | -3.53 | -6.12 | -8.28 | -10.46 | -24.49 | -33.78 | -38.55
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Consumer Transformation | Thermal headroom (MW) | 12.11 | 11.96 | 11.73 | 11.47 | 11.09 | 10.33 | 9.7 | 9.02 | 8.26 | 7.4 | 4.77 | 2.15 | -0.46 | -2.99 | -5.63 | -10.8 | -18.19 | -24.01
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Leading the Way | Thermal headroom (MW) | 12.11 | 11.77 | 11.35 | 10.86 | 10.06 | 9.03 | 8.16 | 6.99 | 4.8 | 2.37 | 0.98 | -0.9 | -3.14 | -5.37 | -7.36 | -9.49 | -10.12 | -10.13
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Steady Progression | Thermal headroom (MW) | 12.11 | 12.19 | 12.19 | 12.18 | 12.16 | 11.94 | 11.79 | 11.63 | 11.44 | 10.45 | 9.22 | 8.86 | 8.44 | 7.78 | 7.34 | 4.06 | 1.86 | 1.68
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | System Transformation | Thermal headroom (MW) | 12.11 | 12 | 11.87 | 11.68 | 11.38 | 11.07 | 10.74 | 10.32 | 9.82 | 9.38 | 8.16 | 7.66 | 6.41 | 5.63 | 4.41 | 0.27 | -2.2 | -2.98
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | WPD Best View | Thermal headroom (MW) | 12.11 | 11.96 | 11.73 | 11.47 | 11.09 | 10.33 | 9.7 | 9.02 | 8.26 | 7.4 | 4.77 | 2.15 | -0.46 | -2.99 | -5.63 | -10.8 | -18.19 | -24.01
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Consumer Transformation | Thermal headroom (MW) | -0.696 | -1.316 | -1.996 | -2.806 | -4.276 | -5.906 | -7.286 | -8.766 | -10.326 | -12.176 | -15.856 | -20.326 | -24.886 | -29.366 | -33.956 | -52.826 | -70.336 | -81.486
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Leading the Way | Thermal headroom (MW) | -0.696 | -1.736 | -2.876 | -4.136 | -6.526 | -9.046 | -11.316 | -13.906 | -17.456 | -22.086 | -25.886 | -29.866 | -34.356 | -38.886 | -43.086 | -55.876 | -62.576 | -67.026
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Steady Progression | Thermal headroom (MW) | -0.696 | -0.756 | -0.866 | -1.006 | -1.496 | -2.056 | -2.606 | -3.356 | -4.166 | -5.866 | -8.036 | -9.236 | -10.546 | -12.096 | -13.386 | -21.206 | -27.166 | -30.016
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | System Transformation | Thermal headroom (MW) | -0.696 | -1.056 | -1.416 | -1.866 | -2.796 | -3.396 | -4.086 | -5.046 | -6.206 | -7.506 | -9.786 | -11.156 | -13.206 | -14.676 | -16.566 | -25.906 | -33.106 | -36.246
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | WPD Best View | Thermal headroom (MW) | -0.696 | -1.316 | -1.996 | -2.806 | -4.276 | -5.906 | -7.286 | -8.766 | -10.326 | -12.176 | -15.856 | -20.326 | -24.886 | -29.366 | -33.956 | -52.826 | -70.336 | -81.486
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Consumer Transformation | Thermal headroom (MW) | 19.98 | 19.81 | 19.32 | 18.68 | 17.76 | 16.44 | 15.01 | 13.77 | 12.49 | 10.71 | 6.24 | 1.35 | -3.59 | -8.4 | -13.27 | -34.65 | -53.18 | -63.95
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Leading the Way | Thermal headroom (MW) | 19.98 | 19.35 | 18.36 | 17.27 | 15.52 | 13.07 | 10.71 | 8.17 | 4.52 | 0.52 | -3.57 | -8.04 | -12.71 | -17.35 | -21.74 | -35.84 | -43.19 | -47.08
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Steady Progression | Thermal headroom (MW) | 19.98 | 20.3 | 20.35 | 20.37 | 20.32 | 19.91 | 19.47 | 19.05 | 18.58 | 17.53 | 16.09 | 15.12 | 14.07 | 12.85 | 11.4 | 2.87 | -4.5 | -7.99
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | System Transformation | Thermal headroom (MW) | 19.98 | 20.15 | 20.03 | 19.84 | 19.52 | 19.16 | 18.71 | 18.26 | 17.6 | 16.8 | 15.23 | 13.57 | 11.88 | 10.24 | 8.76 | -1.11 | -6.43 | -8.73
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | WPD Best View | Thermal headroom (MW) | 19.98 | 19.81 | 19.32 | 18.68 | 17.76 | 16.44 | 15.01 | 13.77 | 12.49 | 10.71 | 6.24 | 1.35 | -3.59 | -8.4 | -13.27 | -34.65 | -53.18 | -63.95
Willington 132kV | Derby South | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Consumer Transformation | Thermal headroom (MW) | 9.46 | 9.56 | 9.54 | 9.51 | 9.45 | 9.19 | 8.89 | 8.61 | 8.26 | 7.87 | 7.16 | 6.43 | 5.69 | 5 | 4.31 | 0.89 | -1.3 | -2.42
Willington 132kV | Derby South | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Leading the Way | Thermal headroom (MW) | 9.46 | 9.39 | 9.22 | 9.05 | 8.83 | 8.29 | 7.76 | 7.18 | 6.4 | 5.65 | 5.03 | 4.38 | 3.66 | 2.95 | 2.3 | 0.16 | -0.59 | -0.99
Willington 132kV | Derby South | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Steady Progression | Thermal headroom (MW) | 9.46 | 9.63 | 9.69 | 9.75 | 9.8 | 9.72 | 9.6 | 9.47 | 9.34 | 9.21 | 8.99 | 8.76 | 8.48 | 8.19 | 7.89 | 5.71 | 4.89 | 4.74
Willington 132kV | Derby South | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | System Transformation | Thermal headroom (MW) | 9.46 | 9.61 | 9.65 | 9.68 | 9.69 | 9.65 | 9.62 | 9.59 | 9.52 | 9.43 | 9.19 | 8.87 | 8.53 | 8.17 | 7.79 | 5.76 | 4.79 | 4.72
Willington 132kV | Derby South | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | WPD Best View | Thermal headroom (MW) | 9.46 | 9.56 | 9.54 | 9.51 | 9.45 | 9.19 | 8.89 | 8.61 | 8.26 | 7.87 | 7.16 | 6.43 | 5.69 | 5 | 4.31 | 0.89 | -1.3 | -2.42
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Consumer Transformation | Thermal headroom (MW) | 13.78 | 13.5 | 12.91 | 12.22 | 11.23 | 8.88 | 6.72 | 4.48 | 2.17 | -0.13 | -3.87 | -8.17 | -12.47 | -16.66 | -20.86 | -43.51 | -60.8 | -71.7
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Leading the Way | Thermal headroom (MW) | 13.78 | 12.9 | 11.66 | 10.17 | 8.23 | 4.53 | 1.34 | -2.13 | -5.72 | -9.82 | -14.71 | -19.63 | -24.43 | -29.14 | -33.55 | -50.32 | -60.56 | -68.76
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Steady Progression | Thermal headroom (MW) | 13.78 | 14.04 | 14.02 | 13.99 | 13.89 | 13.13 | 12.46 | 11.65 | 10.67 | 9.65 | 8.26 | 6.84 | 5.37 | 3.84 | 2.33 | -6.14 | -13.48 | -17.03
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | System Transformation | Thermal headroom (MW) | 13.78 | 13.87 | 13.65 | 13.41 | 13.03 | 12.25 | 11.5 | 10.37 | 8.97 | 7.63 | 5.91 | 4.16 | 2.44 | 0.8 | -0.7 | -9.87 | -17.26 | -21.65
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | WPD Best View | Thermal headroom (MW) | 13.78 | 13.5 | 12.91 | 12.22 | 11.23 | 8.88 | 6.72 | 4.48 | 2.17 | -0.13 | -3.87 | -8.17 | -12.47 | -16.66 | -20.86 | -43.51 | -60.8 | -71.7
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Consumer Transformation | Thermal headroom (MW) | 10.4 | 10.29 | 10.03 | 9.65 | 8.56 | 7.62 | 6.79 | 5.81 | 4.45 | 2.72 | -1.38 | -5.91 | -10.14 | -13.96 | -17.95 | -31.25 | -44.2 | -52.3
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Leading the Way | Thermal headroom (MW) | 10.4 | 10.03 | 9.47 | 8.89 | 7.02 | 5.54 | 4.29 | 2.47 | -1.15 | -5.09 | -8.3 | -12.17 | -15.91 | -19.65 | -23.26 | -32.68 | -36.89 | -39.06
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Steady Progression | Thermal headroom (MW) | 10.4 | 10.49 | 10.46 | 10.39 | 9.83 | 9.47 | 9.15 | 8.8 | 8.24 | 6.87 | 5.12 | 4.12 | 3.12 | 1.82 | 0.57 | -6.87 | -11.09 | -12.78
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | System Transformation | Thermal headroom (MW) | 10.4 | 10.28 | 10.1 | 9.8 | 8.86 | 8.49 | 8.13 | 7.53 | 6.5 | 5.46 | 3.42 | 2.12 | 0.34 | -1.49 | -3.88 | -12.88 | -17.91 | -19.79
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | WPD Best View | Thermal headroom (MW) | 10.4 | 10.29 | 10.03 | 9.65 | 8.56 | 7.62 | 6.79 | 5.81 | 4.45 | 2.72 | -1.38 | -5.91 | -10.14 | -13.96 | -17.95 | -31.25 | -44.2 | -52.3
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Consumer Transformation | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Leading the Way | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Steady Progression | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | System Transformation | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | WPD Best View | Thermal headroom (MW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Consumer Transformation | Thermal headroom (MW) | 13.6 | 13.57 | 13.46 | 13.29 | 13.06 | 12.4 | 11.63 | 11.19 | 10.73 | 9.8 | 8.42 | 7.42 | 6.36 | 5.32 | 4.3 | -2.25 | -5.89 | -7.6
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Leading the Way | Thermal headroom (MW) | 13.6 | 13.29 | 12.89 | 12.47 | 11.96 | 10.81 | 9.51 | 8.66 | 7.79 | 6.22 | 4.59 | 3.46 | 2.35 | 1.3 | 0.28 | -3.65 | -5.25 | -6.13
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Steady Progression | Thermal headroom (MW) | 13.6 | 13.71 | 13.72 | 13.73 | 13.73 | 13.41 | 13.05 | 12.86 | 12.65 | 12.18 | 11.56 | 11.11 | 10.66 | 10.2 | 9.75 | 6.9 | 5.58 | 5.06
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | System Transformation | Thermal headroom (MW) | 13.6 | 13.67 | 13.63 | 13.58 | 13.5 | 13.16 | 12.67 | 12.45 | 12.16 | 11.47 | 10.74 | 10.23 | 9.68 | 9.13 | 8.59 | 5.52 | 4.41 | 4.08
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | WPD Best View | Thermal headroom (MW) | 13.6 | 13.57 | 13.46 | 13.29 | 13.06 | 12.4 | 11.63 | 11.19 | 10.73 | 9.8 | 8.42 | 7.42 | 6.36 | 5.32 | 4.3 | -2.25 | -5.89 | -7.6
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Consumer Transformation | Thermal headroom (MW) | 10.476 | 10.176 | 9.746 | 9.236 | 8.606 | 7.476 | 6.446 | 5.386 | 4.266 | 2.926 | 0.186 | -2.464 | -5.154 | -7.764 | -10.324 | -25.324 | -35.204 | -40.344
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Leading the Way | Thermal headroom (MW) | 10.476 | 9.586 | 8.506 | 7.406 | 6.066 | 4.196 | 2.396 | 0.476 | -1.504 | -3.754 | -6.654 | -9.534 | -12.474 | -15.324 | -17.984 | -28.054 | -32.814 | -35.564
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Steady Progression | Thermal headroom (MW) | 10.476 | 10.606 | 10.556 | 10.506 | 10.416 | 10.066 | 9.626 | 9.176 | 8.736 | 8.246 | 7.396 | 6.586 | 5.676 | 4.766 | 3.766 | -3.074 | -8.034 | -10.654
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | System Transformation | Thermal headroom (MW) | 10.476 | 10.496 | 10.346 | 10.106 | 9.796 | 9.416 | 9.066 | 8.636 | 8.136 | 7.526 | 6.536 | 5.516 | 4.356 | 3.066 | 1.726 | -6.284 | -10.134 | -11.574
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | WPD Best View | Thermal headroom (MW) | 10.476 | 10.176 | 9.746 | 9.236 | 8.606 | 7.476 | 6.446 | 5.386 | 4.266 | 2.926 | 0.186 | -2.464 | -5.154 | -7.764 | -10.324 | -25.324 | -35.204 | -40.344
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Consumer Transformation | Thermal headroom (MW) | 8.08 | 7.97 | 7.78 | 7.52 | 7.14 | 6.55 | 5.94 | 5.28 | 4.6 | 3.84 | 2.64 | 1.14 | -0.68 | -2.36 | -4.02 | -13.84 | -20.47 | -23.9
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Leading the Way | Thermal headroom (MW) | 8.08 | 7.76 | 7.36 | 6.9 | 6.19 | 5.07 | 3.99 | 2.83 | 1.68 | 0.34 | -1.56 | -3.59 | -5.61 | -7.56 | -9.37 | -16.42 | -19.88 | -22.02
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Steady Progression | Thermal headroom (MW) | 8.08 | 8.22 | 8.27 | 8.28 | 8.26 | 8.09 | 7.9 | 7.68 | 7.36 | 6.99 | 6.45 | 5.88 | 5.25 | 4.59 | 3.92 | -0.21 | -3.68 | -5.1
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | System Transformation | Thermal headroom (MW) | 8.08 | 8.15 | 8.12 | 8.05 | 7.93 | 7.77 | 7.59 | 7.25 | 6.84 | 6.33 | 5.55 | 4.71 | 3.86 | 3.02 | 2.23 | -2.19 | -5.29 | -6.19
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | WPD Best View | Thermal headroom (MW) | 8.08 | 7.97 | 7.78 | 7.52 | 7.14 | 6.55 | 5.94 | 5.28 | 4.6 | 3.84 | 2.64 | 1.14 | -0.68 | -2.36 | -4.02 | -13.84 | -20.47 | -23.9
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Consumer Transformation | Thermal headroom (MW) | 6.04 | 6 | 5.9 | 5.82 | 5.68 | 5.46 | 5.23 | 4.98 | 4.72 | 4.45 | 4.14 | 3.75 | 3.21 | 2.62 | 2.04 | -1.68 | -3.86 | -4.95
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Leading the Way | Thermal headroom (MW) | 6.04 | 5.94 | 5.76 | 5.62 | 5.4 | 4.99 | 4.57 | 4.13 | 3.68 | 3.21 | 2.67 | 2.07 | 1.44 | 0.81 | 0.2 | -2.27 | -3.4 | -4.01
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Steady Progression | Thermal headroom (MW) | 6.04 | 6.09 | 6.09 | 6.1 | 6.09 | 6.02 | 5.94 | 5.83 | 5.68 | 5.52 | 5.31 | 5.09 | 4.84 | 4.58 | 4.32 | 3.01 | 2.09 | 1.61
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | System Transformation | Thermal headroom (MW) | 6.04 | 6.07 | 6.04 | 6.02 | 5.97 | 5.93 | 5.86 | 5.74 | 5.6 | 5.42 | 5.18 | 4.93 | 4.67 | 4.43 | 4.22 | 2.91 | 1.92 | 1.5
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | WPD Best View | Thermal headroom (MW) | 6.04 | 6 | 5.9 | 5.82 | 5.68 | 5.46 | 5.23 | 4.98 | 4.72 | 4.45 | 4.14 | 3.75 | 3.21 | 2.62 | 2.04 | -1.68 | -3.86 | -4.95
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Consumer Transformation | Thermal headroom (MW) | 3.205 | 3.135 | 2.835 | 2.555 | 2.155 | 1.615 | 1.005 | 0.315 | -0.425 | -1.185 | -2.665 | -4.565 | -6.505 | -8.355 | -10.125 | -20.065 | -26.375 | -29.605
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Leading the Way | Thermal headroom (MW) | 3.205 | 2.905 | 2.345 | 1.855 | 1.195 | 0.155 | -0.895 | -2.085 | -3.595 | -5.345 | -7.545 | -9.635 | -11.765 | -13.825 | -15.735 | -22.225 | -25.045 | -26.555
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Steady Progression | Thermal headroom (MW) | 3.205 | 3.405 | 3.415 | 3.455 | 3.465 | 3.335 | 3.165 | 2.955 | 2.715 | 2.365 | 1.775 | 1.195 | 0.565 | -0.115 | -0.775 | -4.975 | -8.535 | -9.805
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | System Transformation | Thermal headroom (MW) | 3.205 | 3.335 | 3.245 | 3.195 | 3.075 | 2.935 | 2.755 | 2.475 | 2.055 | 1.565 | 0.755 | -0.035 | -0.835 | -1.615 | -2.315 | -7.345 | -10.055 | -10.825
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | WPD Best View | Thermal headroom (MW) | 3.205 | 3.135 | 2.835 | 2.555 | 2.155 | 1.615 | 1.005 | 0.315 | -0.425 | -1.185 | -2.665 | -4.565 | -6.505 | -8.355 | -10.125 | -20.065 | -26.375 | -29.605
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Consumer Transformation | Thermal headroom (MW) | 12.63 | 12.46 | 12.22 | 11.97 | 11.58 | 11.1 | 10.69 | 10.25 | 9.78 | 9.24 | 7.06 | 4.75 | 2.43 | 0.12 | -2.36 | -9.01 | -18.64 | -25.78
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Leading the Way | Thermal headroom (MW) | 12.63 | 12.35 | 12 | 11.6 | 10.86 | 10.04 | 9.31 | 8.36 | 6.36 | 4.15 | 3.06 | 1.41 | -0.65 | -2.78 | -4.8 | -8.94 | -11.74 | -13.94
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Steady Progression | Thermal headroom (MW) | 12.63 | 12.59 | 12.5 | 12.41 | 12.29 | 12.09 | 11.89 | 11.69 | 11.47 | 10.52 | 9.35 | 9.05 | 8.69 | 8.1 | 7.75 | 5.52 | 3.61 | 2.86
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | System Transformation | Thermal headroom (MW) | 12.63 | 12.41 | 12.21 | 11.95 | 11.6 | 11.35 | 11.04 | 10.66 | 10.2 | 9.82 | 8.62 | 8.23 | 7.17 | 6.63 | 5.62 | 2.16 | -1.22 | -3.03
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | WPD Best View | Thermal headroom (MW) | 12.63 | 12.44 | 12.19 | 11.91 | 11.27 | 10.68 | 10.14 | 9.42 | 7.69 | 5.83 | 4.89 | 3.37 | 1.39 | -0.64 | -2.61 | -8.13 | -12.39 | -15.2
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Consumer Transformation | Thermal headroom (MW) | 11.28 | 11.22 | 11.03 | 10.74 | 10.4 | 9.83 | 9.34 | 8.79 | 8.08 | 7.22 | 5.69 | 3.8 | 1.85 | 0.36 | -1.12 | -11.36 | -17.91 | -20.98
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Leading the Way | Thermal headroom (MW) | 11.28 | 10.76 | 10.14 | 9.43 | 8.65 | 7.47 | 6.41 | 5.18 | 3.88 | 2.43 | 0.77 | -0.94 | -2.67 | -4.39 | -5.98 | -12.47 | -15.75 | -17.35
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Steady Progression | Thermal headroom (MW) | 11.28 | 11.41 | 11.43 | 11.42 | 11.4 | 11.19 | 10.99 | 10.79 | 10.53 | 10.24 | 9.78 | 9.35 | 8.81 | 8.26 | 7.62 | 2.62 | -0.89 | -2.37
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | System Transformation | Thermal headroom (MW) | 11.28 | 11.35 | 11.29 | 11.18 | 11.05 | 10.89 | 10.7 | 10.51 | 10.3 | 10.03 | 9.47 | 8.77 | 8.07 | 6.94 | 5.82 | -0.06 | -3.4 | -4.35
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | WPD Best View | Thermal headroom (MW) | 11.28 | 11.22 | 11.03 | 10.74 | 10.4 | 9.83 | 9.34 | 8.79 | 8.08 | 7.22 | 5.69 | 3.8 | 1.85 | 0.36 | -1.12 | -11.36 | -17.91 | -20.98
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Consumer Transformation | Thermal headroom (MW) | 25 | 22.5568 | 20.3821 | 0.83782 | -7.5542 | -14.1868 | -20.7525 | -27.4972 | -35.4655 | -43.4725 | -54.3493 | -66.6656 | -79.6148 | -92.3627 | -104.6101 | -162.2637 | -207.2766 | -237.1501
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Leading the Way | Thermal headroom (MW) | 25 | 21.2004 | 17.6878 | -8.7163 | -20.9096 | -30.5623 | -38.7369 | -47.7329 | -60.4166 | -73.3495 | -85.1303 | -98.0668 | -111.8725 | -125.499 | -137.2719 | -175.6125 | -195.8248 | -211.5621
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Steady Progression | Thermal headroom (MW) | 25 | 24.1817 | 23.6194 | 8.9738 | 4.1785 | 1.2071 | -1.9226 | -5.3116 | -9.3823 | -14.4256 | -20.5301 | -25.3303 | -29.2762 | -33.3696 | -37.1431 | -60.4276 | -74.1497 | -77.8359
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | System Transformation | Thermal headroom (MW) | 25 | 23.3041 | 22.1067 | 3.9825 | -2.6424 | -5.6835 | -8.8656 | -12.9222 | -18.5041 | -23.351 | -28.9406 | -33.2499 | -38.8629 | -43.6511 | -48.9687 | -76.6054 | -95.2241 | -102.876
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | WPD Best View | Thermal headroom (MW) | 25 | 22.5568 | 20.3821 | 0.83782 | -7.5542 | -14.1868 | -20.7525 | -27.4972 | -35.4655 | -43.4725 | -54.3493 | -66.6656 | -79.6148 | -92.3627 | -104.6101 | -162.2637 | -207.2766 | -237.1501
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Consumer Transformation | Thermal headroom (MW) | 5.49 | 5.3 | 4.86 | 4.35 | 3.54 | 2.44 | 1.38 | 0.25 | -1.37 | -2.91 | -4.67 | -7.07 | -9.7 | -12.29 | -14.82 | -29.38 | -39.05 | -44.05
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Leading the Way | Thermal headroom (MW) | 5.49 | 4.97 | 4.17 | 3.31 | 1.97 | 0.14 | -1.6 | -3.47 | -6.14 | -8.94 | -11.81 | -14.84 | -17.85 | -20.8 | -23.53 | -33.41 | -37.87 | -40.71
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Steady Progression | Thermal headroom (MW) | 5.49 | 5.69 | 5.68 | 5.65 | 5.56 | 5.21 | 4.8 | 4.24 | 3.35 | 2.44 | 1.4 | 0.31 | -0.85 | -2.07 | -3.29 | -10.09 | -14.27 | -16.33
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | System Transformation | Thermal headroom (MW) | 5.49 | 5.59 | 5.46 | 5.29 | 5.01 | 4.66 | 4.15 | 3.52 | 2.33 | 1.17 | 0 | -1.25 | -2.51 | -3.75 | -5.07 | -11.58 | -15.52 | -16.81
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | WPD Best View | Thermal headroom (MW) | 5.49 | 5.3 | 4.86 | 4.35 | 3.54 | 2.44 | 1.38 | 0.25 | -1.37 | -2.91 | -4.67 | -7.07 | -9.7 | -12.29 | -14.82 | -29.38 | -39.05 | -44.05
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Consumer Transformation | Thermal headroom (MW) | 9.772 | 9.762 | 9.662 | -3.078 | -4.338 | -5.728 | -7.108 | -8.528 | -10.378 | -11.938 | -12.928 | -13.838 | -14.738 | -15.588 | -16.348 | -20.208 | -21.338 | -21.148
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Leading the Way | Thermal headroom (MW) | 9.772 | 9.702 | 9.512 | -7.458 | -8.818 | -10.388 | -10.988 | -11.718 | -13.208 | -14.098 | -15.148 | -16.148 | -17.118 | -18.008 | -18.728 | -20.868 | -20.518 | -19.308
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Steady Progression | Thermal headroom (MW) | 9.772 | 9.902 | 9.922 | -0.458 | -1.388 | -2.358 | -3.368 | -4.358 | -5.618 | -6.668 | -7.788 | -8.888 | -9.148 | -9.398 | -9.708 | -12.108 | -13.108 | -12.848
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | System Transformation | Thermal headroom (MW) | 9.772 | 9.882 | 9.872 | -2.528 | -3.488 | -4.508 | -5.508 | -6.568 | -8.038 | -9.158 | -9.488 | -9.828 | -10.268 | -10.778 | -11.278 | -14.358 | -14.618 | -13.598
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | WPD Best View | Thermal headroom (MW) | 9.772 | 9.762 | 9.662 | -3.078 | -4.338 | -5.728 | -7.108 | -8.528 | -10.378 | -11.938 | -12.928 | -13.838 | -14.738 | -15.588 | -16.348 | -20.208 | -21.338 | -21.148
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Consumer Transformation | Thermal headroom (MW) | 0.22 | -0.19 | -0.8 | -1.83 | -4.63 | -5.82 | -6.99 | -8.15 | -9.37 | -10.76 | -13.68 | -16.46 | -19.22 | -21.99 | -24.64 | -32.19 | -43.47 | -53.96
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Leading the Way | Thermal headroom (MW) | 0.22 | -0.3 | -1.06 | -2.39 | -6.6 | -8.19 | -9.73 | -11.38 | -14.09 | -17.03 | -18.89 | -21.21 | -23.93 | -26.73 | -28.93 | -34.53 | -40.22 | -46.73
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Steady Progression | Thermal headroom (MW) | 0.22 | -0.05 | -0.46 | -1.16 | -3.14 | -3.58 | -4.02 | -4.45 | -4.86 | -5.94 | -7.24 | -7.71 | -8.16 | -8.66 | -8.89 | -10.31 | -10.87 | -10.69
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | System Transformation | Thermal headroom (MW) | 0.22 | -0.27 | -0.85 | -1.83 | -4.54 | -5.07 | -5.62 | -6.35 | -7.28 | -7.91 | -9.3 | -9.77 | -10.89 | -11.51 | -12.44 | -15.49 | -20 | -23.68
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | WPD Best View | Thermal headroom (MW) | 0.22 | -0.19 | -0.8 | -1.83 | -4.63 | -5.82 | -6.99 | -8.15 | -9.37 | -10.76 | -13.68 | -16.46 | -19.22 | -21.99 | -24.64 | -32.19 | -43.47 | -53.96
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Consumer Transformation | Thermal headroom (MW) | 7.92 | 7.36 | 6.68 | 5.41 | 3.76 | 1.84 | -0.05 | -2.12 | -4.15 | -6.31 | -8.94 | -13.01 | -17.13 | -21.03 | -24.9 | -48.45 | -62.69 | -70.2
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Leading the Way | Thermal headroom (MW) | 7.92 | 6.91 | 5.74 | 3.92 | 1.34 | -1.96 | -5 | -8.44 | -11.97 | -16.01 | -20.33 | -24.88 | -29.47 | -33.85 | -37.86 | -53.06 | -59.96 | -64.51
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Steady Progression | Thermal headroom (MW) | 7.92 | 8 | 7.99 | 7.62 | 7.12 | 6.36 | 5.59 | 4.68 | 3.62 | 2.49 | 0.95 | -0.66 | -2.35 | -4.07 | -5.79 | -15.39 | -22.24 | -24.91
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | System Transformation | Thermal headroom (MW) | 7.92 | 7.81 | 7.6 | 6.94 | 6.1 | 5.35 | 4.53 | 3.29 | 1.93 | 0.41 | -1.37 | -3.26 | -5.16 | -6.97 | -8.7 | -19.13 | -25.12 | -27
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | WPD Best View | Thermal headroom (MW) | 7.92 | 7.36 | 6.68 | 5.41 | 3.76 | 1.84 | -0.05 | -2.12 | -4.15 | -6.31 | -8.94 | -13.01 | -17.13 | -21.03 | -24.9 | -48.45 | -62.69 | -70.2
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Consumer Transformation | Thermal headroom (MW) | 11.56 | 10.6 | 10.6 | 10.59 | 10.55 | 10.5 | 10.52 | 10.53 | 10.52 | 10.46 | 10.31 | 9.96 | 9.56 | 9.24 | 8.97 | 7.53 | 6.95 | 6.84
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Leading the Way | Thermal headroom (MW) | 11.56 | 10.44 | 10.41 | 10.38 | 10.37 | 10.34 | 10.3 | 10.23 | 10.18 | 9.98 | 9.58 | 9.2 | 8.78 | 8.37 | 8.05 | 7.24 | 7.3 | 7.67
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Steady Progression | Thermal headroom (MW) | 11.56 | 10.78 | 10.82 | 10.87 | 10.9 | 10.91 | 10.91 | 10.9 | 10.96 | 11 | 11.01 | 11.01 | 10.99 | 10.97 | 10.94 | 10.04 | 9.21 | 9.35
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | System Transformation | Thermal headroom (MW) | 11.56 | 10.62 | 10.66 | 10.68 | 10.68 | 10.69 | 10.76 | 10.8 | 10.84 | 10.85 | 10.84 | 10.81 | 10.76 | 10.72 | 10.64 | 9.21 | 8.77 | 9.16
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | WPD Best View | Thermal headroom (MW) | 11.56 | 10.6 | 10.6 | 10.59 | 10.55 | 10.5 | 10.52 | 10.53 | 10.52 | 10.46 | 10.31 | 9.96 | 9.56 | 9.24 | 8.97 | 7.53 | 6.95 | 6.84
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Consumer Transformation | Thermal headroom (MW) | 28.7199 | 27.9804 | 26.5876 | 25.136 | 23.2067 | 20.0344 | 16.9482 | 13.667 | 9.5344 | 4.5006 | -3.4351 | -11.724 | -20.1413 | -27.5875 | -35.0376 | -75.4773 | -100.1469 | -111.8555
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Leading the Way | Thermal headroom (MW) | 28.7199 | 26.407 | 23.4976 | 20.585 | 16.9935 | 12.0115 | 7.0438 | 1.4923 | -5.2339 | -12.8662 | -21.6216 | -30.1849 | -38.8193 | -47.0503 | -54.7949 | -83.2382 | -95.3805 | -100.9782
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Steady Progression | Thermal headroom (MW) | 28.7199 | 29.1698 | 29.0297 | 28.9762 | 28.8102 | 27.7441 | 26.5898 | 25.2825 | 23.6606 | 21.7308 | 19.1429 | 16.6302 | 13.6901 | 10.6286 | 7.4371 | -14.2054 | -28.3812 | -34.1165
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | System Transformation | Thermal headroom (MW) | 28.7199 | 28.8139 | 28.2628 | 27.7567 | 27.035 | 26.0086 | 24.7535 | 23.2903 | 21.1814 | 18.6609 | 15.2815 | 11.8909 | 8.2609 | 3.7795 | -0.96111 | -25.1705 | -35.954 | -39.0072
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | WPD Best View | Thermal headroom (MW) | 28.7199 | 27.9738 | 26.5744 | 25.1167 | 23.1807 | 19.9991 | 16.9043 | 13.6136 | 9.4737 | 4.4564 | -3.4796 | -11.7702 | -20.1924 | -27.6684 | -35.1202 | -75.5074 | -100.1335 | -111.8281
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Consumer Transformation | Thermal headroom (MW) | 0.065 | -0.265 | -0.815 | -1.455 | -2.285 | -3.645 | -4.795 | -6.055 | -7.525 | -9.275 | -12.145 | -15.015 | -17.925 | -20.795 | -23.585 | -38.945 | -48.495 | -53.225
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Leading the Way | Thermal headroom (MW) | 0.065 | -0.915 | -2.065 | -3.255 | -4.755 | -6.875 | -8.835 | -10.985 | -13.375 | -16.155 | -19.245 | -22.375 | -25.545 | -28.645 | -31.585 | -42.025 | -46.615 | -48.825
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Steady Progression | Thermal headroom (MW) | 0.065 | 0.215 | 0.175 | 0.135 | 0.035 | -0.425 | -0.855 | -1.325 | -1.835 | -2.435 | -3.275 | -4.135 | -5.085 | -6.125 | -7.165 | -14.405 | -19.455 | -21.605
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | System Transformation | Thermal headroom (MW) | 0.065 | 0.055 | -0.165 | -0.415 | -0.755 | -1.225 | -1.705 | -2.245 | -2.855 | -3.675 | -4.725 | -5.875 | -7.105 | -8.425 | -9.825 | -17.785 | -21.525 | -22.815
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | WPD Best View | Thermal headroom (MW) | 0.065 | -0.265 | -0.815 | -1.455 | -2.285 | -3.645 | -4.795 | -6.055 | -7.525 | -9.275 | -12.145 | -15.015 | -17.925 | -20.795 | -23.585 | -38.945 | -48.495 | -53.225
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Consumer Transformation | Thermal headroom (MW) | 6.63 | 6.35 | 5.89 | 5.36 | 4.58 | 3.36 | 2.02 | 0.55 | -1.15 | -3.21 | -6.33 | -10.19 | -14.17 | -17.2 | -20.23 | -36.26 | -45.25 | -49.06
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Leading the Way | Thermal headroom (MW) | 6.63 | 5.88 | 4.89 | 3.84 | 2.49 | 0.69 | -1.29 | -3.64 | -6.28 | -9.2 | -12.63 | -16.26 | -19.96 | -23.33 | -26.48 | -38.08 | -42.58 | -44.05
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Steady Progression | Thermal headroom (MW) | 6.63 | 6.79 | 6.76 | 6.72 | 6.63 | 6.27 | 5.84 | 5.28 | 4.65 | 3.89 | 2.86 | 1.76 | 0.48 | -0.86 | -2.28 | -12.01 | -18.05 | -20.52
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | System Transformation | Thermal headroom (MW) | 6.63 | 6.64 | 6.46 | 6.23 | 5.91 | 5.6 | 5.06 | 4.35 | 3.45 | 2.39 | 1.04 | -0.45 | -2.07 | -4.52 | -7.09 | -18.46 | -23.12 | -23.87
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | WPD Best View | Thermal headroom (MW) | 6.63 | 6.34 | 5.88 | 5.34 | 4.55 | 3.32 | 1.97 | 0.48 | -1.22 | -3.26 | -6.38 | -10.24 | -14.23 | -17.29 | -20.33 | -36.3 | -45.24 | -49.03
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Consumer Transformation | Thermal headroom (MW) | 10.22 | 10.05 | 9.63 | 9.27 | 8.82 | 8.04 | 7.29 | 6.54 | 5.43 | 4.04 | 1.84 | -0.14 | -2.12 | -4.01 | -5.96 | -16.67 | -23.62 | -27.11
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Leading the Way | Thermal headroom (MW) | 10.22 | 9.56 | 8.71 | 7.92 | 6.99 | 5.69 | 4.42 | 3.06 | 1.18 | -0.98 | -3.45 | -5.64 | -7.81 | -9.94 | -11.94 | -19.47 | -22.9 | -24.83
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Steady Progression | Thermal headroom (MW) | 10.22 | 10.37 | 10.31 | 10.32 | 10.31 | 10.02 | 9.69 | 9.36 | 8.86 | 8.27 | 7.5 | 6.86 | 6.06 | 5.26 | 4.41 | -1.12 | -4.79 | -6.2
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | System Transformation | Thermal headroom (MW) | 10.22 | 10.29 | 10.13 | 10.05 | 9.91 | 9.63 | 9.32 | 9.01 | 8.38 | 7.68 | 6.66 | 5.78 | 4.85 | 3.88 | 2.85 | -3.11 | -5.91 | -6.94
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | WPD Best View | Thermal headroom (MW) | 10.22 | 10.05 | 9.63 | 9.27 | 8.82 | 8.04 | 7.29 | 6.54 | 5.43 | 4.04 | 1.84 | -0.14 | -2.12 | -4.01 | -5.96 | -16.67 | -23.62 | -27.11
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Consumer Transformation | Thermal headroom (MW) | 16.7884 | 16.8127 | 16.705 | 16.2623 | 14.8829 | 12.1857 | 10.5902 | 8.9137 | 7.1833 | 5.2169 | 1.8454 | -1.6941 | -5.1861 | -8.5943 | -12.0541 | -24.0074 | -32.6897 | -37.5368
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Leading the Way | Thermal headroom (MW) | 16.7884 | 16.3482 | 15.7675 | 14.9095 | 12.8844 | 8.7349 | 6.2887 | 3.5983 | 0.24414 | -3.2246 | -5.7456 | -8.6517 | -11.7318 | -14.8196 | -17.5912 | -26.784 | -30.6968 | -32.8009
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Steady Progression | Thermal headroom (MW) | 16.7884 | 17.0106 | 17.033 | 16.9125 | 16.2089 | 14.698 | 13.915 | 13.0997 | 12.0595 | 10.6893 | 8.8426 | 7.5941 | 6.1873 | 4.6324 | 3.1243 | -8.0619 | -12.915 | -14.2752
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | System Transformation | Thermal headroom (MW) | 16.7884 | 16.9046 | 16.8656 | 16.62 | 15.636 | 14.2902 | 13.8002 | 13.2787 | 12.6495 | 12.0882 | 10.3748 | 8.8841 | 7.0303 | 5.3173 | 3.2728 | -8.1858 | -15.8381 | -17.5122
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | WPD Best View | Thermal headroom (MW) | 16.7884 | 16.9721 | 16.9817 | 16.7825 | 15.842 | 14.2712 | 13.5868 | 12.8437 | 12.0208 | 11.2411 | 9.686 | 7.981 | 6.1472 | 4.2514 | 2.26 | -8.1719 | -14.2129 | -15.2378
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Consumer Transformation | Thermal headroom (MW) | 2.95 | 2.71 | 2.34 | 1.79 | 1.06 | -0.83 | -1.88 | -2.88 | -4 | -5.18 | -8.08 | -11 | -13.93 | -16.82 | -19.75 | -29.81 | -39.54 | -45.49
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Leading the Way | Thermal headroom (MW) | 2.95 | 2.31 | 1.53 | 0.63 | -0.49 | -3.31 | -4.78 | -6.39 | -8.54 | -10.75 | -12.96 | -15.43 | -17.95 | -20.45 | -22.74 | -29.42 | -32.59 | -34.29
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Steady Progression | Thermal headroom (MW) | 2.95 | 3.03 | 2.98 | 2.9 | 2.8 | 1.86 | 1.48 | 1.06 | 0.55 | -0.26 | -1.35 | -1.95 | -2.68 | -3.53 | -4.34 | -10.11 | -13.48 | -14.84
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | System Transformation | Thermal headroom (MW) | 2.95 | 2.95 | 2.84 | 2.66 | 2.43 | 1.35 | 1.01 | 0.64 | 0.15 | -0.3 | -1.35 | -2.47 | -3.67 | -4.94 | -6.22 | -12.79 | -15.85 | -16.62
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | WPD Best View | Thermal headroom (MW) | 2.95 | 2.96 | 2.85 | 2.66 | 2.42 | 1.24 | 0.78 | 0.3 | -0.29 | -0.82 | -1.94 | -3.11 | -4.38 | -5.71 | -7.05 | -13.59 | -16.49 | -17.3
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Consumer Transformation | Thermal headroom (MW) | 5.63 | 5.65 | 5.69 | 5.61 | 5.09 | 4.38 | 3.95 | 3.48 | 3.01 | 2.43 | 1.76 | 1.02 | 0.32 | -0.36 | -1.05 | -3.43 | -4.44 | -4.89
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Leading the Way | Thermal headroom (MW) | 5.63 | 5.57 | 5.54 | 5.39 | 4.68 | 3.58 | 2.92 | 2.19 | 1.28 | 0.34 | -0.17 | -0.8 | -1.48 | -2.18 | -2.78 | -5.02 | -6.02 | -6.58
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Steady Progression | Thermal headroom (MW) | 5.63 | 5.65 | 5.64 | 5.56 | 5.17 | 4.71 | 4.44 | 4.17 | 3.81 | 3.37 | 2.82 | 2.41 | 1.95 | 1.47 | 1.01 | -2.48 | -3.93 | -4.29
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | System Transformation | Thermal headroom (MW) | 5.63 | 5.62 | 5.61 | 5.51 | 5.02 | 4.64 | 4.46 | 4.27 | 4.07 | 3.89 | 3.36 | 2.98 | 2.43 | 1.99 | 1.36 | -2.1 | -4.91 | -5.62
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | WPD Best View | Thermal headroom (MW) | 5.63 | 5.66 | 5.67 | 5.6 | 5.14 | 4.68 | 4.45 | 4.19 | 3.93 | 3.67 | 3.27 | 2.8 | 2.3 | 1.79 | 1.23 | -1.7 | -3.69 | -4
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Consumer Transformation | Thermal headroom (MW) | 8.58 | 8.74 | 8.82 | 8.88 | 8.91 | 8.71 | 8.54 | 8.35 | 8.17 | 7.99 | 7.7 | 7.37 | 7.05 | 6.72 | 6.4 | 5.23 | 4.76 | 4.65
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Leading the Way | Thermal headroom (MW) | 8.58 | 8.67 | 8.67 | 8.68 | 8.64 | 8.26 | 7.93 | 7.56 | 7.2 | 6.82 | 6.67 | 6.49 | 6.27 | 6.05 | 5.84 | 4.96 | 4.91 | 4.92
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Steady Progression | Thermal headroom (MW) | 8.58 | 8.74 | 8.81 | 8.88 | 8.94 | 8.86 | 8.79 | 8.73 | 8.66 | 8.59 | 8.43 | 8.29 | 8.15 | 8 | 7.82 | 6.49 | 6.44 | 6.64
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | System Transformation | Thermal headroom (MW) | 8.58 | 8.72 | 8.78 | 8.83 | 8.87 | 8.92 | 8.98 | 9.04 | 9.1 | 9.15 | 9.07 | 8.98 | 8.88 | 8.78 | 8.68 | 7.59 | 6.84 | 6.93
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | WPD Best View | Thermal headroom (MW) | 8.58 | 8.72 | 8.78 | 8.84 | 8.88 | 8.9 | 8.93 | 8.96 | 9 | 9.03 | 8.92 | 8.81 | 8.68 | 8.55 | 8.42 | 7.42 | 6.74 | 6.82
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Consumer Transformation | Thermal headroom (MW) | 47.6352 | 47.3513 | 46.9712 | 46.3892 | 45.1028 | 43.2601 | 41.5359 | 39.6831 | 37.6919 | 35.3025 | 31.4752 | 27.2852 | 23.1491 | 19.4076 | 15.7785 | -2.7465 | -13.3852 | -18.7185
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Leading the Way | Thermal headroom (MW) | 47.6352 | 46.9358 | 46.0622 | 45.0743 | 43.2055 | 40.0248 | 37.0937 | 33.8103 | 30.396 | 26.5768 | 22.8558 | 18.8376 | 14.8569 | 10.9587 | 7.459 | -4.6578 | -9.2565 | -10.8002
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Steady Progression | Thermal headroom (MW) | 47.6352 | 47.7743 | 47.7487 | 47.6902 | 47.31 | 46.4506 | 45.7306 | 44.8717 | 43.9761 | 42.9139 | 41.4678 | 40.0971 | 38.5496 | 36.8923 | 35.0799 | 22.8208 | 15.7184 | 13.1155
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | System Transformation | Thermal headroom (MW) | 47.6352 | 47.6693 | 47.5443 | 47.3422 | 46.6453 | 45.7218 | 44.8836 | 44.045 | 43.1238 | 42.012 | 40.3631 | 38.6242 | 36.5353 | 34.0435 | 31.372 | 17.7901 | 11.4983 | 10.5518
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | WPD Best View | Thermal headroom (MW) | 47.6352 | 47.3526 | 46.9737 | 46.3946 | 45.111 | 43.2757 | 41.5579 | 39.7102 | 37.7248 | 35.3395 | 31.5276 | 27.3523 | 23.231 | 19.5045 | 15.8899 | -2.5671 | -13.1523 | -18.4555
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Consumer Transformation | Thermal headroom (MW) | 7.644 | 7.524 | 7.364 | 7.054 | 6.184 | 4.574 | 3.224 | 2.194 | 1.064 | -0.776 | -4.076 | -7.336 | -10.676 | -13.906 | -17.226 | -29.546 | -38.366 | -43.626
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Leading the Way | Thermal headroom (MW) | 7.644 | 7.364 | 7.024 | 6.554 | 5.344 | 2.494 | 0.214 | -1.826 | -4.286 | -7.346 | -10.006 | -12.866 | -15.756 | -18.556 | -21.226 | -29.046 | -32.006 | -33.236
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Steady Progression | Thermal headroom (MW) | 7.644 | 7.734 | 7.764 | 7.744 | 7.374 | 6.374 | 5.634 | 5.084 | 4.514 | 3.474 | 2.224 | 1.324 | 0.364 | -0.846 | -2.066 | -10.046 | -13.616 | -14.876
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | System Transformation | Thermal headroom (MW) | 7.644 | 7.664 | 7.614 | 7.494 | 6.914 | 5.784 | 4.924 | 4.424 | 3.874 | 3.044 | 2.154 | 1.234 | -0.196 | -1.916 | -3.686 | -12.276 | -15.866 | -16.616
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | WPD Best View | Thermal headroom (MW) | 7.644 | 7.524 | 7.374 | 7.084 | 6.224 | 4.644 | 3.324 | 2.324 | 1.214 | -0.606 | -3.846 | -7.036 | -10.306 | -13.466 | -16.716 | -28.736 | -37.306 | -42.436
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Consumer Transformation | Thermal headroom (MW) | 7.12 | 6.98 | 6.84 | 6.65 | 6.37 | 5.96 | 5.5 | 4.97 | 4.4 | 3.73 | 2.75 | 1.69 | 0.7 | -0.25 | -1.18 | -6.06 | -8.4 | -9.6
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Leading the Way | Thermal headroom (MW) | 7.12 | 6.87 | 6.6 | 6.32 | 5.89 | 5.24 | 4.57 | 3.73 | 2.84 | 1.86 | 0.84 | -0.26 | -1.36 | -2.39 | -3.33 | -6.5 | -7.37 | -7.4
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Steady Progression | Thermal headroom (MW) | 7.12 | 7.11 | 7.06 | 6.99 | 6.92 | 6.76 | 6.62 | 6.35 | 6.08 | 5.79 | 5.43 | 5.05 | 4.6 | 4.15 | 3.6 | 0.07 | -2.23 | -3.22
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | System Transformation | Thermal headroom (MW) | 7.12 | 7.1 | 7.03 | 6.95 | 6.82 | 6.65 | 6.44 | 6.22 | 5.92 | 5.55 | 5.08 | 4.52 | 3.93 | 3.28 | 2.55 | -1.61 | -3.29 | -3.43
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | WPD Best View | Thermal headroom (MW) | 7.12 | 6.98 | 6.84 | 6.65 | 6.37 | 5.96 | 5.5 | 4.97 | 4.4 | 3.73 | 2.75 | 1.69 | 0.7 | -0.25 | -1.18 | -6.06 | -8.4 | -9.6
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Consumer Transformation | Thermal headroom (MW) | 8.76 | 8.63 | 8.55 | 8.4 | 8.13 | 7.68 | 7.34 | 6.87 | 6.35 | 5.77 | 4.88 | 3.97 | 3.05 | 2.17 | 1.36 | -2.84 | -5.02 | -6.02
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Leading the Way | Thermal headroom (MW) | 8.76 | 8.57 | 8.41 | 8.19 | 7.8 | 6.98 | 6.24 | 5.37 | 4.58 | 3.77 | 2.87 | 1.94 | 1.05 | 0.18 | -0.51 | -3.12 | -4.02 | -4.26
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Steady Progression | Thermal headroom (MW) | 8.76 | 8.72 | 8.71 | 8.69 | 8.63 | 8.38 | 8.19 | 7.95 | 7.73 | 7.51 | 7.18 | 6.82 | 6.4 | 5.98 | 5.53 | 2.42 | 0.48 | -0.08
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | System Transformation | Thermal headroom (MW) | 8.76 | 8.69 | 8.66 | 8.6 | 8.47 | 8.2 | 7.98 | 7.72 | 7.48 | 7.24 | 6.85 | 6.42 | 5.88 | 5.34 | 4.74 | 1.46 | -0.13 | -0.36
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | WPD Best View | Thermal headroom (MW) | 8.76 | 8.63 | 8.55 | 8.4 | 8.13 | 7.68 | 7.34 | 6.87 | 6.35 | 5.77 | 4.88 | 3.97 | 3.05 | 2.17 | 1.36 | -2.84 | -5.02 | -6.02
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Consumer Transformation | Thermal headroom (MW) | -1.71 | -1.54 | -1.48 | -1.44 | -1.74 | -2.05 | -2.3 | -2.57 | -2.86 | -3.17 | -3.51 | -3.81 | -4.1 | -4.49 | -4.89 | -8.15 | -9.45 | -10.08
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Leading the Way | Thermal headroom (MW) | -1.71 | -1.58 | -1.56 | -1.56 | -1.98 | -2.48 | -2.83 | -3.23 | -3.63 | -4.1 | -4.5 | -4.94 | -5.35 | -5.88 | -6.44 | -8.79 | -9.29 | -9.4
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Steady Progression | Thermal headroom (MW) | -1.71 | -1.48 | -1.36 | -1.26 | -1.38 | -1.5 | -1.54 | -1.62 | -1.72 | -1.83 | -2 | -2.19 | -2.41 | -2.65 | -2.89 | -3.97 | -3.98 | -3.99
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | System Transformation | Thermal headroom (MW) | -1.71 | -1.49 | -1.4 | -1.31 | -1.52 | -1.65 | -1.71 | -1.82 | -1.96 | -2.12 | -2.34 | -2.57 | -2.81 | -3.05 | -3.27 | -4.11 | -4.48 | -4.47
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | WPD Best View | Thermal headroom (MW) | -1.71 | -1.54 | -1.48 | -1.44 | -1.74 | -2.05 | -2.3 | -2.57 | -2.86 | -3.17 | -3.51 | -3.81 | -4.1 | -4.49 | -4.89 | -8.15 | -9.45 | -10.08
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Consumer Transformation | Thermal headroom (MW) | 11.94 | 12.12 | 12.22 | 12.31 | 12.38 | 12.36 | 12.3 | 12.24 | 12.16 | 12.07 | 11.92 | 11.77 | 11.64 | 11.52 | 11.4 | 11.01 | 11.01 | 11.14
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Leading the Way | Thermal headroom (MW) | 11.94 | 12.11 | 12.18 | 12.26 | 12.29 | 12.13 | 11.98 | 11.79 | 11.48 | 11.11 | 11.02 | 10.82 | 10.61 | 10.38 | 10.16 | 9.56 | 9.22 | 8.93
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Steady Progression | Thermal headroom (MW) | 11.94 | 12.11 | 12.2 | 12.28 | 12.36 | 12.36 | 12.37 | 12.37 | 12.38 | 12.31 | 12.19 | 12.12 | 12.06 | 11.93 | 11.82 | 11.11 | 11.07 | 11.23
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | System Transformation | Thermal headroom (MW) | 11.94 | 12.09 | 12.16 | 12.22 | 12.27 | 12.32 | 12.37 | 12.4 | 12.43 | 12.43 | 12.17 | 12.09 | 11.86 | 11.74 | 11.53 | 10.61 | 9.79 | 9.58
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | WPD Best View | Thermal headroom (MW) | 11.94 | 12.12 | 12.22 | 12.31 | 12.38 | 12.36 | 12.3 | 12.24 | 12.16 | 12.07 | 11.92 | 11.77 | 11.64 | 11.52 | 11.4 | 11.01 | 11.01 | 11.14
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Consumer Transformation | Thermal headroom (MW) | 11.89 | 11.59 | 11.19 | 10.67 | 9.6 | 8.64 | 7.61 | 6.5 | 5.53 | 4.38 | 2.5 | 0.25 | -1.96 | -3.72 | -5.43 | -15.15 | -21 | -23.69
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Leading the Way | Thermal headroom (MW) | 11.89 | 11.26 | 10.47 | 9.65 | 8.2 | 6.67 | 5.11 | 3.34 | 1.7 | -0.1 | -2.07 | -4.15 | -6.12 | -8.01 | -9.74 | -15.83 | -18.56 | -19.56
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Steady Progression | Thermal headroom (MW) | 11.89 | 11.88 | 11.76 | 11.62 | 11.18 | 10.8 | 10.4 | 9.95 | 9.48 | 8.97 | 8.32 | 7.71 | 7 | 6.28 | 5.49 | -0.09 | -3.68 | -5.17
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | System Transformation | Thermal headroom (MW) | 11.89 | 11.82 | 11.62 | 11.38 | 10.75 | 10.37 | 9.93 | 9.45 | 8.96 | 8.43 | 7.68 | 6.84 | 5.94 | 4.6 | 3.23 | -2.99 | -5.83 | -6.46
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | WPD Best View | Thermal headroom (MW) | 11.89 | 11.59 | 11.19 | 10.67 | 9.6 | 8.64 | 7.61 | 6.5 | 5.53 | 4.38 | 2.5 | 0.25 | -1.96 | -3.72 | -5.43 | -15.15 | -21 | -23.69
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Consumer Transformation | Thermal headroom (MW) | 3.78 | 3.73 | 3.6 | 3.46 | 3.17 | 2.68 | 2.22 | 1.8 | 1.28 | 0.7 | -0.4 | -1.88 | -3.38 | -4.49 | -5.57 | -11.39 | -15.79 | -18.09
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Leading the Way | Thermal headroom (MW) | 3.78 | 3.53 | 3.17 | 2.82 | 2.37 | 1.54 | 0.75 | -0.1 | -1.1 | -2.28 | -3.29 | -4.43 | -5.69 | -6.94 | -8.06 | -12.11 | -14.39 | -15.53
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Steady Progression | Thermal headroom (MW) | 3.78 | 3.83 | 3.83 | 3.84 | 3.83 | 3.65 | 3.48 | 3.31 | 3.07 | 2.81 | 2.41 | 2.05 | 1.68 | 1.27 | 0.82 | -2.75 | -5.04 | -5.99
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | System Transformation | Thermal headroom (MW) | 3.78 | 3.81 | 3.78 | 3.75 | 3.62 | 3.43 | 3.25 | 3.08 | 2.89 | 2.62 | 2.19 | 1.76 | 1.29 | 0.41 | -0.5 | -4.59 | -6.69 | -6.98
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | WPD Best View | Thermal headroom (MW) | 3.78 | 3.73 | 3.6 | 3.46 | 3.17 | 2.68 | 2.22 | 1.8 | 1.28 | 0.7 | -0.4 | -1.88 | -3.38 | -4.49 | -5.57 | -11.39 | -15.79 | -18.09

## Generation headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | Limiting constraint | 0 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Consumer Transformation | Headroom (MW) | N/A | 4.44 | 4.41 | 4.4 | 4.38 | 4.35 | 4.33 | 4.32 | 4.25 | 4.2 | 4.15 | 4.1 | 4.05 | 4.01 | 3.95 | 3.9 | 3.59 | 3.21 | 2.79
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Leading the Way | Headroom (MW) | N/A | 4.44 | 4.41 | 4.39 | 4.38 | 4.34 | 4.32 | 4.29 | 4.22 | 4.16 | 4.11 | 4.06 | 4.01 | 3.96 | 3.91 | 3.85 | 3.52 | 3.09 | 2.57
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | Steady Progression | Headroom (MW) | N/A | 4.44 | 4.41 | 4.4 | 4.39 | 4.37 | 4.36 | 4.35 | 4.34 | 4.32 | 4.31 | 4.3 | 4.28 | 4.27 | 4.26 | 4.24 | 4.17 | 4.1 | 4.02
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | System Transformation | Headroom (MW) | N/A | 4.44 | 4.41 | 4.4 | 4.39 | 4.36 | 4.35 | 4.34 | 4.32 | 4.31 | 4.29 | 4.28 | 4.25 | 4.22 | 4.19 | 4.16 | 4.03 | 3.82 | 3.6
Berkswell 132kV | Coventry Central | COURTAULDS 33 11kV S STN | Primary | 6.6 | -1.5052 | 52.4249 | WPD Best View | Headroom (MW) | N/A | 4.44 | 4.41 | 4.4 | 4.38 | 4.35 | 4.33 | 4.32 | 4.25 | 4.2 | 4.15 | 4.1 | 4.05 | 4.01 | 3.95 | 3.9 | 3.59 | 3.21 | 2.79
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Consumer Transformation | Headroom (MW) | N/A | 9.4754 | 9.4664 | 9.4557 | 9.4376 | 9.3919 | 9.3422 | 9.279 | 9.2108 | 9.1487 | 9.0629 | 8.9884 | 8.9106 | 8.8305 | 8.7469 | 8.6646 | 8.2577 | 7.9954 | 7.746
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Leading the Way | Headroom (MW) | N/A | 12.9678 | 12.9547 | 12.9377 | 12.9091 | 12.8442 | 12.7732 | 12.6836 | 12.5809 | 12.4913 | 12.3554 | 12.2473 | 12.1338 | 12.0195 | 11.9052 | 11.7901 | 11.2372 | 10.872 | 10.5144
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | Steady Progression | Headroom (MW) | N/A | 5.2272 | 5.2247 | 5.2225 | 5.2194 | 5.2172 | 5.2132 | 5.2073 | 5.2004 | 5.1945 | 5.1852 | 5.1758 | 5.1659 | 5.1547 | 5.1422 | 5.1304 | 5.0784 | 5.0554 | 5.0336
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | System Transformation | Headroom (MW) | N/A | 7.4696 | 7.4643 | 7.4585 | 7.4492 | 7.4354 | 7.4176 | 7.3905 | 7.3607 | 7.3344 | 7.2953 | 7.2624 | 7.2272 | 7.1903 | 7.1507 | 7.1116 | 6.9234 | 6.8233 | 6.7313
Berkswell 132kV | Coventry Central | COX STREET 33 6 6kV S STN | Primary | 6.6 | -1.502 | 52.4098 | WPD Best View | Headroom (MW) | N/A | 7.7881 | 7.7807 | 7.7719 | 7.757 | 7.7195 | 7.6787 | 7.6267 | 7.5706 | 7.5196 | 7.4491 | 7.3879 | 7.3239 | 7.258 | 7.1894 | 7.1217 | 6.7873 | 6.5716 | 6.3666
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Consumer Transformation | Headroom (MW) | N/A | 15.38 | 15.29 | 15.23 | 15.16 | 15.04 | 14.95 | 14.76 | 14.52 | 14.29 | 14.08 | 13.91 | 13.74 | 13.56 | 13.36 | 13.13 | 11.06 | 8.14 | 4.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Leading the Way | Headroom (MW) | N/A | 15.38 | 15.28 | 15.21 | 15.14 | 14.99 | 14.88 | 14.67 | 14.41 | 14.16 | 13.92 | 13.71 | 13.49 | 13.25 | 12.96 | 12.62 | 10.13 | 6.72 | 2.25
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | Steady Progression | Headroom (MW) | N/A | 15.38 | 15.31 | 15.27 | 15.22 | 15.17 | 15.13 | 15.09 | 15.04 | 15 | 14.96 | 14.91 | 14.86 | 14.82 | 14.77 | 14.72 | 14.5 | 14.17 | 13.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | System Transformation | Headroom (MW) | N/A | 15.38 | 15.3 | 15.25 | 15.19 | 15.12 | 15.06 | 14.99 | 14.93 | 14.86 | 14.79 | 14.73 | 14.67 | 14.6 | 14.53 | 14.47 | 13.88 | 12.5 | 11.17
Berkswell 132kV | Coventry Central | Courthouse Green 33/11kv S Stn | Primary | 11 | -1.4842 | 52.4305 | WPD Best View | Headroom (MW) | N/A | 15.38 | 15.29 | 15.23 | 15.16 | 15.04 | 14.95 | 14.76 | 14.52 | 14.29 | 14.08 | 13.91 | 13.74 | 13.56 | 13.36 | 13.13 | 11.06 | 8.14 | 4.82
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Consumer Transformation | Headroom (MW) | N/A | 6.52 | 6.48 | 6.46 | 6.43 | 6.35 | 6.33 | 6.25 | 6.17 | 6.1 | 6.03 | 5.97 | 5.9 | 5.84 | 5.77 | 5.7 | 5.12 | 4.46 | 3.74
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Leading the Way | Headroom (MW) | N/A | 6.52 | 6.47 | 6.45 | 6.42 | 6.29 | 6.27 | 6.19 | 6.1 | 6.02 | 5.94 | 5.87 | 5.79 | 5.72 | 5.63 | 5.55 | 4.97 | 4.24 | 3.34
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | Steady Progression | Headroom (MW) | N/A | 6.52 | 6.49 | 6.47 | 6.46 | 6.42 | 6.4 | 6.38 | 6.37 | 6.35 | 6.34 | 6.32 | 6.3 | 6.29 | 6.27 | 6.26 | 6.18 | 6.09 | 5.99
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | System Transformation | Headroom (MW) | N/A | 6.52 | 6.48 | 6.46 | 6.44 | 6.38 | 6.36 | 6.34 | 6.33 | 6.31 | 6.27 | 6.24 | 6.2 | 6.17 | 6.14 | 6.11 | 5.94 | 5.61 | 5.26
Berkswell 132kV | Coventry Central | Courthouse Green 33/6 6kv S Stn | Primary | 6.6 | -1.4843 | 52.4302 | WPD Best View | Headroom (MW) | N/A | 6.52 | 6.48 | 6.46 | 6.43 | 6.35 | 6.33 | 6.25 | 6.17 | 6.1 | 6.03 | 5.97 | 5.9 | 5.84 | 5.77 | 5.7 | 5.12 | 4.46 | 3.74
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Consumer Transformation | Headroom (MW) | N/A | 12.16 | 12.12 | 12.1 | 12.07 | 12.02 | 12 | 11.98 | 11.96 | 11.94 | 11.88 | 11.83 | 11.78 | 11.73 | 11.68 | 11.62 | 11.24 | 10.8 | 10.33
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Leading the Way | Headroom (MW) | N/A | 12.16 | 12.11 | 12.09 | 12.07 | 11.99 | 11.97 | 11.95 | 11.93 | 11.9 | 11.84 | 11.79 | 11.73 | 11.68 | 11.62 | 11.55 | 11.16 | 10.68 | 10.08
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | Steady Progression | Headroom (MW) | N/A | 12.16 | 12.12 | 12.1 | 12.09 | 12.06 | 12.04 | 12.02 | 12.01 | 11.99 | 11.97 | 11.96 | 11.94 | 11.92 | 11.91 | 11.89 | 11.81 | 11.72 | 11.63
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | System Transformation | Headroom (MW) | N/A | 12.16 | 12.12 | 12.1 | 12.08 | 12.04 | 12.02 | 12 | 11.99 | 11.97 | 11.95 | 11.93 | 11.91 | 11.89 | 11.88 | 11.86 | 11.76 | 11.53 | 11.28
Berkswell 132kV | Coventry Central | DUNLOP 33 6 6kV S STN | Primary | 6.6 | -1.5122 | 52.4375 | WPD Best View | Headroom (MW) | N/A | 12.16 | 12.12 | 12.1 | 12.07 | 12.02 | 12 | 11.98 | 11.96 | 11.94 | 11.88 | 11.83 | 11.78 | 11.73 | 11.68 | 11.62 | 11.24 | 10.8 | 10.33
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Consumer Transformation | Headroom (MW) | N/A | 17.17 | 17.1 | 17.03 | 16.95 | 16.77 | 16.67 | 16.57 | 16.46 | 16.13 | 15.82 | 15.54 | 15.27 | 14.99 | 14.68 | 14.34 | 11.69 | 8.04 | 3.93
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Leading the Way | Headroom (MW) | N/A | 17.17 | 17.09 | 17.02 | 16.92 | 16.66 | 16.54 | 16.43 | 16.28 | 15.93 | 15.59 | 15.27 | 14.95 | 14.6 | 14.2 | 13.74 | 10.6 | 6.42 | 0.91
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | Steady Progression | Headroom (MW) | N/A | 17.17 | 17.12 | 17.08 | 17.04 | 16.98 | 16.93 | 16.9 | 16.86 | 16.8 | 16.75 | 16.69 | 16.64 | 16.58 | 16.52 | 16.46 | 16.2 | 15.78 | 15.32
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | System Transformation | Headroom (MW) | N/A | 17.17 | 17.12 | 17.06 | 17 | 16.89 | 16.82 | 16.75 | 16.7 | 16.62 | 16.55 | 16.48 | 16.4 | 16.32 | 16.23 | 16.15 | 15.65 | 13.93 | 12.21
Berkswell 132kV | Coventry Central | HOLBROOK LANE 33 6 6kV S STN | Primary | 6.6 | -1.5071 | 52.4356 | WPD Best View | Headroom (MW) | N/A | 17.17 | 17.1 | 17.03 | 16.95 | 16.76 | 16.66 | 16.56 | 16.45 | 16.13 | 15.82 | 15.53 | 15.26 | 14.97 | 14.66 | 14.32 | 11.64 | 7.97 | 3.78
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Consumer Transformation | Headroom (MW) | N/A | 15.41 | 15.31 | 15.25 | 15.19 | 15.02 | 14.95 | 14.88 | 14.74 | 14.45 | 14.15 | 13.88 | 13.65 | 13.41 | 13.15 | 12.88 | 10.77 | 7.84 | 4.57
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Leading the Way | Headroom (MW) | N/A | 15.41 | 15.29 | 15.24 | 15.16 | 14.94 | 14.86 | 14.78 | 14.61 | 14.29 | 13.96 | 13.64 | 13.37 | 13.09 | 12.77 | 12.4 | 9.99 | 6.62 | 2.21
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | Steady Progression | Headroom (MW) | N/A | 15.41 | 15.33 | 15.3 | 15.26 | 15.19 | 15.15 | 15.11 | 15.08 | 15.04 | 15.01 | 14.97 | 14.93 | 14.89 | 14.85 | 14.81 | 14.61 | 14.33 | 13.99
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | System Transformation | Headroom (MW) | N/A | 15.41 | 15.32 | 15.28 | 15.23 | 15.12 | 15.07 | 15.02 | 14.97 | 14.93 | 14.89 | 14.83 | 14.78 | 14.72 | 14.66 | 14.6 | 13.98 | 12.62 | 11.22
Berkswell 132kV | Coventry Central | SANDY LANE 33 6 6kV S STN | Primary | 6.6 | -1.5118 | 52.4178 | WPD Best View | Headroom (MW) | N/A | 15.41 | 15.31 | 15.25 | 15.19 | 15.02 | 14.95 | 14.88 | 14.74 | 14.45 | 14.15 | 13.88 | 13.65 | 13.41 | 13.15 | 12.88 | 10.77 | 7.84 | 4.57
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Consumer Transformation | Headroom (MW) | N/A | 14.69 | 14.6 | 14.53 | 14.45 | 14.33 | 14.26 | 14.18 | 13.99 | 13.79 | 13.62 | 13.46 | 13.31 | 13.08 | 12.82 | 12.54 | 10.74 | 8.07 | 4.98
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Leading the Way | Headroom (MW) | N/A | 14.69 | 14.59 | 14.51 | 14.42 | 14.28 | 14.2 | 14.11 | 13.91 | 13.71 | 13.53 | 13.34 | 13.14 | 12.83 | 12.5 | 12.14 | 9.88 | 6.73 | 2.34
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | Steady Progression | Headroom (MW) | N/A | 14.69 | 14.62 | 14.58 | 14.54 | 14.5 | 14.46 | 14.43 | 14.39 | 14.35 | 14.32 | 14.28 | 14.24 | 14.2 | 14.16 | 14.13 | 13.96 | 13.7 | 13.36
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | System Transformation | Headroom (MW) | N/A | 14.69 | 14.61 | 14.55 | 14.5 | 14.43 | 14.38 | 14.33 | 14.29 | 14.24 | 14.19 | 14.14 | 14.09 | 14.04 | 13.99 | 13.94 | 13.4 | 12.16 | 11.03
Berkswell 132kV | Coventry South | HOLYHEAD ROAD 33 11kV S STN | Primary | 11 | -1.5434 | 52.4171 | WPD Best View | Headroom (MW) | N/A | 14.69 | 14.6 | 14.53 | 14.45 | 14.33 | 14.26 | 14.18 | 13.99 | 13.79 | 13.62 | 13.46 | 13.31 | 13.08 | 12.82 | 12.54 | 10.74 | 8.07 | 4.98
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Consumer Transformation | Headroom (MW) | N/A | 14.2 | 14.14 | 14.11 | 14.08 | 14 | 13.95 | 13.8 | 13.61 | 13.41 | 13.24 | 13.06 | 12.89 | 12.74 | 12.57 | 12.39 | 11.05 | 9.7 | 8.24
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Leading the Way | Headroom (MW) | N/A | 14.2 | 14.14 | 14.11 | 14.08 | 13.97 | 13.9 | 13.71 | 13.51 | 13.28 | 13.07 | 12.87 | 12.69 | 12.51 | 12.32 | 12.12 | 10.83 | 9.31 | 7.58
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | Steady Progression | Headroom (MW) | N/A | 14.2 | 14.15 | 14.13 | 14.1 | 14.07 | 14.05 | 14.03 | 14 | 13.98 | 13.95 | 13.92 | 13.89 | 13.86 | 13.83 | 13.8 | 13.65 | 13.39 | 13.21
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | System Transformation | Headroom (MW) | N/A | 14.2 | 14.15 | 14.13 | 14.09 | 14.04 | 14 | 13.96 | 13.92 | 13.87 | 13.8 | 13.69 | 13.6 | 13.52 | 13.44 | 13.36 | 12.97 | 12.31 | 11.61
Berkswell 132kV | Coventry South | SPON STREET 33 6 6kV S STN | Primary | 6.6 | -1.5176 | 52.4088 | WPD Best View | Headroom (MW) | N/A | 14.2 | 14.14 | 14.11 | 14.08 | 14 | 13.95 | 13.8 | 13.61 | 13.41 | 13.24 | 13.06 | 12.89 | 12.74 | 12.57 | 12.39 | 11.05 | 9.7 | 8.24
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Consumer Transformation | Headroom (MW) | Thermal | 15.17 | 14.97 | 14.8 | 14.59 | 14.16 | 13.79 | 13.23 | 12.45 | 11.86 | 11.22 | 10.57 | 9.93 | 9.35 | 8.72 | 8.06 | 4.53 | 6.84 | -6.46
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Leading the Way | Headroom (MW) | Thermal | 15.17 | 14.95 | 14.78 | 14.57 | 14.09 | 13.71 | 13.12 | 12.53 | 12.1 | 11.46 | 10.85 | 10.25 | 9.69 | 9.11 | 13.82 | -2.2 | -6.64 | -12.15
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | Steady Progression | Headroom (MW) | N/A | 15.17 | 15.04 | 14.98 | 14.93 | 14.86 | 14.79 | 14.73 | 14.66 | 14.61 | 14.35 | 14.26 | 14.17 | 14.06 | 13.99 | 13.94 | 13.91 | 13.58 | 12.8
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | System Transformation | Headroom (MW) | N/A | 15.17 | 15.01 | 14.9 | 14.79 | 14.6 | 14.42 | 14.24 | 14.03 | 13.73 | 13.45 | 13.16 | 12.88 | 12.66 | 12.46 | 13.35 | 4.01 | 2.34 | 0.62
Berkswell 132kV | Coventry South | UNIVERSITY OF WARWICK 33 11kV S STN | Primary | 11 | -1.5646 | 52.3839 | WPD Best View | Headroom (MW) | Thermal | 15.17 | 14.97 | 14.8 | 14.59 | 14.16 | 13.79 | 13.23 | 12.45 | 11.86 | 11.22 | 10.57 | 9.93 | 9.35 | 8.72 | 8.06 | 4.53 | 6.84 | -6.46
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Consumer Transformation | Headroom (MW) | Thermal | 14.39 | 14.31 | 14.24 | 14.17 | 14.03 | 13.81 | 12.61 | 10.43 | 8.74 | 7.13 | 5.36 | 3.62 | 1.84 | -0.01 | -2.06 | -10.93 | -22.43 | -34.61
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Leading the Way | Headroom (MW) | Thermal | 14.39 | 14.3 | 14.24 | 14.18 | 14.03 | 13.8 | 12.52 | 11.46 | 10.63 | 9.43 | 8.33 | 7.3 | 5.91 | 4.44 | 2.83 | -4.78 | -14.77 | -24.93
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | Steady Progression | Headroom (MW) | N/A | 14.39 | 14.33 | 14.3 | 14.28 | 14.24 | 14.21 | 14.18 | 14.15 | 13.97 | 13.08 | 12.89 | 12.68 | 12.21 | 11.84 | 11.43 | 10.79 | 9.82 | 8.56
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | System Transformation | Headroom (MW) | Thermal | 14.39 | 14.32 | 14.28 | 14.25 | 14.18 | 14.14 | 14.1 | 13.97 | 12.88 | 12.22 | 11.4 | 10.6 | 9.81 | 9.16 | 8.42 | 6.17 | 2.54 | -1.48
Berkswell 132kV | Coventry West | COVENTRY WEST 6 6kV S STN | Primary | 6.6 | -1.6054 | 52.4016 | WPD Best View | Headroom (MW) | Thermal | 14.39 | 14.31 | 14.24 | 14.17 | 14.03 | 13.81 | 12.61 | 10.43 | 8.74 | 7.13 | 5.36 | 3.62 | 1.84 | -0.01 | -2.06 | -10.93 | -22.43 | -34.61
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Consumer Transformation | Headroom (MW) | N/A | 7.68 | 7.66 | 7.65 | 7.63 | 7.58 | 7.52 | 7.44 | 7.33 | 7.21 | 7.08 | 6.96 | 6.89 | 6.81 | 6.74 | 6.65 | 5.68 | 5.17 | 4.62
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Leading the Way | Headroom (MW) | N/A | 7.68 | 7.66 | 7.65 | 7.63 | 7.57 | 7.5 | 7.4 | 7.25 | 7.08 | 6.9 | 6.73 | 6.64 | 6.54 | 6.45 | 6.36 | 5.5 | 4.91 | 4.3
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | Steady Progression | Headroom (MW) | N/A | 7.68 | 7.67 | 7.66 | 7.66 | 7.66 | 7.66 | 7.66 | 7.67 | 7.67 | 7.66 | 7.65 | 7.64 | 7.62 | 7.61 | 7.6 | 7.58 | 7.43 | 7.32
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | System Transformation | Headroom (MW) | N/A | 7.68 | 7.67 | 7.66 | 7.66 | 7.64 | 7.61 | 7.57 | 7.51 | 7.43 | 7.35 | 7.27 | 7.23 | 7.19 | 7.15 | 7.11 | 6.75 | 6.52 | 6.28
Berkswell 132kV | Coventry West | HAWKESMILL LANE 33 6 6kV S STN | Primary | 6.6 | -1.5606 | 52.4428 | WPD Best View | Headroom (MW) | N/A | 7.68 | 7.66 | 7.65 | 7.63 | 7.58 | 7.52 | 7.44 | 7.33 | 7.21 | 7.08 | 6.96 | 6.89 | 6.81 | 6.74 | 6.65 | 5.68 | 5.17 | 4.62
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Consumer Transformation | Headroom (MW) | N/A | 12.35 | 12.27 | 12.2 | 12.12 | 11.93 | 11.87 | 11.92 | 11.87 | 11.79 | 11.63 | 11.45 | 11.33 | 11.22 | 11.09 | 10.97 | 10.25 | 9.22 | 8.07
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Leading the Way | Headroom (MW) | N/A | 12.35 | 12.27 | 12.19 | 12.1 | 11.89 | 11.87 | 12.02 | 12.01 | 11.95 | 11.76 | 11.53 | 11.41 | 11.28 | 11.15 | 11.02 | 10.17 | 8.98 | 7.44
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | Steady Progression | Headroom (MW) | N/A | 12.35 | 12.31 | 12.29 | 12.27 | 12.24 | 12.29 | 12.4 | 12.47 | 12.54 | 12.56 | 12.58 | 12.61 | 12.63 | 12.65 | 12.67 | 12.82 | 12.65 | 12.32
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | System Transformation | Headroom (MW) | N/A | 12.35 | 12.29 | 12.25 | 12.2 | 12.12 | 12.14 | 12.28 | 12.32 | 12.34 | 12.27 | 12.19 | 12.15 | 12.11 | 12.07 | 12.03 | 11.9 | 11.34 | 10.77
Berkswell 132kV | Coventry West | JAGUAR CARS BROWNS LANE 33 11kV S STN | Primary | 11 | -1.5558 | 52.438 | WPD Best View | Headroom (MW) | N/A | 12.35 | 12.27 | 12.2 | 12.12 | 11.93 | 11.87 | 11.92 | 11.87 | 11.79 | 11.63 | 11.45 | 11.33 | 11.22 | 11.09 | 10.97 | 10.25 | 9.22 | 8.07
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Consumer Transformation | Headroom (MW) | N/A | 15.35 | 15.17 | 15.03 | 14.86 | 14.47 | 14.18 | 13.9 | 13.65 | 13.41 | 13.18 | 12.97 | 12.76 | 12.54 | 12.3 | 12.05 | 10.04 | 7.11 | 3.85
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Leading the Way | Headroom (MW) | N/A | 15.35 | 15.15 | 15.01 | 14.83 | 14.39 | 14.08 | 13.78 | 13.53 | 13.27 | 13.04 | 12.79 | 12.54 | 12.27 | 11.96 | 11.6 | 9.15 | 5.76 | 1.3
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | Steady Progression | Headroom (MW) | N/A | 15.35 | 15.24 | 15.18 | 15.13 | 15.06 | 14.99 | 14.93 | 14.87 | 14.81 | 14.75 | 14.7 | 14.65 | 14.62 | 14.59 | 14.58 | 14.36 | 14.05 | 13.38
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | System Transformation | Headroom (MW) | N/A | 15.35 | 15.21 | 15.11 | 15.01 | 14.83 | 14.69 | 14.54 | 14.4 | 14.28 | 14.16 | 14.05 | 13.96 | 13.88 | 13.81 | 13.74 | 13.13 | 11.73 | 10.34
Berkswell 132kV | Coventry West | TORRINGTON AVENUE 33 11kV S STN | Primary | 11 | -1.5716 | 52.3994 | WPD Best View | Headroom (MW) | N/A | 15.35 | 15.17 | 15.03 | 14.86 | 14.47 | 14.18 | 13.9 | 13.65 | 13.41 | 13.18 | 12.97 | 12.76 | 12.54 | 12.3 | 12.05 | 10.04 | 7.11 | 3.85
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Consumer Transformation | Headroom (MW) | N/A | 14.16 | 14.29 | 14.38 | 14.42 | 14.49 | 14.45 | 14.41 | 14.16 | 13.86 | 13.52 | 13.1 | 12.6 | 12.05 | 11.55 | 10.93 | 9.73 | 8.14 | 6.23
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Leading the Way | Headroom (MW) | N/A | 14.16 | 14.31 | 14.42 | 14.46 | 14.53 | 14.48 | 14.43 | 14.38 | 14.34 | 14.3 | 14.25 | 14.2 | 13.79 | 13.39 | 12.96 | 11.56 | 9.61 | 8.46
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | Steady Progression | Headroom (MW) | N/A | 14.16 | 14.28 | 14.37 | 14.42 | 14.54 | 14.56 | 14.58 | 14.54 | 14.49 | 14.41 | 14.32 | 14.21 | 13.94 | 13.67 | 13.29 | 12.81 | 12.17 | 11.43
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | System Transformation | Headroom (MW) | N/A | 14.16 | 14.3 | 14.4 | 14.45 | 14.56 | 14.56 | 14.54 | 14.31 | 14.03 | 13.7 | 13.31 | 12.83 | 12.3 | 11.84 | 11.25 | 10.37 | 9.06 | 7.48
Berkswell 132kV | Harbury | GAYDON 33 11kV S STN | Primary | 11 | -1.4852 | 52.2017 | WPD Best View | Headroom (MW) | N/A | 14.16 | 14.28 | 14.37 | 14.42 | 14.54 | 14.56 | 14.58 | 14.53 | 14.48 | 14.4 | 14.31 | 14.2 | 13.93 | 13.65 | 13.27 | 12.78 | 12.13 | 11.39
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Consumer Transformation | Headroom (MW) | Thermal | 12.23 | 12.17 | 12.13 | 12.08 | 11.88 | 11.71 | 11.54 | 10.91 | 10.17 | 9.33 | 8.35 | 7.22 | 5.99 | 4.88 | 3.46 | 0.26 | -3.28 | -7.51
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Leading the Way | Headroom (MW) | Thermal | 12.23 | 12.17 | 12.14 | 12.09 | 11.86 | 11.66 | 11.46 | 11.27 | 11.07 | 10.87 | 10.69 | 10.51 | 9.55 | 8.61 | 7.61 | 4.15 | -0.23 | -2.74
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | Steady Progression | Headroom (MW) | N/A | 12.23 | 12.21 | 12.26 | 12.27 | 12.25 | 12.04 | 12.02 | 11.89 | 11.75 | 11.57 | 11.34 | 11.06 | 10.42 | 9.79 | 8.95 | 7.88 | 6.6 | 5.21
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | System Transformation | Headroom (MW) | Thermal | 12.23 | 12.19 | 12.24 | 12.17 | 12.09 | 12.02 | 11.73 | 11.19 | 10.5 | 9.72 | 8.81 | 7.74 | 6.59 | 5.55 | 4.24 | 2.18 | -0.55 | -3.82
Berkswell 132kV | Harbury | HARBURY 11kV S STN | Primary | 11 | -1.4307 | 52.227 | WPD Best View | Headroom (MW) | N/A | 12.23 | 12.21 | 12.26 | 12.27 | 12.24 | 12.02 | 11.97 | 11.8 | 11.64 | 11.42 | 11.18 | 10.89 | 10.24 | 9.6 | 8.74 | 7.52 | 6.21 | 4.78
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Consumer Transformation | Headroom (MW) | Thermal | 9.06 | 8.96 | 8.48 | 8.37 | 8.08 | 7.84 | 7.61 | 7.25 | 6.86 | 6.46 | 6.03 | 5.56 | 5.06 | 4.57 | 3.98 | 1.58 | -1.18 | -4.33
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Leading the Way | Headroom (MW) | Thermal | 9.06 | 8.95 | 8.47 | 8.36 | 8.01 | 7.75 | 7.49 | 7.25 | 7.01 | 6.78 | 6.57 | 6.34 | 5.86 | 5.38 | 4.85 | 2.26 | -1 | -4.18
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | Steady Progression | Headroom (MW) | N/A | 9.06 | 9.01 | 8.99 | 8.58 | 8.54 | 8.5 | 8.47 | 8.39 | 8.32 | 8.24 | 8.14 | 8.04 | 7.83 | 7.63 | 7.37 | 7.12 | 6.5 | 5.73
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | System Transformation | Headroom (MW) | N/A | 9.06 | 8.98 | 8.94 | 8.49 | 8.37 | 8.26 | 8.13 | 7.87 | 7.57 | 7.26 | 6.91 | 6.53 | 6.12 | 5.76 | 5.33 | 4.41 | 2.78 | 0.98
Berkswell 132kV | Harbury | SOUTHAM 33 11kV S STN | Primary | 11 | -1.3905 | 52.2731 | WPD Best View | Headroom (MW) | N/A | 9.06 | 9.01 | 8.99 | 8.58 | 8.54 | 8.5 | 8.45 | 8.37 | 8.29 | 8.2 | 8.1 | 7.99 | 7.78 | 7.58 | 7.32 | 6.95 | 6.32 | 5.5
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Consumer Transformation | Headroom (MW) | N/A | 40.01 | 39.54 | 39.16 | 38.7 | 37.68 | 36.92 | 36.33 | 35.53 | 34.77 | 33.99 | 33.08 | 32.12 | 31.12 | 30.12 | 28.98 | 23.27 | 15.42 | 6.57
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Leading the Way | Headroom (MW) | N/A | 40.01 | 39.51 | 39.11 | 38.62 | 37.49 | 36.71 | 36.16 | 35.54 | 35 | 34.42 | 33.75 | 33.07 | 32.06 | 30.97 | 29.77 | 22.92 | 13.8 | 3
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | Steady Progression | Headroom (MW) | N/A | 40.01 | 39.72 | 39.6 | 39.48 | 39.36 | 39.24 | 39.2 | 39.09 | 39 | 38.86 | 38.71 | 38.56 | 38.31 | 38.09 | 37.8 | 37.88 | 36.28 | 34.13
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | System Transformation | Headroom (MW) | N/A | 40.01 | 39.64 | 39.4 | 39.15 | 38.73 | 38.39 | 38.15 | 37.7 | 37.24 | 36.74 | 36.14 | 35.51 | 34.89 | 34.34 | 33.71 | 32 | 27.89 | 23.26
Berkswell 132kV | Warwick 132 11 (GT1B) | WARWICK 11kV S STN | Primary | 11 | -1.5621 | 52.286 | WPD Best View | Headroom (MW) | N/A | 40.01 | 39.54 | 39.16 | 38.7 | 37.68 | 36.92 | 36.34 | 35.56 | 34.81 | 34.04 | 33.13 | 32.17 | 31.18 | 30.18 | 29.05 | 23.47 | 15.64 | 6.85
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Consumer Transformation | Headroom (MW) | Thermal | 6.19 | 6.04 | 5.88 | 5.74 | 5.32 | 4.98 | 4.65 | 4.32 | 4.01 | 3.76 | 3.49 | 3.23 | 2.97 | 2.65 | 2.33 | -0.38 | -3.61 | -6.51
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Leading the Way | Headroom (MW) | Thermal | 6.19 | 6.02 | 5.86 | 5.72 | 5.26 | 4.93 | 4.57 | 4.24 | 3.91 | 3.65 | 3.37 | 3.09 | 2.77 | 2.42 | 2.04 | -1.75 | -5.96 | -9.98
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | Steady Progression | Headroom (MW) | N/A | 6.19 | 6.13 | 6.11 | 6.13 | 6.1 | 6.07 | 6.03 | 5.99 | 5.94 | 5.9 | 5.85 | 5.82 | 5.79 | 5.76 | 5.75 | 5.89 | 5.58 | 4.93
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | System Transformation | Headroom (MW) | N/A | 6.19 | 6.09 | 6.01 | 5.97 | 5.81 | 5.67 | 5.5 | 5.34 | 5.17 | 5.04 | 4.89 | 4.75 | 4.63 | 4.53 | 4.44 | 3.19 | 1.3 | 0.03
Berkswell 132kV | Warwick 33 | BANBURY ROAD 33 11kV S STN | Primary | 11 | -1.565 | 52.2576 | WPD Best View | Headroom (MW) | Thermal | 6.19 | 6.08 | 5.98 | 5.91 | 5.69 | 5.5 | 5.31 | 5.11 | 4.91 | 4.76 | 4.6 | 4.44 | 4.29 | 4.14 | 4 | 2.44 | 0.51 | -1.12
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Consumer Transformation | Headroom (MW) | N/A | 12.43 | 12.33 | 12.33 | 12.25 | 12.13 | 11.88 | 11.59 | 11.31 | 11.05 | 10.82 | 10.6 | 10.38 | 10.15 | 9.91 | 9.64 | 7.42 | 4.51 | 1.23
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Leading the Way | Headroom (MW) | Thermal | 12.43 | 12.32 | 12.33 | 12.24 | 12.09 | 11.81 | 11.48 | 11.19 | 10.91 | 10.66 | 10.39 | 10.12 | 9.82 | 9.49 | 9.11 | 6.51 | 3.1 | -1.39
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | Steady Progression | Headroom (MW) | N/A | 12.43 | 12.35 | 12.38 | 12.34 | 12.3 | 12.26 | 12.23 | 12.19 | 12.15 | 12.11 | 12.07 | 12.02 | 11.97 | 11.93 | 11.88 | 11.68 | 11.32 | 10.95
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | System Transformation | Headroom (MW) | N/A | 12.43 | 12.34 | 12.36 | 12.31 | 12.24 | 12.18 | 12.12 | 12.05 | 11.98 | 11.87 | 11.75 | 11.65 | 11.57 | 11.5 | 11.43 | 10.71 | 9.38 | 8.11
Berkswell 132kV | Warwick 33 | CAMPION HILLS 33 11kV S STN | Primary | 11 | -1.516 | 52.2964 | WPD Best View | Headroom (MW) | N/A | 12.43 | 12.33 | 12.33 | 12.25 | 12.13 | 11.88 | 11.59 | 11.31 | 11.06 | 10.83 | 10.61 | 10.39 | 10.16 | 9.92 | 9.65 | 7.44 | 4.53 | 1.26
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Consumer Transformation | Headroom (MW) | Thermal | 9.97 | 9.81 | 9.68 | 9.54 | 9.18 | 8.91 | 8.66 | 7.72 | 6.61 | 5.35 | 3.8 | 2 | 0.06 | -1.73 | -4.01 | -8.5 | -14.1 | -20.85
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Leading the Way | Headroom (MW) | Thermal | 9.97 | 9.8 | 9.66 | 9.51 | 9.11 | 8.83 | 8.57 | 8.33 | 8.11 | 7.91 | 7.68 | 7.46 | 5.97 | 4.53 | 2.98 | -2.17 | -9.22 | -13.32
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | Steady Progression | Headroom (MW) | Thermal | 9.97 | 9.87 | 9.83 | 9.79 | 9.74 | 9.68 | 9.63 | 9.4 | 9.18 | 8.9 | 8.55 | 8.11 | 7.09 | 6.09 | 4.75 | 3.14 | 1.26 | -0.99
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | System Transformation | Headroom (MW) | Thermal | 9.97 | 9.84 | 9.76 | 9.68 | 9.53 | 9.4 | 9.27 | 8.45 | 7.4 | 6.23 | 4.76 | 3.05 | 1.2 | -0.46 | -2.54 | -5.65 | -10.06 | -15.39
Berkswell 132kV | Warwick 33 | CLAVERDON 33 11kV S STN | Primary | 11 | -1.6953 | 52.2769 | WPD Best View | Headroom (MW) | Thermal | 9.97 | 9.85 | 9.78 | 9.71 | 9.56 | 9.44 | 9.33 | 8.84 | 8.3 | 7.65 | 6.82 | 5.83 | 4.45 | 3.15 | 1.47 | -1.08 | -4.26 | -8.13
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Consumer Transformation | Headroom (MW) | Thermal | 15.3077 | 15.1544 | 14.9835 | 14.7535 | 14.2407 | 13.7279 | 13.207 | 12.3465 | 11.4152 | 10.431 | 9.2634 | 7.9603 | 6.5835 | 5.2867 | 3.7873 | -0.022369 | -5.54 | -13.38
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Leading the Way | Headroom (MW) | Thermal | 18.86 | 18.74 | 18.6047 | 18.3086 | 17.6593 | 16.9827 | 16.3077 | 15.6045 | 14.9204 | 14.2793 | 13.64 | 12.9783 | 11.5266 | 10.1301 | 8.7072 | 3.5201 | -4.41 | -11.9
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | Steady Progression | Headroom (MW) | N/A | 9.7028 | 9.6752 | 9.6585 | 9.64 | 9.6158 | 9.5664 | 9.5118 | 9.3987 | 9.289 | 9.1542 | 8.993 | 8.805 | 8.4328 | 8.0638 | 7.5864 | 6.7386 | 5.8956 | 5.047
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | System Transformation | Headroom (MW) | Fault level | 12.8507 | 12.778 | 12.7074 | 12.6205 | 12.4641 | 12.274 | 12.0512 | 11.5462 | 10.9648 | 10.3444 | 9.5722 | 8.6887 | 7.7455 | 6.869 | 5.8191 | 3.6504 | 1.2018 | -1.633
Berkswell 132kV | Warwick 33 | KENILWORTH 33 11kV S STN | Primary | 11 | -1.5846 | 52.3371 | WPD Best View | Headroom (MW) | Fault level | 13.2567 | 13.124 | 12.9759 | 12.7768 | 12.3327 | 11.8886 | 11.4375 | 10.6923 | 9.8857 | 9.0334 | 8.0222 | 6.8937 | 5.7015 | 4.5784 | 3.2799 | -0.019372 | -5.54 | -13.38
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Consumer Transformation | Headroom (MW) | N/A | 13.08 | 12.99 | 13 | 12.93 | 12.84 | 12.76 | 12.63 | 12.5 | 12.37 | 12.25 | 12.13 | 11.99 | 11.87 | 11.75 | 11.62 | 10.29 | 9.19 | 8
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Leading the Way | Headroom (MW) | N/A | 13.08 | 12.99 | 13 | 12.93 | 12.83 | 12.76 | 12.62 | 12.46 | 12.31 | 12.16 | 12 | 11.84 | 11.7 | 11.54 | 11.38 | 9.66 | 8.42 | 6.89
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | Steady Progression | Headroom (MW) | N/A | 10.9477 | 10.9461 | 10.9433 | 10.9411 | 10.9383 | 10.9321 | 10.9249 | 10.9169 | 10.9084 | 10.8982 | 10.887 | 10.8748 | 10.8636 | 10.8521 | 10.8412 | 10.7955 | 10.7503 | 10.7042
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | System Transformation | Headroom (MW) | N/A | 13.08 | 13.01 | 13.03 | 12.99 | 12.99 | 12.97 | 12.9 | 12.83 | 12.76 | 12.68 | 12.61 | 12.53 | 12.47 | 12.42 | 12.36 | 11.68 | 11.14 | 10.58
Berkswell 132kV | Warwick 33 | LOCKHEED 33 11kV S STN | Primary | 11 | -1.5403 | 52.272 | WPD Best View | Headroom (MW) | N/A | 13.08 | 12.99 | 13 | 12.93 | 12.84 | 12.76 | 12.63 | 12.5 | 12.37 | 12.25 | 12.13 | 11.99 | 11.87 | 11.75 | 11.62 | 10.29 | 9.19 | 8
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Consumer Transformation | Headroom (MW) | N/A | 7.52 | 7.46 | 7.42 | 7.37 | 7.25 | 7.14 | 7.03 | 6.93 | 6.83 | 6.74 | 6.66 | 6.58 | 6.5 | 6.42 | 6.33 | 5.55 | 4.8 | 3.93
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Leading the Way | Headroom (MW) | N/A | 7.52 | 7.46 | 7.41 | 7.36 | 7.22 | 7.1 | 6.97 | 6.85 | 6.72 | 6.59 | 6.5 | 6.4 | 6.3 | 6.19 | 6.08 | 5.28 | 4.42 | 3.32
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | Steady Progression | Headroom (MW) | N/A | 7.52 | 7.48 | 7.47 | 7.45 | 7.43 | 7.41 | 7.39 | 7.37 | 7.35 | 7.33 | 7.32 | 7.3 | 7.29 | 7.28 | 7.27 | 7.19 | 7.05 | 6.89
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | System Transformation | Headroom (MW) | N/A | 7.52 | 7.47 | 7.44 | 7.41 | 7.36 | 7.3 | 7.24 | 7.18 | 7.12 | 7.06 | 7.02 | 6.98 | 6.95 | 6.92 | 6.89 | 6.7 | 6.34 | 5.99
Berkswell 132kV | Warwick 33 | PRINCETHORPE 33 11kV S STN | Primary | 11 | -1.4146 | 52.3302 | WPD Best View | Headroom (MW) | N/A | 7.52 | 7.48 | 7.46 | 7.43 | 7.39 | 7.35 | 7.3 | 7.25 | 7.21 | 7.16 | 7.13 | 7.1 | 7.07 | 7.04 | 7.01 | 6.81 | 6.54 | 6.23
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Consumer Transformation | Headroom (MW) | N/A | 13.21 | 13.17 | 13.15 | 13.13 | 13.09 | 13.06 | 13.03 | 13 | 12.98 | 12.95 | 12.92 | 12.89 | 12.86 | 12.83 | 12.8 | 12.37 | 11.71 | 10.98
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Leading the Way | Headroom (MW) | N/A | 13.21 | 13.17 | 13.15 | 13.11 | 13.07 | 13.04 | 13.01 | 12.98 | 12.94 | 12.91 | 12.88 | 12.84 | 12.8 | 12.76 | 12.72 | 12.16 | 11.4 | 10.38
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | Steady Progression | Headroom (MW) | N/A | 13.21 | 13.18 | 13.17 | 13.15 | 13.13 | 13.12 | 13.1 | 13.09 | 13.07 | 13.05 | 13.03 | 13.01 | 12.99 | 12.97 | 12.95 | 12.87 | 12.76 | 12.64
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | System Transformation | Headroom (MW) | N/A | 13.21 | 13.18 | 13.16 | 13.14 | 13.11 | 13.09 | 13.07 | 13.05 | 13.03 | 13.01 | 12.98 | 12.96 | 12.94 | 12.92 | 12.9 | 12.79 | 12.62 | 12.4
Berkswell 132kV | Warwick 33 | Tournament Fields 33/11kv S Stn | Primary | 11 | -1.6112 | 52.2651 | WPD Best View | Headroom (MW) | N/A | 13.21 | 13.17 | 13.15 | 13.13 | 13.09 | 13.06 | 13.03 | 13 | 12.98 | 12.95 | 12.92 | 12.89 | 12.86 | 12.83 | 12.8 | 12.37 | 11.71 | 10.98
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Consumer Transformation | Headroom (MW) | N/A | 16.39 | 16.19 | 16.02 | 15.83 | 15.34 | 14.96 | 14.61 | 14.28 | 13.97 | 13.68 | 13.39 | 13.09 | 12.8 | 12.48 | 12.14 | 9.69 | 6.3 | 2.56
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Leading the Way | Headroom (MW) | Thermal | 16.39 | 16.17 | 16 | 15.79 | 15.25 | 14.86 | 14.49 | 14.15 | 13.84 | 13.54 | 13.21 | 12.87 | 12.51 | 12.11 | 11.67 | 8.77 | 4.9 | -0.16
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | Steady Progression | Headroom (MW) | N/A | 16.39 | 16.27 | 16.2 | 16.14 | 16.07 | 15.99 | 15.91 | 15.83 | 15.77 | 15.71 | 15.64 | 15.59 | 15.56 | 15.53 | 15.52 | 15.43 | 14.92 | 14.13
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | System Transformation | Headroom (MW) | N/A | 16.39 | 16.23 | 16.12 | 16 | 15.79 | 15.62 | 15.42 | 15.25 | 15.09 | 14.94 | 14.8 | 14.67 | 14.55 | 14.44 | 14.34 | 13.66 | 12.02 | 10.44
Berkswell 132kV | Warwick 33 | WISE STREET 33 11kV S STN | Primary | 11 | -1.5329 | 52.2833 | WPD Best View | Headroom (MW) | N/A | 16.39 | 16.19 | 16.02 | 15.83 | 15.34 | 14.96 | 14.61 | 14.28 | 13.97 | 13.68 | 13.39 | 13.09 | 12.8 | 12.48 | 12.14 | 9.69 | 6.3 | 2.56
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Consumer Transformation | Headroom (MW) | Thermal | 6.95 | 6.87 | 6.8 | 6.72 | 6.53 | 6.09 | 5.61 | 3.98 | 2.05 | -0.16 | -2.89 | -6.06 | -9.49 | -12.62 | -16.5 | -24.55 | -33.69 | -44.97
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Leading the Way | Headroom (MW) | Thermal | 6.95 | 6.86 | 6.79 | 6.71 | 6.5 | 5.85 | 5.16 | 4.44 | 3.69 | 2.91 | 2.41 | 1.89 | -0.87 | -3.51 | -6.29 | -15.29 | -26.79 | -32.4
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | Steady Progression | Headroom (MW) | Thermal | 6.95 | 6.91 | 6.88 | 6.86 | 6.83 | 6.78 | 6.73 | 6.38 | 6.05 | 5.61 | 5.02 | 4.27 | 2.49 | 0.74 | -1.63 | -4.73 | -7.98 | -11.31
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | System Transformation | Headroom (MW) | Thermal | 6.95 | 6.89 | 6.84 | 6.8 | 6.72 | 6.55 | 6.34 | 4.9 | 3.05 | 1.08 | -1.42 | -4.35 | -7.54 | -10.41 | -14.02 | -19.41 | -26.94 | -36.3
Bicker Fen 132kV | Grantham | BILLINGBOROUGH 33 11kV S STN | Primary | 11 | -0.365 | 52.8948 | WPD Best View | Headroom (MW) | Thermal | 6.95 | 6.88 | 6.83 | 6.76 | 6.63 | 6.46 | 6.29 | 5.45 | 4.48 | 3.33 | 1.86 | 0.12 | -2.31 | -4.61 | -7.59 | -12.31 | -17.6 | -23.71
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Consumer Transformation | Headroom (MW) | Thermal | 5.69 | 5.65 | 5.62 | 5.59 | 5.53 | 5.45 | 5.36 | 4.81 | 4.12 | 3.31 | 2.28 | 1.07 | -0.23 | -1.41 | -2.89 | -5.31 | -8.06 | -11.49
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Leading the Way | Headroom (MW) | Thermal | 5.69 | 5.65 | 5.62 | 5.59 | 5.53 | 5.42 | 5.3 | 5.17 | 5.03 | 4.89 | 4.83 | 4.76 | 3.8 | 2.87 | 1.9 | -0.75 | -4.32 | -5.22
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | Steady Progression | Headroom (MW) | Thermal | 5.69 | 5.66 | 5.64 | 5.63 | 5.61 | 5.59 | 5.57 | 5.44 | 5.3 | 5.13 | 4.89 | 4.58 | 3.85 | 3.13 | 2.16 | 0.85 | -0.46 | -1.79
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | System Transformation | Headroom (MW) | Thermal | 5.69 | 5.65 | 5.63 | 5.61 | 5.58 | 5.53 | 5.47 | 4.95 | 4.27 | 3.49 | 2.48 | 1.29 | 0.01 | -1.15 | -2.61 | -4.7 | -7.3 | -10.55
Bicker Fen 132kV | Grantham | EASTON 33 11kV S STN | Primary | 11 | -0.6075 | 52.8279 | WPD Best View | Headroom (MW) | Thermal | 5.69 | 5.65 | 5.62 | 5.59 | 5.53 | 5.45 | 5.36 | 4.81 | 4.12 | 3.31 | 2.28 | 1.07 | -0.23 | -1.41 | -2.89 | -5.31 | -8.06 | -11.49
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Consumer Transformation | Headroom (MW) | Thermal | 15.55 | 15.33 | 15.07 | 14.76 | 14.09 | 13.49 | 9.56 | 2.16 | -3.48 | -8.93 | -14.9 | -20.78 | -26.63 | -32.8 | -39.66 | -68.71 | -116.7231 | -171.396
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Leading the Way | Headroom (MW) | Thermal | 15.55 | 15.31 | 15.09 | 14.81 | 14.16 | 13.58 | 9.34 | 5.78 | 3.01 | -1.1 | -4.81 | -8.32 | -13 | -17.99 | -23.36 | -46.99 | -99.7328 | -156.2032
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | Steady Progression | Headroom (MW) | Thermal | 15.55 | 15.43 | 15.37 | 15.31 | 15.23 | 15.15 | 15.06 | 14.86 | 14.12 | 10.7 | 9.86 | 8.84 | 7.17 | 5.92 | 4.57 | 2.26 | -0.48 | -3.72
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | System Transformation | Headroom (MW) | Thermal | 15.55 | 15.38 | 15.26 | 15.13 | 14.88 | 14.64 | 14.36 | 13.61 | 9.97 | 7.82 | 5.18 | 2.57 | -0.01 | -2.15 | -4.63 | -11.84 | -22.5 | -34.36
Bicker Fen 132kV | Grantham | NEW BEACON ROAD GRANTHAM 33 11kV S STN | Primary | 11 | -0.6291 | 52.9133 | WPD Best View | Headroom (MW) | Thermal | 15.55 | 15.33 | 15.07 | 14.76 | 14.1 | 13.49 | 9.57 | 2.16 | -3.48 | -8.92 | -14.89 | -20.76 | -26.62 | -32.78 | -39.64 | -68.69 | -105.56 | -144.27
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Consumer Transformation | Headroom (MW) | Thermal | 7 | 6.95 | 6.91 | 6.86 | 6.75 | 6.61 | 6.45 | 6.15 | 5.8 | 5.41 | 5.01 | 4.54 | 4.04 | 3.58 | 3.02 | 1.5 | -0.07 | -1.93
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Leading the Way | Headroom (MW) | Thermal | 7 | 6.95 | 6.91 | 6.85 | 6.73 | 6.55 | 6.36 | 6.16 | 5.95 | 5.72 | 5.61 | 5.49 | 5.08 | 4.68 | 4.26 | 2.68 | 0.75 | -0.5
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | Steady Progression | Headroom (MW) | N/A | 7 | 6.97 | 6.96 | 6.95 | 6.93 | 6.91 | 6.88 | 6.82 | 6.76 | 6.69 | 6.59 | 6.48 | 6.22 | 5.97 | 5.64 | 5.22 | 4.71 | 4.13
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | System Transformation | Headroom (MW) | N/A | 7 | 6.96 | 6.94 | 6.91 | 6.86 | 6.78 | 6.69 | 6.45 | 6.15 | 5.82 | 5.45 | 5.03 | 4.58 | 4.17 | 3.66 | 2.82 | 1.65 | 0.28
Bicker Fen 132kV | Grantham | SKILLINGTON 33 11kV S STN | Primary | 11 | -0.6766 | 52.812 | WPD Best View | Headroom (MW) | Thermal | 7 | 6.95 | 6.91 | 6.86 | 6.75 | 6.61 | 6.45 | 6.15 | 5.8 | 5.41 | 5.01 | 4.54 | 4.04 | 3.58 | 3.02 | 1.5 | -0.07 | -1.93
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Consumer Transformation | Headroom (MW) | Thermal | 5.07 | 5 | 4.79 | 4.71 | 4.52 | 4.35 | 4.18 | 3.88 | 3.56 | 3.2 | 2.82 | 2.39 | 1.93 | 1.5 | 0.96 | -0.7 | -2.76 | -5.16
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Leading the Way | Headroom (MW) | Thermal | 5.07 | 4.99 | 4.78 | 4.7 | 4.47 | 4.28 | 4.09 | 3.9 | 3.72 | 3.54 | 3.41 | 3.28 | 2.88 | 2.48 | 2.05 | 0.18 | -2.28 | -4.44
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | Steady Progression | Headroom (MW) | N/A | 5.07 | 5.03 | 5 | 4.98 | 4.95 | 4.92 | 4.89 | 4.83 | 4.77 | 4.7 | 4.62 | 4.52 | 4.3 | 4.09 | 3.81 | 3.48 | 3.02 | 2.38
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | System Transformation | Headroom (MW) | Thermal | 5.07 | 5.01 | 4.97 | 4.79 | 4.7 | 4.61 | 4.52 | 4.29 | 4.04 | 3.75 | 3.42 | 3.05 | 2.65 | 2.3 | 1.86 | 1.11 | -0.24 | -1.8
Bicker Fen 132kV | Skegness | ALFORD 33 11kV S STN | Primary | 11 | 0.1883 | 53.2546 | WPD Best View | Headroom (MW) | Thermal | 5.07 | 5.01 | 4.97 | 4.79 | 4.7 | 4.61 | 4.52 | 4.29 | 4.04 | 3.75 | 3.42 | 3.05 | 2.65 | 2.3 | 1.86 | 1.11 | -0.24 | -1.8
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Consumer Transformation | Headroom (MW) | Thermal | 7.63 | 7.56 | 7.49 | 7.41 | 7.24 | 7.08 | 6.91 | 6.35 | 5.71 | 4.98 | 4.08 | 3.03 | 1.91 | 0.87 | -0.42 | -3.01 | -6.21 | -10.06
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Leading the Way | Headroom (MW) | Thermal | 7.63 | 7.55 | 7.49 | 7.41 | 7.23 | 7.04 | 6.85 | 6.66 | 6.47 | 6.28 | 6.14 | 6 | 5.13 | 4.29 | 3.4 | 0.48 | -3.53 | -5.66
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | Steady Progression | Headroom (MW) | N/A | 7.63 | 7.58 | 7.55 | 7.53 | 7.5 | 7.46 | 7.43 | 7.3 | 7.17 | 7 | 6.79 | 6.53 | 5.92 | 5.33 | 4.54 | 3.48 | 2.36 | 1.08
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | System Transformation | Headroom (MW) | Thermal | 7.63 | 7.57 | 7.53 | 7.48 | 7.41 | 7.33 | 7.23 | 6.76 | 6.16 | 5.5 | 4.65 | 3.66 | 2.59 | 1.63 | 0.42 | -1.39 | -3.97 | -7.09
Bicker Fen 132kV | Skegness | CHAPEL ST LEONARDS 33 11kV S STN | Primary | 11 | 0.3159 | 53.2251 | WPD Best View | Headroom (MW) | Thermal | 7.63 | 7.57 | 7.53 | 7.48 | 7.41 | 7.33 | 7.23 | 6.76 | 6.16 | 5.5 | 4.65 | 3.66 | 2.59 | 1.63 | 0.42 | -1.39 | -3.97 | -7.09
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Consumer Transformation | Headroom (MW) | Thermal | 10.96 | 10.75 | 10.61 | 10.46 | 10.05 | 9.68 | 9.21 | 8.48 | 7.72 | 6.92 | 6.14 | 5.35 | 4.53 | 3.72 | 2.7 | -0.59 | -3.83 | -7.56
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Leading the Way | Headroom (MW) | Thermal | 10.96 | 10.73 | 10.6 | 10.44 | 10.02 | 9.54 | 9.03 | 8.36 | 7.69 | 6.94 | 6.36 | 5.79 | 4.95 | 4.16 | 3.29 | -0.34 | -4.53 | -8.68
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | Steady Progression | Headroom (MW) | N/A | 10.96 | 10.8 | 10.74 | 10.68 | 10.59 | 10.5 | 10.43 | 10.29 | 10.15 | 10.01 | 9.85 | 9.7 | 9.44 | 9.19 | 8.87 | 8.38 | 7.64 | 6.7
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | System Transformation | Headroom (MW) | N/A | 10.96 | 10.78 | 10.68 | 10.59 | 10.38 | 10.14 | 9.94 | 9.47 | 8.96 | 8.41 | 7.86 | 7.34 | 6.82 | 6.32 | 5.62 | 4.35 | 2.45 | 0.34
Bicker Fen 132kV | Skegness | HORNCASTLE 33 11kV S STN | Primary | 11 | -0.1122 | 53.2181 | WPD Best View | Headroom (MW) | N/A | 10.96 | 10.78 | 10.68 | 10.59 | 10.38 | 10.14 | 9.94 | 9.47 | 8.96 | 8.41 | 7.86 | 7.34 | 6.82 | 6.32 | 5.62 | 4.35 | 2.45 | 0.34
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Consumer Transformation | Headroom (MW) | N/A | 12.74 | 12.67 | 12.62 | 12.58 | 12.46 | 12.39 | 12.22 | 11.96 | 11.69 | 11.4 | 10.97 | 10.47 | 9.94 | 9.44 | 8.79 | 7.18 | 5.6 | 3.78
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Leading the Way | Headroom (MW) | N/A | 12.74 | 12.66 | 12.62 | 12.57 | 12.48 | 12.36 | 12.19 | 11.93 | 11.67 | 11.35 | 11.02 | 10.71 | 10.24 | 9.78 | 9.26 | 7.97 | 6.08 | 4.24
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | Steady Progression | Headroom (MW) | N/A | 12.74 | 12.67 | 12.64 | 12.6 | 12.55 | 12.51 | 12.48 | 12.41 | 12.35 | 12.29 | 12.23 | 12.19 | 12.15 | 12.1 | 12.06 | 11.84 | 11.35 | 10.76
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | System Transformation | Headroom (MW) | N/A | 12.74 | 12.67 | 12.63 | 12.59 | 12.51 | 12.44 | 12.37 | 12.22 | 12.07 | 11.9 | 11.73 | 11.6 | 11.3 | 11 | 10.55 | 9.85 | 8.76 | 7.53
Bicker Fen 132kV | Skegness | INGOLDMELLS 33 11kV S STN | Primary | 11 | 0.3314 | 53.1802 | WPD Best View | Headroom (MW) | N/A | 12.74 | 12.67 | 12.63 | 12.59 | 12.51 | 12.44 | 12.37 | 12.22 | 12.07 | 11.9 | 11.73 | 11.6 | 11.3 | 11 | 10.55 | 9.85 | 8.76 | 7.53
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Consumer Transformation | Headroom (MW) | Thermal | 4.66 | 4.54 | 4.46 | 4.37 | 4.15 | 3.88 | 3.57 | 2.73 | 1.73 | 0.62 | -0.67 | -2.16 | -3.77 | -5.24 | -7.09 | -11.13 | -15.49 | -20.78
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Leading the Way | Headroom (MW) | Thermal | 4.66 | 4.53 | 4.45 | 4.35 | 4.11 | 3.76 | 3.37 | 2.99 | 2.57 | 2.15 | 1.96 | 1.78 | 0.52 | -0.69 | -1.98 | -6.36 | -11.78 | -14.46
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | Steady Progression | Headroom (MW) | Thermal | 4.66 | 4.58 | 4.55 | 4.52 | 4.49 | 4.45 | 4.38 | 4.18 | 3.99 | 3.76 | 3.45 | 3.08 | 2.22 | 1.38 | 0.23 | -1.2 | -2.8 | -4.59
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | System Transformation | Headroom (MW) | Thermal | 4.66 | 4.56 | 4.51 | 4.46 | 4.36 | 4.21 | 4.01 | 3.28 | 2.37 | 1.38 | 0.16 | -1.27 | -2.8 | -4.17 | -5.9 | -8.54 | -12.07 | -16.38
Bicker Fen 132kV | Skegness | SPILSBY 33 11kV S STN | Primary | 11 | 0.1046 | 53.1686 | WPD Best View | Headroom (MW) | Thermal | 4.66 | 4.56 | 4.51 | 4.46 | 4.36 | 4.21 | 4.01 | 3.28 | 2.37 | 1.38 | 0.16 | -1.27 | -2.8 | -4.17 | -5.9 | -8.54 | -12.07 | -16.38
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Consumer Transformation | Headroom (MW) | Thermal | 8.03 | 7.91 | 7.8 | 7.68 | 7.33 | 7.06 | 5.7 | 5.45 | 5.24 | 5.03 | 4.85 | 4.66 | 4.46 | 4.25 | 4.02 | 2.34 | -0.08 | -2.8
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Leading the Way | Headroom (MW) | Thermal | 8.03 | 7.9 | 7.79 | 7.66 | 7.28 | 6.99 | 5.62 | 5.37 | 5.15 | 4.94 | 4.72 | 4.5 | 4.26 | 3.99 | 3.68 | 1.63 | -1.14 | -4.82
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | Steady Progression | Headroom (MW) | N/A | 8.03 | 7.96 | 7.92 | 7.89 | 7.85 | 7.8 | 7.76 | 7.71 | 7.67 | 7.62 | 7.59 | 7.56 | 7.53 | 7.51 | 7.5 | 7.49 | 7.3 | 6.8
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | System Transformation | Headroom (MW) | N/A | 8.03 | 7.94 | 7.87 | 7.81 | 7.68 | 7.56 | 6.88 | 6.76 | 6.65 | 6.55 | 6.46 | 6.39 | 6.32 | 6.27 | 6.21 | 5.8 | 4.67 | 3.52
Bicker Fen 132kV | Skegness | TRUSTHORPE 33 11kV S STN | Primary | 11 | 0.2642 | 53.3259 | WPD Best View | Headroom (MW) | N/A | 8.03 | 7.94 | 7.87 | 7.81 | 7.68 | 7.56 | 6.88 | 6.76 | 6.65 | 6.55 | 6.46 | 6.39 | 6.32 | 6.27 | 6.21 | 5.8 | 4.67 | 3.52
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Consumer Transformation | Headroom (MW) | Thermal | 17.77 | 17.52 | 17.34 | 17.13 | 16.5 | 15.95 | 15.36 | 14.33 | 13.23 | 12.04 | 10.62 | 9.07 | 7.43 | 5.88 | 3.99 | -2.87 | -9.95 | -18.6
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Leading the Way | Headroom (MW) | Thermal | 17.77 | 17.49 | 17.31 | 17.08 | 16.39 | 15.73 | 15.06 | 14.38 | 13.71 | 13.04 | 12.34 | 11.66 | 10.16 | 8.68 | 7.08 | -1.41 | -10.46 | -18.72
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | Steady Progression | Headroom (MW) | N/A | 17.77 | 17.61 | 17.54 | 17.46 | 17.36 | 17.25 | 17.14 | 16.92 | 16.71 | 16.47 | 16.17 | 15.85 | 15.18 | 14.53 | 13.67 | 12.53 | 11.16 | 9.18
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | System Transformation | Headroom (MW) | Thermal | 17.77 | 17.57 | 17.45 | 17.32 | 17.04 | 16.81 | 16.56 | 15.83 | 14.96 | 14.09 | 12.99 | 11.79 | 10.54 | 9.4 | 7.95 | 4.34 | -0.05 | -5.48
Bicker Fen 132kV | Skegness | WARTH LANE SKEGNESS 33 11kV S STN | Primary | 11 | 0.307 | 53.1429 | WPD Best View | Headroom (MW) | Thermal | 17.77 | 17.57 | 17.45 | 17.32 | 17.04 | 16.81 | 16.56 | 15.83 | 14.96 | 14.09 | 12.99 | 11.79 | 10.54 | 9.4 | 7.95 | 4.34 | -0.05 | -5.48
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Consumer Transformation | Headroom (MW) | Thermal | 5 | 4.9 | 4.82 | 4.74 | 4.58 | 4.41 | 4.24 | 4.08 | 3.92 | 3.76 | 3.63 | 3.52 | 3.4 | 3.27 | 3.14 | 2.16 | 1.08 | -0.12
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Leading the Way | Headroom (MW) | Thermal | 5 | 4.89 | 4.81 | 4.72 | 4.56 | 4.36 | 4.17 | 3.98 | 3.78 | 3.59 | 3.45 | 3.31 | 3.16 | 3 | 2.83 | 1.77 | 0.56 | -1.06
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | Steady Progression | Headroom (MW) | N/A | 5 | 4.92 | 4.88 | 4.85 | 4.82 | 4.78 | 4.73 | 4.68 | 4.64 | 4.59 | 4.55 | 4.51 | 4.47 | 4.43 | 4.39 | 4.28 | 4.09 | 3.8
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | System Transformation | Headroom (MW) | N/A | 5 | 4.91 | 4.86 | 4.8 | 4.73 | 4.64 | 4.54 | 4.43 | 4.34 | 4.24 | 4.17 | 4.1 | 4.04 | 3.98 | 3.93 | 3.63 | 3.08 | 2.55
Bicker Fen 132kV | Skegness | WRANGLE 33 11kV S STN | Primary | 11 | 0.1201 | 53.041 | WPD Best View | Headroom (MW) | N/A | 5 | 4.92 | 4.87 | 4.83 | 4.79 | 4.73 | 4.67 | 4.62 | 4.56 | 4.51 | 4.45 | 4.41 | 4.36 | 4.32 | 4.28 | 4.11 | 3.79 | 3.42
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Consumer Transformation | Headroom (MW) | Thermal | 4.51 | 4.48 | 4.45 | 4.41 | 4.37 | 4.31 | 3.8 | 2.84 | 2.11 | 1.43 | 0.73 | 0.07 | -0.57 | -1.27 | -2.02 | -5.87 | -10.73 | -15.75
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Leading the Way | Headroom (MW) | Thermal | 4.51 | 4.48 | 4.45 | 4.43 | 4.39 | 4.33 | 3.76 | 3.28 | 2.89 | 2.29 | 1.79 | 1.32 | 0.8 | 0.25 | -0.35 | -3.35 | -7.17 | -11.23
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | Steady Progression | Headroom (MW) | N/A | 4.51 | 4.48 | 4.46 | 4.45 | 4.43 | 4.41 | 4.39 | 4.37 | 4.27 | 3.81 | 3.72 | 3.61 | 3.46 | 3.37 | 3.3 | 3.09 | 2.83 | 2.57
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | System Transformation | Headroom (MW) | Thermal | 4.51 | 4.48 | 4.46 | 4.44 | 4.42 | 4.38 | 4.34 | 4.3 | 3.89 | 3.68 | 3.46 | 3.27 | 3.09 | 2.97 | 2.84 | 2.1 | 0.97 | -0.26
Bicker Fen 132kV | Sleaford | CRANWELL 33 11kV S STN | Primary | 11 | -0.4983 | 53.0368 | WPD Best View | Headroom (MW) | N/A | 4.51 | 4.48 | 4.46 | 4.45 | 4.43 | 4.39 | 4.35 | 4.3 | 4.18 | 3.69 | 3.59 | 3.48 | 3.32 | 3.23 | 3.16 | 2.82 | 2.56 | 2.29
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Consumer Transformation | Headroom (MW) | Thermal | 3.71 | 3.64 | 3.57 | 3.5 | 3.34 | 3.06 | 2.75 | 2.23 | 1.63 | 0.97 | 0.38 | -0.29 | -1.01 | -1.67 | -2.5 | -5.23 | -7.6 | -10.39
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Leading the Way | Headroom (MW) | Thermal | 3.71 | 3.63 | 3.57 | 3.49 | 3.31 | 2.93 | 2.51 | 2.05 | 1.55 | 1.02 | 0.84 | 0.64 | 0 | -0.61 | -1.26 | -3.98 | -6.89 | -8.83
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | Steady Progression | Headroom (MW) | Thermal | 3.71 | 3.67 | 3.64 | 3.62 | 3.6 | 3.56 | 3.52 | 3.42 | 3.33 | 3.21 | 3.07 | 2.9 | 2.54 | 2.19 | 1.71 | 1.11 | 0.35 | -0.5
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | System Transformation | Headroom (MW) | Thermal | 3.71 | 3.65 | 3.61 | 3.57 | 3.5 | 3.33 | 3.13 | 2.71 | 2.22 | 1.67 | 1.15 | 0.55 | -0.1 | -0.69 | -1.42 | -2.74 | -4.45 | -6.45
Bicker Fen 132kV | Sleaford | GREAT HALE 33 11kV S STN | Primary | 11 | -0.2947 | 52.9686 | WPD Best View | Headroom (MW) | Thermal | 3.71 | 3.67 | 3.64 | 3.62 | 3.6 | 3.56 | 3.52 | 3.42 | 3.33 | 3.21 | 3.07 | 2.9 | 2.54 | 2.19 | 1.71 | 1.11 | 0.35 | -0.5
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Consumer Transformation | Headroom (MW) | Thermal | 7.1 | 6.99 | 6.91 | 6.82 | 6.61 | 6.44 | 6.28 | 5.79 | 5.22 | 4.59 | 3.77 | 2.83 | 1.82 | 0.89 | -0.25 | -2.6 | -5.62 | -9.24
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Leading the Way | Headroom (MW) | Thermal | 7.1 | 6.99 | 6.9 | 6.8 | 6.57 | 6.4 | 6.23 | 6.07 | 5.92 | 5.78 | 5.64 | 5.48 | 4.7 | 3.94 | 3.13 | 0.47 | -3.28 | -5.54
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | Steady Progression | Headroom (MW) | N/A | 7.1 | 7.03 | 6.99 | 6.96 | 6.91 | 6.87 | 6.83 | 6.71 | 6.59 | 6.43 | 6.23 | 6 | 5.46 | 4.94 | 4.24 | 3.33 | 2.33 | 1.14
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | System Transformation | Headroom (MW) | Thermal | 7.1 | 7.01 | 6.96 | 6.9 | 6.8 | 6.72 | 6.64 | 6.22 | 5.69 | 5.11 | 4.35 | 3.47 | 2.53 | 1.68 | 0.62 | -1 | -3.35 | -6.18
Bicker Fen 132kV | Sleaford | LEADENHAM 33 11kV S STN | Primary | 11 | -0.577 | 53.0461 | WPD Best View | Headroom (MW) | Thermal | 7.1 | 7.01 | 6.95 | 6.88 | 6.75 | 6.64 | 6.53 | 6.34 | 6.16 | 5.96 | 5.71 | 5.42 | 4.84 | 4.25 | 3.5 | 2.11 | 0.51 | -1.29
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Consumer Transformation | Headroom (MW) | Thermal | 13.44 | 13.32 | 13.22 | 13.1 | 12.86 | 12.63 | 12.39 | 11.74 | 10.97 | 10.1 | 9.05 | 7.85 | 6.56 | 5.35 | 3.85 | 0.59 | -3.36 | -8.1
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Leading the Way | Headroom (MW) | Thermal | 13.44 | 13.31 | 13.21 | 13.08 | 12.83 | 12.57 | 12.3 | 12.02 | 11.75 | 11.47 | 11.26 | 11.05 | 10.04 | 9.04 | 7.96 | 4.25 | -0.69 | -3.76
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | Steady Progression | Headroom (MW) | N/A | 13.44 | 13.36 | 13.32 | 13.28 | 13.24 | 13.19 | 13.14 | 12.99 | 12.84 | 12.65 | 12.41 | 12.1 | 11.42 | 10.75 | 9.86 | 8.7 | 7.34 | 5.78
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | System Transformation | Headroom (MW) | Thermal | 13.44 | 13.34 | 13.28 | 13.21 | 13.11 | 12.99 | 12.85 | 12.3 | 11.6 | 10.82 | 9.84 | 8.72 | 7.5 | 6.42 | 5.06 | 2.87 | -0.2 | -3.83
Bicker Fen 132kV | Sleaford | RUSKINGTON 33 11kV S STN | Primary | 11 | -0.4003 | 53.0445 | WPD Best View | Headroom (MW) | N/A | 13.44 | 13.36 | 13.32 | 13.28 | 13.24 | 13.19 | 13.14 | 12.99 | 12.84 | 12.65 | 12.41 | 12.1 | 11.42 | 10.75 | 9.86 | 8.7 | 7.34 | 5.78
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Consumer Transformation | Headroom (MW) | Thermal | 13.89 | 13.7 | 13.54 | 13.33 | 12.82 | 12.48 | 12.07 | 11.11 | 10.03 | 8.82 | 7.3 | 5.57 | 3.7 | 1.89 | -0.32 | -5.67 | -12.07 | -19.58
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Leading the Way | Headroom (MW) | Thermal | 13.89 | 13.69 | 13.51 | 13.29 | 12.72 | 12.39 | 11.96 | 11.53 | 11.11 | 10.71 | 10.25 | 9.77 | 8.19 | 6.64 | 4.99 | -1.08 | -8.91 | -14.73
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Steady Progression | Headroom (MW) | N/A | 13.89 | 13.79 | 13.74 | 13.7 | 13.64 | 13.63 | 13.58 | 13.38 | 13.18 | 12.94 | 12.62 | 12.24 | 11.36 | 10.5 | 9.34 | 7.89 | 6.12 | 3.84
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | System Transformation | Headroom (MW) | Thermal | 13.89 | 13.75 | 13.65 | 13.54 | 13.33 | 13.22 | 13.02 | 12.26 | 11.33 | 10.31 | 8.97 | 7.43 | 5.77 | 4.26 | 2.39 | -0.91 | -5.5 | -10.82
Bicker Fen 132kV | Sleaford | SLEAFORD 11kV S STN | Primary | 11 | -0.033 | 52.9778 | WPD Best View | Headroom (MW) | N/A | 13.89 | 13.79 | 13.74 | 13.7 | 13.64 | 13.63 | 13.58 | 13.38 | 13.18 | 12.94 | 12.62 | 12.24 | 11.36 | 10.5 | 9.34 | 7.89 | 6.12 | 3.84
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Consumer Transformation | Headroom (MW) | N/A | 10.33 | 10.2 | 10.09 | 9.96 | 9.65 | 9.41 | 9.09 | 8.72 | 8.38 | 8.05 | 7.72 | 7.41 | 7.1 | 6.77 | 6.38 | 4.7 | 2.64 | 0.55
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Leading the Way | Headroom (MW) | Thermal | 10.33 | 10.2 | 10.08 | 9.94 | 9.63 | 9.36 | 9.02 | 8.64 | 8.31 | 7.95 | 7.59 | 7.24 | 6.87 | 6.52 | 6.13 | 4.17 | 1.97 | -1.24
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | Steady Progression | Headroom (MW) | N/A | 10.33 | 10.25 | 10.21 | 10.17 | 10.12 | 10.06 | 10 | 9.93 | 9.86 | 9.8 | 9.73 | 9.68 | 9.64 | 9.61 | 9.57 | 9.47 | 9.24 | 8.77
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | System Transformation | Headroom (MW) | N/A | 10.33 | 10.23 | 10.16 | 10.08 | 9.94 | 9.82 | 9.66 | 9.46 | 9.29 | 9.1 | 8.93 | 8.79 | 8.67 | 8.55 | 8.37 | 7.9 | 6.94 | 6.01
Bicker Fen 132kV | Sleaford | TATTERSHALL 33 11kV S STN | Primary | 11 | -0.224 | 53.0866 | WPD Best View | Headroom (MW) | N/A | 10.33 | 10.24 | 10.18 | 10.11 | 9.99 | 9.89 | 9.77 | 9.61 | 9.46 | 9.3 | 9.15 | 9.04 | 8.94 | 8.83 | 8.68 | 8.3 | 7.55 | 6.78
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Consumer Transformation | Headroom (MW) | Thermal | 3.58 | 3.51 | 3.46 | 3.39 | 3.22 | 3.08 | 2.94 | 2.81 | 2.68 | 2.57 | 2.46 | 2.36 | 2.25 | 2.13 | 2.01 | 1.22 | 0.11 | -1.12
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Leading the Way | Headroom (MW) | Thermal | 3.58 | 3.51 | 3.45 | 3.38 | 3.19 | 3.04 | 2.9 | 2.76 | 2.63 | 2.52 | 2.4 | 2.27 | 2.14 | 2.01 | 1.86 | 0.91 | -0.35 | -2.02
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | Steady Progression | Headroom (MW) | N/A | 3.58 | 3.54 | 3.52 | 3.51 | 3.49 | 3.46 | 3.44 | 3.42 | 3.39 | 3.37 | 3.34 | 3.32 | 3.31 | 3.29 | 3.28 | 3.28 | 3.18 | 2.94
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | System Transformation | Headroom (MW) | N/A | 3.58 | 3.53 | 3.49 | 3.46 | 3.39 | 3.33 | 3.26 | 3.19 | 3.13 | 3.07 | 3.01 | 2.96 | 2.91 | 2.88 | 2.85 | 2.64 | 2.13 | 1.62
Bicker Fen 132kV | Sleaford | WOODHALL SPA 33 11kV S STN | Primary | 11 | -0.2404 | 53.1421 | WPD Best View | Headroom (MW) | N/A | 3.58 | 3.53 | 3.49 | 3.46 | 3.39 | 3.33 | 3.26 | 3.2 | 3.14 | 3.09 | 3.03 | 2.98 | 2.94 | 2.91 | 2.89 | 2.68 | 2.17 | 1.65
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Consumer Transformation | Headroom (MW) | N/A | 12.25 | 12.18 | 12.13 | 12.06 | 11.94 | 12.1 | 12.23 | 12.36 | 12.31 | 12.26 | 12.02 | 11.8 | 11.55 | 11.33 | 11.05 | 10 | 8.52 | 6.77
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Leading the Way | Headroom (MW) | N/A | 12.25 | 12.18 | 12.12 | 12.06 | 11.93 | 12.23 | 12.44 | 12.7 | 12.69 | 12.67 | 12.57 | 12.53 | 12.31 | 12.08 | 11.83 | 10.44 | 8.65 | 7.21
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | Steady Progression | Headroom (MW) | N/A | 12.25 | 12.21 | 12.18 | 12.15 | 12.13 | 12.3 | 12.41 | 12.54 | 12.59 | 12.63 | 12.64 | 12.63 | 12.56 | 12.48 | 12.36 | 12.39 | 11.95 | 11.37
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | System Transformation | Headroom (MW) | N/A | 12.25 | 12.19 | 12.16 | 12.11 | 12.06 | 12.27 | 12.44 | 12.6 | 12.59 | 12.58 | 12.4 | 12.22 | 12.03 | 11.86 | 11.64 | 11.16 | 10.11 | 8.86
Chesterfield 132kV | Alfreton | AMBERGATE 33 11kV S STN | Primary | 11 | -1.4824 | 53.0628 | WPD Best View | Headroom (MW) | N/A | 12.25 | 12.18 | 12.13 | 12.06 | 11.94 | 12.1 | 12.23 | 12.36 | 12.31 | 12.26 | 12.02 | 11.8 | 11.55 | 11.33 | 11.05 | 10 | 8.52 | 6.77
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Consumer Transformation | Headroom (MW) | Thermal | 14.63 | 14.53 | 14.45 | 11.28 | 10.91 | 10.69 | 9.88 | 8.37 | 7.12 | 5.97 | 4.66 | 3.35 | 2.03 | 0.67 | -0.91 | -7.7 | -16.83 | -26.64
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Leading the Way | Headroom (MW) | Thermal | 14.63 | 14.52 | 14.44 | 11.27 | 10.89 | 10.72 | 9.88 | 9.19 | 8.55 | 7.75 | 6.95 | 6.2 | 5.1 | 3.93 | 2.66 | -3.6 | -12.03 | -20.77
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | Steady Progression | Headroom (MW) | N/A | 14.63 | 14.55 | 14.51 | 11.39 | 11.33 | 11.36 | 11.37 | 11.39 | 11.27 | 10.62 | 10.43 | 10.2 | 9.81 | 9.5 | 9.15 | 8.66 | 7.78 | 6.53
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | System Transformation | Headroom (MW) | Thermal | 14.63 | 14.54 | 14.48 | 11.35 | 11.26 | 11.26 | 11.19 | 10.99 | 10.18 | 9.69 | 9.05 | 8.41 | 7.77 | 7.24 | 6.62 | 4.81 | 1.5 | -2.12
Chesterfield 132kV | Alfreton | BLACKWELL 33 11kV S STN | Primary | 11 | -1.3441 | 53.1155 | WPD Best View | Headroom (MW) | Thermal | 14.63 | 14.53 | 14.45 | 11.28 | 10.91 | 10.69 | 9.88 | 8.37 | 7.12 | 5.97 | 4.66 | 3.35 | 2.03 | 0.67 | -0.91 | -7.7 | -16.83 | -26.64
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Consumer Transformation | Headroom (MW) | N/A | 14.94 | 14.72 | 13.1 | 12.98 | 12.69 | 12.51 | 12.36 | 12.19 | 11.99 | 11.79 | 11.55 | 11.33 | 11.12 | 10.92 | 10.71 | 9.26 | 7.71 | 5.98
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Leading the Way | Headroom (MW) | N/A | 14.94 | 14.72 | 13.09 | 12.96 | 12.63 | 12.47 | 12.35 | 12.2 | 11.99 | 11.77 | 11.48 | 11.23 | 10.97 | 10.73 | 10.46 | 8.88 | 7.31 | 4.97
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | Steady Progression | Headroom (MW) | N/A | 14.94 | 14.85 | 13.28 | 13.15 | 13.09 | 13.07 | 13.05 | 13.03 | 12.99 | 12.95 | 12.91 | 12.87 | 12.84 | 12.8 | 12.77 | 12.7 | 12.45 | 11.97
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | System Transformation | Headroom (MW) | N/A | 14.94 | 14.83 | 13.16 | 13.08 | 12.94 | 12.88 | 12.83 | 12.76 | 12.65 | 12.55 | 12.43 | 12.32 | 12.21 | 12.13 | 12.06 | 11.6 | 10.79 | 9.89
Chesterfield 132kV | Alfreton | MEADOW LANE 33 11kV S STN | Primary | 11 | -1.3758 | 53.1021 | WPD Best View | Headroom (MW) | N/A | 14.94 | 14.72 | 13.1 | 12.98 | 12.69 | 12.51 | 12.36 | 12.19 | 11.99 | 11.79 | 11.55 | 11.33 | 11.12 | 10.92 | 10.71 | 9.26 | 7.71 | 5.98
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Consumer Transformation | Headroom (MW) | Thermal | 7.98 | 7.93 | 7.88 | 7.83 | 7.74 | 7.53 | 7.16 | 6.1 | 4.98 | 3.74 | 2.18 | 0.43 | -1.44 | -3.17 | -5.29 | -10.7 | -16.71 | -23.8
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Leading the Way | Headroom (MW) | Thermal | 7.98 | 7.92 | 7.88 | 7.83 | 7.74 | 7.45 | 6.97 | 6.53 | 6.11 | 5.63 | 5.2 | 4.78 | 3.27 | 1.81 | 0.28 | -5.25 | -12.12 | -15.98
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | Steady Progression | Headroom (MW) | Thermal | 7.98 | 7.94 | 7.92 | 7.91 | 7.88 | 7.85 | 7.82 | 7.66 | 7.47 | 7.11 | 6.78 | 6.38 | 5.46 | 4.58 | 3.4 | 1.8 | 0.02 | -1.67
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | System Transformation | Headroom (MW) | Thermal | 7.98 | 7.93 | 7.91 | 7.88 | 7.83 | 7.76 | 7.67 | 7 | 5.99 | 5 | 3.71 | 2.21 | 0.6 | -0.83 | -2.62 | -5.59 | -9.63 | -14.61
Chesterfield 132kV | Alfreton | RAVENSDALE PARK 33 11kV S STN | Primary | 11 | -1.5997 | 53.0007 | WPD Best View | Headroom (MW) | Thermal | 7.98 | 7.93 | 7.88 | 7.83 | 7.74 | 7.53 | 7.16 | 6.1 | 4.98 | 3.74 | 2.18 | 0.43 | -1.44 | -3.17 | -5.29 | -10.7 | -16.71 | -23.8
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Consumer Transformation | Headroom (MW) | Fault level | -46.7716 | -46.8049 | -46.8444 | -46.8963 | -47.0357 | -47.1683 | -48.9056 | -50.5126 | -51.9486 | -52.9242 | -53.6318 | -53.958 | -54.1154 | -54.2751 | -54.4359 | -56.029 | -54.5055 | -53.4413
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Leading the Way | Headroom (MW) | Fault level | -64.0104 | -64.0575 | -64.1131 | -64.1865 | -64.3764 | -64.5648 | -65.3795 | -66.2081 | -67.0506 | -67.236 | -67.6213 | -67.8437 | -68.0708 | -68.3063 | -68.5495 | -70.7885 | -38.8275 | -87.2107
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | Steady Progression | Headroom (MW) | Fault level | -25.802 | -25.8058 | -25.8089 | -25.812 | -25.8157 | -25.8241 | -27.0988 | -28.3626 | -29.5862 | -30.7212 | -31.7409 | -32.5823 | -32.9991 | -33.3029 | -33.4722 | -33.5463 | -33.6332 | -33.7222
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | System Transformation | Headroom (MW) | Fault level | -36.871 | -36.8848 | -36.8994 | -36.9172 | -36.9533 | -36.9951 | -38.3095 | -39.5203 | -40.5963 | -41.3098 | -41.7817 | -41.9757 | -42.0384 | -42.102 | -42.1669 | -42.8042 | -23.9503 | -42.3696
Chesterfield 132kV | Alfreton | SOMERCOTES 33 11kV S STN | Primary | 11 | -1.3729 | 53.085 | WPD Best View | Headroom (MW) | Fault level | -38.443 | -38.4703 | -38.5028 | -38.5455 | -38.66 | -38.769 | -40.197 | -41.5178 | -42.6981 | -43.5 | -44.0816 | -44.3497 | -44.4791 | -44.6103 | -44.7425 | -46.0519 | -44.7997 | -43.925
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Consumer Transformation | Headroom (MW) | Thermal | 4.15 | 4.08 | 4.01 | 3.93 | 3.76 | 3.62 | 3.47 | 2.98 | 2.43 | 1.81 | 1 | 0.07 | -0.94 | -1.89 | -3.07 | -5.36 | -8.31 | -11.87
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Leading the Way | Headroom (MW) | Thermal | 4.15 | 4.07 | 4 | 3.91 | 3.73 | 3.59 | 3.43 | 3.28 | 3.16 | 3.04 | 2.91 | 2.78 | 2.01 | 1.26 | 0.44 | -2.24 | -5.92 | -8.12
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | Steady Progression | Headroom (MW) | Thermal | 4.15 | 4.11 | 4.09 | 4.07 | 4.05 | 4.03 | 4 | 3.89 | 3.79 | 3.65 | 3.47 | 3.24 | 2.72 | 2.2 | 1.51 | 0.7 | -0.31 | -1.5
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | System Transformation | Headroom (MW) | Thermal | 4.15 | 4.1 | 4.06 | 4.01 | 3.95 | 3.89 | 3.81 | 3.4 | 2.89 | 2.32 | 1.56 | 0.68 | -0.27 | -1.12 | -2.19 | -3.8 | -6.13 | -8.94
Chesterfield 132kV | Alfreton | WESSINGTON 33 11kV S STN | Primary | 11 | -1.4324 | 53.1179 | WPD Best View | Headroom (MW) | Thermal | 4.15 | 4.08 | 4.01 | 3.93 | 3.76 | 3.62 | 3.47 | 2.98 | 2.43 | 1.81 | 1 | 0.07 | -0.94 | -1.89 | -3.07 | -5.36 | -8.31 | -11.87
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Consumer Transformation | Headroom (MW) | Thermal | 6.79 | 6.67 | 6.54 | 6.38 | 6.07 | 5.8 | 4.62 | 2.42 | 0.74 | -0.87 | -2.65 | -4.4 | -6.15 | -7.97 | -10.05 | -19.87 | -31.46 | -43.79
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Leading the Way | Headroom (MW) | Thermal | 6.79 | 6.66 | 6.54 | 6.39 | 6.08 | 5.81 | 4.54 | 3.48 | 2.68 | 1.53 | 0.48 | -0.52 | -1.92 | -3.41 | -5.02 | -13.64 | -23.79 | -34
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | Steady Progression | Headroom (MW) | N/A | 6.79 | 6.73 | 6.7 | 6.66 | 6.63 | 6.58 | 6.54 | 6.45 | 6.21 | 5.22 | 4.96 | 4.64 | 4.1 | 3.7 | 3.24 | 2.6 | 1.63 | 0.34
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | System Transformation | Headroom (MW) | Thermal | 6.79 | 6.7 | 6.64 | 6.56 | 6.45 | 6.33 | 6.2 | 5.9 | 4.79 | 4.11 | 3.26 | 2.42 | 1.6 | 0.93 | 0.15 | -2.53 | -6.25 | -10.38
Chesterfield 132kV | Annesley (1 & 2) | BLIDWORTH 33 11kV S STN | Primary | 11 | -1.1444 | 53.0884 | WPD Best View | Headroom (MW) | Thermal | 6.79 | 6.67 | 6.54 | 6.38 | 6.07 | 5.8 | 4.62 | 2.42 | 0.74 | -0.87 | -2.65 | -4.4 | -6.15 | -7.97 | -10.05 | -19.87 | -31.46 | -43.79
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Consumer Transformation | Headroom (MW) | Thermal | 11.04 | 10.97 | 10.92 | 10.85 | 10.71 | 10.6 | 10.5 | 10.04 | 9.51 | 8.9 | 8.09 | 7.16 | 6.15 | 5.21 | 4.04 | 0.96 | -2.24 | -5.58
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Leading the Way | Headroom (MW) | Thermal | 11.04 | 10.97 | 10.91 | 10.84 | 10.69 | 10.58 | 10.46 | 10.36 | 10.27 | 10.18 | 10.09 | 10 | 9.23 | 8.48 | 7.67 | 4.23 | 0.29 | -1.48
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | Steady Progression | Headroom (MW) | N/A | 11.04 | 11 | 10.98 | 10.97 | 10.95 | 10.92 | 10.9 | 10.79 | 10.68 | 10.55 | 10.36 | 10.13 | 9.59 | 9.06 | 8.34 | 7.45 | 6.43 | 5.28
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | System Transformation | Headroom (MW) | Thermal | 11.04 | 10.99 | 10.95 | 10.92 | 10.86 | 10.81 | 10.76 | 10.35 | 9.85 | 9.27 | 8.5 | 7.6 | 6.63 | 5.76 | 4.67 | 2.59 | 0.09 | -2.64
Chesterfield 132kV | Annesley (1 & 2) | FARNSFIELD 33 11kV S STN | Primary | 11 | -1.0233 | 53.1047 | WPD Best View | Headroom (MW) | Thermal | 11.04 | 10.97 | 10.92 | 10.85 | 10.71 | 10.6 | 10.5 | 10.04 | 9.51 | 8.9 | 8.09 | 7.16 | 6.15 | 5.21 | 4.04 | 0.96 | -2.24 | -5.58
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Consumer Transformation | Headroom (MW) | Thermal | 22.82 | 22.58 | 22.32 | 22 | 21.29 | 20.75 | 20.24 | 19.75 | 19.29 | 18.87 | 18.3 | 17.7 | 17.03 | 16.36 | 15.62 | 11.21 | 5.26 | -1.5
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Leading the Way | Headroom (MW) | Thermal | 22.82 | 22.56 | 22.29 | 21.95 | 21.17 | 20.61 | 20.09 | 19.66 | 19.24 | 18.87 | 18.42 | 17.96 | 17.3 | 16.59 | 15.77 | 10.32 | 3.27 | -5.22
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | Steady Progression | Headroom (MW) | N/A | 13.7785 | 13.7639 | 13.7508 | 13.7362 | 13.7216 | 13.6898 | 13.6534 | 13.6139 | 13.5753 | 13.5261 | 13.4638 | 13.3981 | 13.3013 | 13.2052 | 13.0915 | 12.7765 | 12.4021 | 12.0217
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | System Transformation | Headroom (MW) | N/A | 19.6895 | 19.6401 | 19.5827 | 19.5106 | 19.3928 | 19.2495 | 19.0801 | 18.9035 | 18.7206 | 18.5329 | 18.254 | 17.9507 | 17.6344 | 17.3288 | 16.997 | 15.5857 | 14.2495 | 11.8
Chesterfield 132kV | Annesley (1 & 2) | HUCKNALL 33 11kV S STN | Primary | 11 | -1.1987 | 53.0415 | WPD Best View | Headroom (MW) | Thermal | 20.5289 | 20.432 | 20.3114 | 20.1481 | 19.7938 | 19.4423 | 19.0828 | 18.7248 | 18.3603 | 17.9897 | 17.5055 | 16.9991 | 16.4778 | 15.9672 | 15.4362 | 11.21 | 5.26 | -1.49
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Consumer Transformation | Headroom (MW) | Thermal | 13.77 | 13.72 | 13.69 | 13.65 | 13.61 | 13.57 | 13.19 | 12.48 | 11.98 | 11.51 | 11.01 | 10.53 | 10.08 | 9.58 | 9.04 | 6.38 | 2.87 | -0.74
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Leading the Way | Headroom (MW) | N/A | 13.77 | 13.72 | 13.69 | 13.66 | 13.62 | 13.59 | 13.18 | 12.84 | 12.59 | 12.2 | 11.85 | 11.52 | 11.17 | 10.78 | 10.37 | 8.36 | 5.7 | 2.9
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | Steady Progression | Headroom (MW) | N/A | 13.77 | 13.72 | 13.7 | 13.67 | 13.64 | 13.62 | 13.59 | 13.56 | 13.48 | 13.12 | 13.05 | 12.95 | 12.83 | 12.76 | 12.7 | 12.49 | 12.26 | 12.04
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | System Transformation | Headroom (MW) | N/A | 13.77 | 13.72 | 13.69 | 13.67 | 13.64 | 13.61 | 13.58 | 13.56 | 13.24 | 13.09 | 12.92 | 12.77 | 12.63 | 12.53 | 12.43 | 11.89 | 11.1 | 10.24
Chesterfield 132kV | Annesley (1 & 2) | SHERWOOD PARK 33 11kV S STN | Primary | 11 | -1.2611 | 53.0707 | WPD Best View | Headroom (MW) | Thermal | 13.77 | 13.72 | 13.69 | 13.65 | 13.61 | 13.57 | 13.19 | 12.48 | 11.98 | 11.51 | 11.01 | 10.53 | 10.08 | 9.58 | 9.04 | 6.38 | 2.87 | -0.74
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Consumer Transformation | Headroom (MW) | Fault level | -33.1429 | -33.2123 | -33.2997 | -33.4182 | -33.7269 | -34.0282 | -35.278 | -36.569 | -37.785 | -38.7606 | -39.6115 | -40.3264 | -40.9702 | -41.587 | -42.2669 | -45.3016 | -35.9551 | -52.3101
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Leading the Way | Headroom (MW) | Fault level | -45.3585 | -45.4542 | -45.5754 | -45.7399 | -46.1523 | -46.5878 | -47.3879 | -48.2033 | -49.0319 | -49.4791 | -49.9756 | -50.486 | -51.3038 | -52.1147 | -33.3156 | -65.6613 | -73.0304 | -76.2916
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | Steady Progression | Headroom (MW) | Fault level | -18.2836 | -18.2883 | -18.2926 | -18.2973 | -18.3026 | -18.321 | -19.0892 | -19.8689 | -20.6257 | -21.3391 | -21.9866 | -22.54 | -22.897 | -23.1856 | -23.4265 | -23.7524 | -24.1141 | -24.4821
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | System Transformation | Headroom (MW) | Fault level | -26.1272 | -26.1516 | -26.1819 | -26.2192 | -26.2944 | -26.3883 | -27.2454 | -28.1342 | -28.9691 | -29.6092 | -30.1327 | -30.5549 | -30.9196 | -31.263 | -29.6359 | -41.6871 | -43.8886 | -45.2684
Chesterfield 132kV | Annesley (3 & 4) | ANNESLEY (KIRKBY) 11kV S STN | Primary | 11 | -1.2451 | 53.0886 | WPD Best View | Headroom (MW) | Fault level | -27.2411 | -27.2981 | -27.37 | -27.4674 | -27.7211 | -27.9688 | -28.996 | -30.0572 | -31.0566 | -31.8585 | -32.5579 | -33.1455 | -33.6747 | -34.1816 | -34.7404 | -37.2348 | -29.5526 | -42.9952
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Consumer Transformation | Headroom (MW) | Thermal | 0.895 | 0.755 | 0.665 | 0.545 | 0.275 | 0.045 | -0.165 | -0.545 | -0.955 | -1.405 | -2.035 | -2.745 | -3.495 | -4.215 | -5.115 | -7.695 | -10.785 | -14.425
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Leading the Way | Headroom (MW) | Thermal | 0.895 | 0.755 | 0.645 | 0.515 | 0.225 | -0.015 | -0.235 | -0.455 | -0.665 | -0.875 | -1.055 | -1.245 | -1.885 | -2.505 | -3.165 | -6.105 | -9.885 | -12.825
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | Steady Progression | Headroom (MW) | Thermal | 0.895 | 0.815 | 0.795 | 0.775 | 0.745 | 0.705 | 0.675 | 0.595 | 0.515 | 0.425 | 0.285 | 0.115 | -0.245 | -0.595 | -1.065 | -1.615 | -2.455 | -3.545
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | System Transformation | Headroom (MW) | Thermal | 0.895 | 0.785 | 0.735 | 0.675 | 0.565 | 0.465 | 0.355 | 0.075 | -0.255 | -0.605 | -1.155 | -1.785 | -2.455 | -3.055 | -3.785 | -5.215 | -7.375 | -9.885
Chesterfield 132kV | Annesley (3 & 4) | CALVERTON 33 11kV S STN | Primary | 11 | -1.1029 | 53.0473 | WPD Best View | Headroom (MW) | Thermal | 0.895 | 0.755 | 0.665 | 0.545 | 0.275 | 0.045 | -0.165 | -0.545 | -0.955 | -1.405 | -2.035 | -2.745 | -3.495 | -4.215 | -5.115 | -7.695 | -10.785 | -14.425
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Consumer Transformation | Headroom (MW) | Thermal | 8.26 | 8.26 | 8.18 | 8.02 | 7.58 | 7.25 | 6.95 | 6.63 | 6.34 | 6.07 | 5.83 | 5.6 | 5.3 | 5 | 4.69 | 2.31 | -2.05 | -5.75
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Leading the Way | Headroom (MW) | Thermal | 8.26 | 8.27 | 8.19 | 8.02 | 7.5 | 7.14 | 6.82 | 6.5 | 6.2 | 5.94 | 5.67 | 3.73 | 3.39 | 3.02 | 2.59 | -0.29 | -6.17 | -11.19
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | Steady Progression | Headroom (MW) | N/A | 8.26 | 8.32 | 8.43 | 8.41 | 8.36 | 8.33 | 8.3 | 8.25 | 8.21 | 8.15 | 8.1 | 8.05 | 8.02 | 8 | 7.99 | 8.06 | 7.77 | 7.03
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | System Transformation | Headroom (MW) | N/A | 8.26 | 8.3 | 8.39 | 8.19 | 8.02 | 7.89 | 7.74 | 7.58 | 7.43 | 7.29 | 7.17 | 7.06 | 6.98 | 6.92 | 6.86 | 6.25 | 3.62 | 1.98
Chesterfield 132kV | Annesley (3 & 4) | HUTHWAITE 33 11kV S STN | Primary | 11 | -1.2911 | 53.1271 | WPD Best View | Headroom (MW) | Thermal | 8.26 | 8.26 | 8.18 | 8.02 | 7.58 | 7.25 | 6.95 | 6.63 | 6.34 | 6.07 | 5.83 | 5.6 | 5.3 | 5 | 4.69 | 2.31 | -2.05 | -5.75
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Consumer Transformation | Headroom (MW) | N/A | 19.89 | 19.69 | 19.55 | 16.12 | 15.77 | 15.53 | 15.05 | 14.59 | 14.17 | 13.82 | 13.54 | 13.31 | 13.1 | 12.87 | 12.63 | 10.85 | 12.14 | 6.45
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Leading the Way | Headroom (MW) | Thermal | 19.89 | 19.67 | 19.53 | 16.08 | 15.68 | 15.44 | 15.11 | 14.78 | 14.45 | 14.21 | 8.38 | 8.17 | 7.94 | 7.69 | 10.84 | 3.91 | 1.33 | -1.93
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | Steady Progression | Headroom (MW) | N/A | 19.89 | 19.74 | 19.66 | 16.3 | 16.21 | 16.14 | 15.73 | 15.32 | 14.93 | 14.55 | 14.22 | 13.93 | 13.76 | 13.63 | 13.53 | 13.32 | 12.92 | 12.31
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | System Transformation | Headroom (MW) | N/A | 19.89 | 19.71 | 19.61 | 16.22 | 16.04 | 15.92 | 15.54 | 15.17 | 14.84 | 14.59 | 14.4 | 14.26 | 14.15 | 14.06 | 14.58 | 10.7 | 9.56 | 8.42
Chesterfield 132kV | Annesley (3 & 4) | SUTTON JUNCTION 33 11kV S STN | Primary | 11 | -1.2316 | 53.1236 | WPD Best View | Headroom (MW) | N/A | 19.89 | 19.69 | 19.55 | 16.12 | 15.77 | 15.53 | 15.05 | 14.59 | 14.17 | 13.82 | 13.54 | 13.31 | 13.1 | 12.87 | 12.63 | 10.85 | 12.14 | 6.45
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Consumer Transformation | Headroom (MW) | Thermal | 3.74 | 3.69 | 3.64 | 3.58 | 3.48 | 3.4 | 2.79 | 1.69 | 0.9 | 0.17 | -0.6 | -1.33 | -2.04 | -2.82 | -3.67 | -8 | -13.7 | -19.63
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Leading the Way | Headroom (MW) | Thermal | 3.74 | 3.69 | 3.64 | 3.58 | 3.5 | 3.44 | 2.8 | 2.24 | 1.81 | 1.2 | 0.64 | 0.11 | -0.46 | -1.09 | -1.79 | -5.33 | -9.96 | -15.07
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | Steady Progression | Headroom (MW) | N/A | 3.74 | 3.71 | 3.69 | 3.68 | 3.69 | 3.69 | 3.69 | 3.67 | 3.58 | 3.06 | 2.97 | 2.85 | 2.71 | 2.62 | 2.56 | 2.46 | 2.17 | 1.79
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | System Transformation | Headroom (MW) | Thermal | 3.74 | 3.7 | 3.67 | 3.64 | 3.63 | 3.61 | 3.59 | 3.54 | 3.07 | 2.85 | 2.6 | 2.38 | 2.19 | 2.05 | 1.91 | 1.13 | -0.31 | -1.87
Chesterfield 132kV | Chesterfield 33 | BIWATER 33 11kV S STN | Primary | 11 | -1.4055 | 53.1739 | WPD Best View | Headroom (MW) | Thermal | 3.74 | 3.69 | 3.64 | 3.58 | 3.48 | 3.4 | 2.79 | 1.69 | 0.9 | 0.17 | -0.6 | -1.33 | -2.04 | -2.82 | -3.67 | -8 | -13.7 | -19.63
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Consumer Transformation | Headroom (MW) | Thermal | 7.61 | 7.5 | 7.37 | 7.21 | 6.82 | 6.42 | 6.05 | 5.63 | 5.21 | 4.8 | 4.23 | 3.62 | 2.97 | 2.34 | 1.63 | -2.57 | -6.95 | -12.02
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Leading the Way | Headroom (MW) | Thermal | 7.61 | 7.49 | 7.35 | 7.18 | 6.74 | 6.26 | 5.82 | 5.35 | 4.88 | 4.44 | 3.97 | 3.48 | 2.81 | 2.14 | 1.41 | -4.3 | -9.43 | -14.99
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | Steady Progression | Headroom (MW) | Thermal | 7.61 | 7.56 | 2.38 | 2.34 | 2.28 | 2.21 | 1.65 | 1.08 | 0.52 | -0.01 | -0.52 | -0.96 | -1.31 | -1.6 | -1.88 | -2.17 | -2.78 | -3.74
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | System Transformation | Headroom (MW) | Thermal | 7.61 | 7.53 | 7.45 | 7.36 | 7.19 | 7.05 | 6.92 | 6.68 | 6.41 | 6.21 | 5.85 | 5.47 | 5.09 | 4.75 | 4.33 | 2.25 | -0.3 | -3.15
Chesterfield 132kV | Chesterfield 33 | Bolsover 11kV S Stn | Primary | 11 | -1.3255 | 53.2354 | WPD Best View | Headroom (MW) | Thermal | 7.61 | 7.5 | 7.37 | 7.21 | 6.82 | 6.42 | 6.05 | 5.63 | 5.21 | 4.8 | 4.23 | 3.62 | 2.97 | 2.34 | 1.63 | -2.57 | -6.95 | -12.02
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Consumer Transformation | Headroom (MW) | Thermal | 2.8 | 2.7 | 2.62 | 2.53 | 2.28 | 2.09 | 1.88 | 1.49 | 1.06 | 0.59 | 0.01 | -0.64 | -1.32 | -1.98 | -2.79 | -5.13 | -9.32 | -12.35
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Leading the Way | Headroom (MW) | Thermal | 2.8 | 2.69 | 2.61 | 2.51 | 2.22 | 2.02 | 1.79 | 1.58 | 1.37 | 1.17 | 0.96 | 0.76 | 0.17 | -0.44 | -1.09 | -3.66 | -9.94 | -12.48
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | Steady Progression | Headroom (MW) | Thermal | 2.8 | 2.74 | 2.71 | 2.68 | 2.63 | 2.59 | 2.55 | 2.46 | 2.37 | 2.26 | 2.12 | 1.96 | 1.64 | 1.32 | 0.9 | 0.32 | -0.41 | -1.3
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | System Transformation | Headroom (MW) | Thermal | 2.8 | 2.72 | 2.67 | 2.61 | 2.5 | 2.41 | 2.29 | 1.99 | 1.63 | 1.24 | 0.74 | 0.18 | -0.42 | -0.96 | -1.63 | -2.94 | -6.3 | -8.34
Chesterfield 132kV | Chesterfield 33 | DANESMOOR 33 11kV S STN | Primary | 11 | -1.3944 | 53.1635 | WPD Best View | Headroom (MW) | Thermal | 2.8 | 2.7 | 2.62 | 2.53 | 2.28 | 2.09 | 1.88 | 1.49 | 1.06 | 0.59 | 0.01 | -0.64 | -1.32 | -1.98 | -2.79 | -5.13 | -9.32 | -12.35
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Consumer Transformation | Headroom (MW) | Thermal | 10.77 | 9.67 | 9.41 | 9.1 | 8.48 | 7.8 | 6.71 | 5.03 | 3.55 | 2.06 | 0.38 | -1.39 | -3.2 | -5.01 | -7.07 | -17.31 | -28.97 | -41.95
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Leading the Way | Headroom (MW) | Thermal | 10.77 | 9.65 | 9.39 | 9.06 | 8.4 | 7.61 | 6.36 | 5.18 | 4.13 | 2.93 | 1.72 | -2.56 | -4.28 | -6.05 | -7.95 | -19.56 | -31.73 | -44.8
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | Steady Progression | Headroom (MW) | N/A | 10.77 | 10.61 | 9.71 | 9.63 | 9.58 | 9.48 | 9.38 | 9.21 | 8.99 | 8.42 | 8.14 | 7.83 | 7.3 | 6.83 | 6.26 | 5.37 | 3.98 | 2.03
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | System Transformation | Headroom (MW) | Thermal | 10.77 | 10.55 | 9.58 | 9.41 | 9.19 | 8.95 | 8.67 | 8.07 | 7.04 | 6.27 | 5.33 | 4.36 | 3.38 | 2.48 | 1.41 | -2.53 | -7.89 | -13.81
Chesterfield 132kV | Chesterfield 33 | GRASSMOOR 33 11kV S STN | Primary | 11 | -1.3839 | 53.1998 | WPD Best View | Headroom (MW) | Thermal | 10.77 | 9.67 | 9.41 | 9.1 | 8.48 | 7.8 | 6.71 | 5.03 | 3.55 | 2.06 | 0.38 | -1.39 | -3.2 | -5.01 | -7.07 | -17.31 | -28.97 | -41.95
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Consumer Transformation | Headroom (MW) | N/A | 9.99 | 9.93 | 9.71 | 9.58 | 9.08 | 8.75 | 8.41 | 8.09 | 7.77 | 7.45 | 7.13 | 6.82 | 6.53 | 6.22 | 5.91 | 3.65 | 1.83 | 0.39
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Leading the Way | Headroom (MW) | Thermal | 9.99 | 9.92 | 9.69 | 9.55 | 8.93 | 8.58 | 8.25 | 7.91 | 7.55 | 7.2 | 6.84 | 6.48 | 6.15 | 5.79 | 5.41 | 3.28 | 6.33 | -7.26
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | Steady Progression | Headroom (MW) | N/A | 9.99 | 9.98 | 9.93 | 9.88 | 9.78 | 9.72 | 9.6 | 9.54 | 9.47 | 9.4 | 9.33 | 9.26 | 9.2 | 9.15 | 9.1 | 8.97 | 8.69 | 8.11
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | System Transformation | Headroom (MW) | N/A | 9.99 | 9.96 | 9.88 | 9.7 | 9.46 | 9.31 | 9.11 | 8.93 | 8.76 | 8.6 | 8.43 | 8.28 | 8.14 | 8.02 | 7.89 | 7.24 | 11.37 | 3.49
Chesterfield 132kV | Chesterfield 33 | SHEEPBRIDGE 6 6kV S STN | Primary | 11 | -1.4424 | 53.2702 | WPD Best View | Headroom (MW) | N/A | 9.99 | 9.93 | 9.71 | 9.58 | 9.08 | 8.75 | 8.41 | 8.09 | 7.78 | 7.45 | 7.14 | 6.83 | 6.54 | 6.23 | 5.92 | 3.66 | 1.84 | 0.4
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Consumer Transformation | Headroom (MW) | Thermal | -0.86 | -0.93 | -1.02 | -1.08 | -1.2 | -1.3 | -1.46 | -1.79 | -2.12 | -2.49 | -3.04 | -3.64 | -4.27 | -4.87 | -5.59 | -7.91 | -11.09 | -13.17
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Leading the Way | Headroom (MW) | Thermal | -0.86 | -0.93 | -1.03 | -1.09 | -1.22 | -1.32 | -1.47 | -1.61 | -1.73 | -1.86 | -2.05 | -2.23 | -2.72 | -3.2 | -3.72 | -1.71 | -13.44 | -15.62
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | Steady Progression | Headroom (MW) | Thermal | -0.86 | -0.91 | -0.94 | -0.97 | -1 | -1.03 | -1.11 | -1.18 | -1.26 | -1.39 | -1.51 | -1.66 | -1.96 | -2.23 | -2.59 | -3.14 | -3.68 | -4.34
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | System Transformation | Headroom (MW) | Thermal | -0.86 | -0.92 | -0.96 | -1.04 | -1.1 | -1.16 | -1.24 | -1.46 | -1.75 | -2.05 | -2.48 | -2.95 | -3.45 | -3.89 | -4.43 | -3.12 | -10.2 | -11.89
Chesterfield 132kV | Clipstone | BILSTHORPE 33 11kV S STN | Primary | 11 | -1.0128 | 53.1515 | WPD Best View | Headroom (MW) | Thermal | -0.86 | -0.93 | -1.02 | -1.08 | -1.2 | -1.3 | -1.46 | -1.79 | -2.12 | -2.49 | -3.04 | -3.64 | -4.27 | -4.87 | -5.59 | -7.91 | -11.09 | -13.17
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Consumer Transformation | Headroom (MW) | Thermal | 3.2 | 3.18 | 3.17 | 3.16 | 3.12 | 3.1 | 3.07 | 2.98 | 2.88 | 2.77 | 2.39 | 1.95 | 1.46 | 1.02 | 0.48 | -0.39 | -1.79 | -3.53
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Leading the Way | Headroom (MW) | Thermal | 3.2 | 3.18 | 3.17 | 3.16 | 3.12 | 3.09 | 3.06 | 3.03 | 3.01 | 2.97 | 2.94 | 2.91 | 2.55 | 2.21 | 1.85 | 0.87 | -0.94 | -1.46
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | Steady Progression | Headroom (MW) | N/A | 3.2 | 3.19 | 3.18 | 3.18 | 3.17 | 3.16 | 3.15 | 3.13 | 3.11 | 3.09 | 3 | 2.88 | 2.62 | 2.36 | 2 | 1.54 | 0.93 | 0.27
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | System Transformation | Headroom (MW) | Thermal | 3.2 | 3.19 | 3.18 | 3.17 | 3.16 | 3.14 | 3.13 | 3.05 | 2.96 | 2.86 | 2.49 | 2.05 | 1.58 | 1.15 | 0.62 | -0.14 | -1.43 | -3.05
Chesterfield 132kV | Clipstone | BUDBY 33 11kV S STN | Primary | 11 | -1.0971 | 53.2256 | WPD Best View | Headroom (MW) | Thermal | 3.2 | 3.18 | 3.17 | 3.16 | 3.12 | 3.1 | 3.07 | 2.98 | 2.88 | 2.77 | 2.39 | 1.95 | 1.46 | 1.02 | 0.48 | -0.39 | -1.79 | -3.53
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Consumer Transformation | Headroom (MW) | N/A | 11.515 | 11.455 | 11.405 | 11.345 | 11.235 | 11.125 | 11.025 | 10.925 | 10.835 | 10.735 | 10.645 | 10.535 | 10.445 | 10.345 | 10.255 | 9.555 | 8.545 | 7.425
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Leading the Way | Headroom (MW) | N/A | 11.515 | 11.455 | 11.405 | 11.335 | 11.215 | 11.115 | 11.005 | 10.905 | 10.815 | 10.705 | 10.595 | 10.465 | 10.355 | 10.245 | 10.125 | 9.285 | 8.135 | 6.585
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | Steady Progression | Headroom (MW) | N/A | 11.515 | 11.485 | 11.475 | 11.455 | 11.455 | 11.445 | 11.425 | 11.415 | 11.405 | 11.395 | 11.375 | 11.365 | 11.365 | 11.365 | 11.365 | 11.395 | 11.285 | 11.045
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | System Transformation | Headroom (MW) | N/A | 11.515 | 11.475 | 11.445 | 11.415 | 11.375 | 11.335 | 11.285 | 11.235 | 11.195 | 11.145 | 11.095 | 11.045 | 11.025 | 10.995 | 10.975 | 10.775 | 10.285 | 9.795
Chesterfield 132kV | Clipstone | CLIPSTONE 11kV S STN | Primary | 11 | -1.1036 | 53.1655 | WPD Best View | Headroom (MW) | N/A | 11.515 | 11.455 | 11.405 | 11.345 | 11.235 | 11.125 | 11.025 | 10.925 | 10.835 | 10.735 | 10.645 | 10.535 | 10.445 | 10.345 | 10.255 | 9.555 | 8.545 | 7.425
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Consumer Transformation | Headroom (MW) | Thermal | 10.6 | 10.45 | 10.3 | 10.12 | 9.75 | 9.43 | 9.12 | 8.83 | 8.53 | 8.26 | 8 | 7.74 | 7.48 | 7.21 | 6.9 | 4.65 | 1.68 | -1.64
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Leading the Way | Headroom (MW) | Thermal | 10.6 | 10.44 | 10.28 | 10.1 | 9.69 | 9.34 | 9.02 | 8.69 | 8.37 | 8.07 | 7.76 | 7.43 | 7.11 | 6.76 | 6.37 | 3.72 | 0.29 | -4.24
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | Steady Progression | Headroom (MW) | N/A | 10.6 | 10.52 | 10.47 | 10.43 | 10.37 | 10.32 | 10.26 | 10.2 | 10.14 | 10.09 | 10.04 | 9.99 | 9.95 | 9.92 | 9.9 | 9.87 | 9.46 | 8.78
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | System Transformation | Headroom (MW) | N/A | 10.6 | 10.49 | 10.4 | 10.3 | 10.15 | 10 | 9.83 | 9.68 | 9.52 | 9.38 | 9.25 | 9.13 | 9.02 | 8.93 | 8.84 | 8.2 | 6.76 | 5.35
Chesterfield 132kV | Clipstone | CROWN FM 33 11kV S STN | Primary | 11 | -1.1571 | 53.1475 | WPD Best View | Headroom (MW) | Thermal | 10.6 | 10.45 | 10.3 | 10.12 | 9.75 | 9.43 | 9.12 | 8.83 | 8.53 | 8.26 | 8 | 7.74 | 7.48 | 7.21 | 6.9 | 4.65 | 1.68 | -1.64
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Consumer Transformation | Headroom (MW) | Thermal | 12.435 | 12.335 | 5.605 | 5.505 | 5.205 | 4.885 | 4.535 | 3.805 | 2.995 | 2.105 | 1.045 | -0.165 | -1.475 | -2.665 | -3.465 | -6.455 | -9.595 | -15.115
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Leading the Way | Headroom (MW) | Thermal | 12.435 | 12.325 | 5.595 | 5.485 | 5.135 | 4.745 | 4.385 | 4.065 | 3.805 | 3.625 | 3.425 | 3.205 | 2.185 | 1.185 | 0.955 | -2.525 | -5.945 | -10.145
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | Steady Progression | Headroom (MW) | Thermal | 12.435 | 12.385 | 5.705 | 5.685 | 5.635 | 5.585 | 5.485 | 5.315 | 5.155 | 4.955 | 4.705 | 4.395 | 3.715 | 3.045 | 2.175 | 0.975 | -0.325 | -1.925
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | System Transformation | Headroom (MW) | Thermal | 12.435 | 12.365 | 5.665 | 5.605 | 5.485 | 5.365 | 5.215 | 4.625 | 3.885 | 3.155 | 2.175 | 1.045 | -0.165 | -1.255 | -2.495 | -4.195 | -6.725 | -11.085
Chesterfield 132kV | Clipstone | OLLERTON 33 11kV S STN | Primary | 11 | -1.0232 | 53.1949 | WPD Best View | Headroom (MW) | Thermal | 12.435 | 12.335 | 5.605 | 5.505 | 5.205 | 4.885 | 4.535 | 3.805 | 2.995 | 2.105 | 1.045 | -0.165 | -1.475 | -2.665 | -3.465 | -6.455 | -9.595 | -15.115
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Consumer Transformation | Headroom (MW) | Thermal | 5.46 | 5.35 | 5.28 | 5.19 | 5.01 | 4.88 | 4.77 | 4.37 | 3.9 | 3.37 | 2.69 | 1.92 | 1.09 | 0.33 | -0.61 | -4.11 | -6.63 | -9.65
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Leading the Way | Headroom (MW) | Thermal | 5.46 | 5.35 | 5.27 | 5.18 | 4.98 | 4.84 | 4.74 | 4.62 | 4.49 | 4.36 | 4.24 | 4.12 | 3.47 | 2.85 | 2.18 | -1.6 | -4.71 | -6.6
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | Steady Progression | Headroom (MW) | N/A | 5.46 | 5.38 | 5.34 | 5.3 | 5.25 | 5.21 | 5.19 | 5.08 | 4.98 | 4.85 | 4.68 | 4.48 | 4.03 | 3.6 | 3.01 | 2.22 | 1.35 | 0.33
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | System Transformation | Headroom (MW) | Thermal | 5.46 | 5.37 | 5.31 | 5.26 | 5.16 | 5.09 | 5.04 | 4.7 | 4.26 | 3.78 | 3.14 | 2.41 | 1.62 | 0.92 | 0.05 | -2.09 | -4.07 | -6.47
Chesterfield 132kV | Clipstone | RUFFORD 33 11kV S STN | Primary | 11 | -1.1097 | 53.1376 | WPD Best View | Headroom (MW) | Thermal | 5.46 | 5.35 | 5.28 | 5.19 | 5.01 | 4.88 | 4.77 | 4.37 | 3.9 | 3.37 | 2.69 | 1.92 | 1.09 | 0.33 | -0.61 | -4.11 | -6.63 | -9.65
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Consumer Transformation | Headroom (MW) | Thermal | 8.9 | 8.91 | 8.9 | 8.86 | 8.75 | 8.59 | 8.42 | 8.04 | 7.59 | 7.12 | 6.56 | 5.92 | 5.22 | 4.57 | 3.78 | 0.96 | -1.28 | -3.92
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Leading the Way | Headroom (MW) | Thermal | 8.9 | 8.92 | 8.9 | 8.87 | 8.75 | 8.56 | 8.36 | 8.15 | 7.93 | 7.72 | 7.57 | 7.4 | 6.81 | 6.25 | 5.66 | 1.86 | -0.9 | -2.75
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | Steady Progression | Headroom (MW) | N/A | 8.9 | 8.93 | 8.96 | 8.98 | 9 | 8.99 | 8.97 | 8.9 | 8.83 | 8.74 | 8.61 | 8.46 | 8.12 | 7.78 | 7.34 | 6.73 | 5.98 | 5.16
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | System Transformation | Headroom (MW) | Thermal | 8.9 | 8.93 | 8.94 | 8.94 | 8.92 | 8.84 | 8.75 | 8.45 | 8.07 | 7.66 | 7.16 | 6.59 | 5.97 | 5.41 | 4.72 | 2.7 | 1.06 | -0.85
Chesterfield 132kV | Clipstone | THORESBY 33 11kV S STN | Primary | 11 | -1.0408 | 53.1984 | WPD Best View | Headroom (MW) | Thermal | 8.9 | 8.91 | 8.9 | 8.86 | 8.75 | 8.59 | 8.42 | 8.04 | 7.59 | 7.12 | 6.56 | 5.92 | 5.22 | 4.57 | 3.78 | 0.96 | -1.28 | -3.92
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Consumer Transformation | Headroom (MW) | N/A | 11.85 | 11.81 | 11.77 | 11.72 | 11.6 | 11.49 | 11.4 | 11.42 | 11.37 | 11.31 | 11.25 | 11.17 | 11.11 | 11.03 | 10.96 | 10.4 | 9.48 | 8.45
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Leading the Way | Headroom (MW) | N/A | 11.85 | 11.8 | 11.77 | 11.71 | 11.58 | 11.47 | 11.37 | 11.46 | 11.42 | 11.35 | 11.27 | 11.19 | 11.1 | 11 | 10.9 | 10.14 | 9.07 | 7.65
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | Steady Progression | Headroom (MW) | N/A | 11.85 | 11.83 | 11.83 | 11.82 | 11.81 | 11.79 | 11.77 | 11.82 | 11.83 | 11.83 | 11.83 | 11.83 | 11.84 | 11.84 | 11.85 | 11.92 | 11.82 | 11.6
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | System Transformation | Headroom (MW) | N/A | 11.85 | 11.82 | 11.81 | 11.78 | 11.73 | 11.69 | 11.64 | 11.7 | 11.69 | 11.67 | 11.65 | 11.63 | 11.62 | 11.61 | 11.6 | 11.49 | 11.05 | 10.59
Chesterfield 132kV | Clipstone | WARSOP 33 11kV S STN | Primary | 11 | -1.1404 | 53.2164 | WPD Best View | Headroom (MW) | N/A | 11.85 | 11.81 | 11.77 | 11.72 | 11.6 | 11.49 | 11.4 | 11.42 | 11.37 | 11.31 | 11.25 | 11.17 | 11.11 | 11.03 | 10.96 | 10.4 | 9.48 | 8.45
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Consumer Transformation | Headroom (MW) | Thermal | 8.05 | 7.95 | 7.87 | 7.77 | 7.46 | 7.22 | 6.98 | 6.76 | 6.54 | 6.34 | 6.13 | 5.93 | 5.73 | 5.52 | 5.29 | 3.59 | 1.66 | -0.44
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Leading the Way | Headroom (MW) | Thermal | 8.05 | 7.94 | 7.85 | 7.75 | 7.39 | 7.14 | 6.89 | 6.65 | 6.41 | 6.19 | 5.96 | 5.73 | 5.49 | 5.24 | 4.96 | 3.16 | 1.02 | -1.65
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | Steady Progression | Headroom (MW) | N/A | 8.05 | 8 | 7.97 | 7.94 | 7.9 | 7.86 | 7.82 | 7.78 | 7.74 | 7.71 | 7.67 | 7.64 | 7.62 | 7.59 | 7.58 | 7.53 | 7.18 | 6.78
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | System Transformation | Headroom (MW) | N/A | 8.05 | 7.97 | 7.92 | 7.86 | 7.73 | 7.62 | 7.5 | 7.38 | 7.27 | 7.17 | 7.08 | 6.99 | 6.9 | 6.83 | 6.76 | 6.29 | 5.4 | 4.54
Chesterfield 132kV | Goitside | EYAM 33 11kV S STN | Primary | 11 | -1.6731 | 53.2801 | WPD Best View | Headroom (MW) | Thermal | 8.05 | 7.95 | 7.87 | 7.77 | 7.46 | 7.22 | 6.98 | 6.76 | 6.55 | 6.34 | 6.14 | 5.95 | 5.75 | 5.53 | 5.31 | 3.6 | 1.68 | -0.42
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Consumer Transformation | Headroom (MW) | Thermal | 15.09 | 14.83 | 14.59 | 14.29 | 13.69 | 13.17 | 12.68 | 12.2 | 11.76 | 11.36 | 10.97 | 10.59 | 10.16 | 9.7 | 9.2 | 5.72 | 0.73 | -4.86
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Leading the Way | Headroom (MW) | Thermal | 15.09 | 14.81 | 14.56 | 14.24 | 13.6 | 13.05 | 12.53 | 12.04 | 11.57 | 11.15 | 10.69 | 10.26 | 9.74 | 9.15 | 8.49 | 4.14 | -1.65 | -9.44
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | Steady Progression | Headroom (MW) | N/A | 15.09 | 14.96 | 14.89 | 14.83 | 14.77 | 14.68 | 14.6 | 14.52 | 14.44 | 14.36 | 14.3 | 14.27 | 14.23 | 14.22 | 14.21 | 14.11 | 13.37 | 12.28
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | System Transformation | Headroom (MW) | N/A | 15.09 | 14.9 | 14.75 | 14.6 | 14.37 | 14.14 | 13.89 | 13.65 | 13.43 | 13.23 | 13.04 | 12.92 | 12.77 | 12.65 | 12.49 | 11.42 | 9.04 | 6.73
Chesterfield 132kV | Goitside | GOITSIDE 6 6kV S STN | Primary | 6.6 | -1.4448 | 53.2334 | WPD Best View | Headroom (MW) | Thermal | 15.09 | 14.83 | 14.59 | 14.29 | 13.69 | 13.17 | 12.68 | 12.2 | 11.76 | 11.36 | 10.97 | 10.59 | 10.16 | 9.7 | 9.2 | 5.72 | 0.73 | -4.86
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Consumer Transformation | Headroom (MW) | N/A | 22.63 | 22.52 | 22.45 | 22.37 | 22.28 | 22.19 | 21.97 | 21.76 | 21.56 | 21.38 | 21.2 | 21.02 | 20.84 | 20.64 | 20.44 | 19.16 | 17.57 | 15.85
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Leading the Way | Headroom (MW) | N/A | 22.63 | 22.51 | 22.44 | 22.36 | 22.24 | 22.15 | 21.92 | 21.71 | 21.51 | 21.32 | 21.12 | 20.93 | 20.72 | 20.5 | 20.26 | 18.81 | 17.04 | 14.82
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | Steady Progression | Headroom (MW) | N/A | 22.63 | 22.53 | 22.47 | 22.41 | 22.35 | 22.3 | 22.25 | 22.19 | 22.14 | 22.09 | 22.03 | 21.98 | 21.92 | 21.87 | 21.82 | 21.58 | 21.3 | 21
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | System Transformation | Headroom (MW) | N/A | 22.63 | 22.52 | 22.46 | 22.39 | 22.32 | 22.26 | 22.2 | 22.14 | 22.09 | 22 | 21.9 | 21.8 | 21.7 | 21.62 | 21.53 | 21.07 | 20.24 | 19.38
Chesterfield 132kV | Goitside | QUEENS PARK 33 11kV S STN | Primary | 11 | -1.4312 | 53.2334 | WPD Best View | Headroom (MW) | N/A | 22.63 | 22.52 | 22.45 | 22.37 | 22.28 | 22.19 | 21.97 | 21.76 | 21.56 | 21.38 | 21.2 | 21.02 | 20.84 | 20.64 | 20.44 | 19.16 | 17.57 | 15.85
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Consumer Transformation | Headroom (MW) | Thermal | -2.49 | -2.52 | -2.55 | -2.59 | -2.68 | -2.76 | -2.84 | -2.92 | -3 | -3.07 | -3.13 | -3.19 | -3.26 | -3.33 | -3.41 | -3.98 | -4.6 | -5.31
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Leading the Way | Headroom (MW) | Thermal | -2.49 | -2.53 | -2.56 | -2.6 | -2.69 | -2.78 | -2.86 | -2.95 | -3.03 | -3.1 | -3.17 | -3.24 | -3.32 | -3.4 | -3.49 | -4.09 | -4.78 | -5.66
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | Steady Progression | Headroom (MW) | Thermal | -2.49 | -2.51 | -2.52 | -2.53 | -2.54 | -2.55 | -2.57 | -2.58 | -2.6 | -2.61 | -2.62 | -2.64 | -2.64 | -2.65 | -2.66 | -2.65 | -2.75 | -2.88
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | System Transformation | Headroom (MW) | Thermal | -2.49 | -2.52 | -2.54 | -2.56 | -2.59 | -2.63 | -2.67 | -2.71 | -2.75 | -2.79 | -2.82 | -2.85 | -2.88 | -2.9 | -2.92 | -3.06 | -3.35 | -3.63
Chesterfield 132kV | Goitside | ROBIN HOOD 33 11kV S STN | Primary | 11 | -1.5801 | 53.2436 | WPD Best View | Headroom (MW) | Thermal | -2.49 | -2.52 | -2.55 | -2.59 | -2.68 | -2.76 | -2.84 | -2.92 | -3 | -3.07 | -3.13 | -3.19 | -3.26 | -3.33 | -3.41 | -3.98 | -4.6 | -5.31
#N/A | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | #N/A | -1.4256 | 53.248 | Consumer Transformation | Headroom (MW) | Fault level | -37.5106 | -37.5829 | -37.6494 | -37.7347 | -37.9485 | -38.1714 | -38.3864 | -38.6059 | -38.8304 | -39.0544 | -39.2999 | -39.5555 | -39.8145 | -40.0797 | -40.3274 | -41.584 | -42.9179 | -44.2716
#N/A | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | #N/A | -1.4256 | 53.248 | Leading the Way | Headroom (MW) | Fault level | -51.3361 | -51.4411 | -51.5353 | -51.6558 | -51.9469 | -52.2589 | -52.5647 | -52.8705 | -53.1856 | -53.5099 | -53.8675 | -54.2435 | -54.6266 | -55.0219 | -55.3841 | -57.2205 | -59.1842 | -61.1882
#N/A | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | #N/A | -1.4256 | 53.248 | Steady Progression | Headroom (MW) | Fault level | -20.6931 | -20.7062 | -20.7127 | -20.7193 | -20.7271 | -20.7442 | -20.7625 | -20.7837 | -20.8039 | -20.8285 | -20.8547 | -20.8808 | -20.9079 | -20.9362 | -20.9627 | -21.0869 | -21.2183 | -21.3527
#N/A | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | #N/A | -1.4256 | 53.248 | System Transformation | Headroom (MW) | Fault level | -29.5704 | -29.6055 | -29.6322 | -29.6629 | -29.7221 | -29.7977 | -29.8813 | -29.9676 | -30.0561 | -30.1451 | -30.2438 | -30.3479 | -30.4547 | -30.565 | -30.6664 | -31.1748 | -31.7002 | -32.2264
#N/A | Goitside | SHEFFIELD ROAD 6 6kV S STN | Primary | #N/A | -1.4256 | 53.248 | WPD Best View | Headroom (MW) | Fault level | -30.8311 | -30.8905 | -30.9452 | -31.0152 | -31.191 | -31.3742 | -31.5509 | -31.7313 | -31.9159 | -32.1 | -32.3018 | -32.5119 | -32.7247 | -32.9427 | -33.1463 | -34.1791 | -35.2755 | -36.3881
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Consumer Transformation | Headroom (MW) | N/A | 7.71 | 7.63 | 7.55 | 7.46 | 7.28 | 7.12 | 6.97 | 6.82 | 6.68 | 6.55 | 6.44 | 6.33 | 6.22 | 6.1 | 5.96 | 4.9 | 3.49 | 1.91
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Leading the Way | Headroom (MW) | N/A | 7.71 | 7.62 | 7.54 | 7.44 | 7.26 | 7.08 | 6.91 | 6.74 | 6.58 | 6.42 | 6.29 | 6.16 | 6.01 | 5.85 | 5.67 | 4.4 | 2.77 | 0.6
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | Steady Progression | Headroom (MW) | N/A | 7.71 | 7.66 | 7.63 | 7.61 | 7.58 | 7.55 | 7.51 | 7.48 | 7.45 | 7.42 | 7.4 | 7.37 | 7.35 | 7.34 | 7.32 | 7.34 | 7.08 | 6.74
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | System Transformation | Headroom (MW) | N/A | 7.71 | 7.65 | 7.6 | 7.54 | 7.47 | 7.39 | 7.3 | 7.21 | 7.13 | 7.06 | 7 | 6.95 | 6.9 | 6.86 | 6.82 | 6.55 | 5.86 | 5.18
Chesterfield 132kV | Goitside | WALTON 33 11kV S STN | Primary | 11 | -1.4661 | 53.2165 | WPD Best View | Headroom (MW) | N/A | 7.71 | 7.63 | 7.55 | 7.46 | 7.28 | 7.12 | 6.97 | 6.82 | 6.68 | 6.55 | 6.44 | 6.33 | 6.22 | 6.1 | 5.96 | 4.9 | 3.49 | 1.91
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Consumer Transformation | Headroom (MW) | Thermal | 6.07 | 5.96 | 5.86 | 5.75 | 5.52 | 5.35 | 5.14 | 4.89 | 4.65 | 4.43 | 4.2 | 3.96 | 3.72 | 3.47 | 3.2 | 1.4 | -0.74 | -3.1
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Leading the Way | Headroom (MW) | Thermal | 6.07 | 5.95 | 5.85 | 5.72 | 5.48 | 5.32 | 5.09 | 4.82 | 4.54 | 4.28 | 3.99 | 3.71 | 3.43 | 3.12 | 2.79 | 0.77 | -1.68 | -4.93
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | Steady Progression | Headroom (MW) | N/A | 6.07 | 6.02 | 5.99 | 5.97 | 5.98 | 5.99 | 5.96 | 5.94 | 5.92 | 5.89 | 5.86 | 5.84 | 5.82 | 5.81 | 5.79 | 5.73 | 5.42 | 4.96
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | System Transformation | Headroom (MW) | N/A | 6.07 | 5.99 | 5.93 | 5.87 | 5.82 | 5.77 | 5.67 | 5.55 | 5.43 | 5.32 | 5.21 | 5.11 | 5.01 | 4.92 | 4.81 | 4.2 | 3.19 | 2.19
Chesterfield 132kV | Goitside | WINGERWORTH 33 11kV S STN | Primary | 11 | -1.4198 | 53.2071 | WPD Best View | Headroom (MW) | Thermal | 6.07 | 5.96 | 5.86 | 5.75 | 5.52 | 5.35 | 5.14 | 4.89 | 4.65 | 4.43 | 4.2 | 3.96 | 3.72 | 3.47 | 3.2 | 1.4 | -0.74 | -3.1
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Consumer Transformation | Headroom (MW) | Fault level | -70.5095 | -70.5433 | -70.5862 | -70.6381 | -70.7854 | -70.9349 | -71.1047 | -71.2831 | -71.4602 | -71.6408 | -71.928 | -72.2344 | -72.5571 | -72.8669 | -73.2055 | -71.1181 | -69.4586 | -67.7331
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Leading the Way | Headroom (MW) | Fault level | -96.4974 | -96.5445 | -96.6048 | -96.6774 | -96.872 | -97.0936 | -97.3052 | -97.5253 | -97.7461 | -97.9685 | -98.2179 | -98.4743 | -98.8859 | -99.2921 | -89.2362 | -50.0284 | -130.7732 | -132.4351
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | Steady Progression | Headroom (MW) | Fault level | -38.8973 | -38.9007 | -38.9041 | -38.9066 | -38.9094 | -38.9194 | -40.204 | -41.4513 | -42.6597 | -42.6781 | -42.7079 | -42.7416 | -42.8023 | -42.8623 | -42.9386 | -43.0942 | -41.9992 | -42.1984
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | System Transformation | Headroom (MW) | Fault level | -55.584 | -55.5974 | -55.6134 | -55.6307 | -55.6668 | -55.7148 | -55.7846 | -55.8602 | -55.9385 | -56.019 | -56.1734 | -56.3469 | -56.5301 | -56.7032 | -56.9029 | -40.0687 | -70.8174 | -71.6025
Chesterfield 132kV | Mansfield | ACREAGE LANE 33 11kV S STN | Primary | 11 | -1.2081 | 53.1954 | WPD Best View | Headroom (MW) | Fault level | -57.9538 | -57.9817 | -58.0169 | -58.0596 | -58.1806 | -58.3035 | -58.4431 | -58.5897 | -58.7353 | -58.8837 | -59.1198 | -59.3716 | -59.6369 | -59.8915 | -60.1698 | -58.4541 | -57.0901 | -55.6719
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Consumer Transformation | Headroom (MW) | N/A | 14.1777 | 14.071 | 13.9757 | 13.8442 | 13.5243 | 13.2089 | 12.8861 | 12.5492 | 12.2028 | 11.8507 | 11.4653 | 11.076 | 10.7098 | 10.3391 | 9.9762 | 8.1994 | 6.3373 | 4.4759
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Leading the Way | Headroom (MW) | N/A | 19.4032 | 19.2542 | 19.1206 | 18.9337 | 18.4997 | 18.0441 | 17.5831 | 17.0981 | 16.5946 | 16.0742 | 15.5081 | 14.9274 | 14.3953 | 13.8625 | 13.3382 | 10.7635 | 8.0785 | 5.317
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | Steady Progression | Headroom (MW) | N/A | 7.8213 | 7.7967 | 7.7892 | 7.7802 | 7.7696 | 7.7466 | 7.7198 | 7.689 | 7.6582 | 7.6211 | 7.5819 | 7.5417 | 7.5028 | 7.4636 | 7.4259 | 7.2961 | 7.1028 | 6.9049
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | System Transformation | Headroom (MW) | N/A | 11.1766 | 11.1223 | 11.0863 | 11.04 | 10.9533 | 10.8483 | 10.7233 | 10.5898 | 10.4515 | 10.3092 | 10.1535 | 9.9934 | 9.8452 | 9.6944 | 9.545 | 8.8466 | 8.11 | 7.356
Chesterfield 132kV | Mansfield | LIME TREE PLACE 33 11kV S STN | Primary | 11 | -1.1911 | 53.1415 | WPD Best View | Headroom (MW) | N/A | 11.6531 | 11.5654 | 11.487 | 11.379 | 11.116 | 10.8568 | 10.5915 | 10.3146 | 10.0298 | 9.7404 | 9.4237 | 9.1037 | 8.8027 | 8.498 | 8.1998 | 6.7393 | 5.2089 | 3.6788
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Consumer Transformation | Headroom (MW) | Fault level | -13.5943 | -13.6959 | -13.8251 | -14.0017 | -14.4379 | -14.8803 | -15.3209 | -15.7729 | -16.2356 | -16.7113 | -17.2264 | -17.7444 | -18.259 | -18.7787 | -19.2933 | -21.9459 | -25.4008 | -28.3812
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Leading the Way | Headroom (MW) | Fault level | -18.6048 | -18.7461 | -18.9261 | -19.1724 | -19.7663 | -20.4057 | -21.0358 | -21.6829 | -22.3548 | -23.0529 | -23.8027 | -24.5741 | -25.3356 | -26.1116 | -26.8831 | -30.8678 | -36.6757 | -41.1145
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | Steady Progression | Headroom (MW) | Fault level | -7.4994 | -7.5075 | -7.5153 | -7.524 | -7.5346 | -7.5645 | -7.5978 | -7.6361 | -7.6747 | -7.7229 | -7.7727 | -7.8229 | -7.872 | -7.9215 | -7.9692 | -8.2185 | -8.5099 | -8.8109
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | System Transformation | Headroom (MW) | Fault level | -10.7167 | -10.754 | -10.7998 | -10.8572 | -10.9689 | -11.1126 | -11.2789 | -11.4528 | -11.6321 | -11.8189 | -12.0191 | -12.2246 | -12.4283 | -12.6352 | -12.8424 | -13.9113 | -15.4935 | -16.663
Chesterfield 132kV | Mansfield | MANSFIELD 11kV S STN | Primary | 11 | -1.1994 | 53.156 | WPD Best View | Headroom (MW) | Fault level | -11.1736 | -11.2571 | -11.3633 | -11.5084 | -11.8669 | -12.2305 | -12.5927 | -12.9642 | -13.3445 | -13.7355 | -14.1589 | -14.5847 | -15.0076 | -15.4348 | -15.8577 | -18.038 | -20.8777 | -23.3274
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Consumer Transformation | Headroom (MW) | Thermal | 6.71 | -1.61 | -1.69 | -1.77 | -1.88 | -1.95 | -2.84 | -3.79 | -4.68 | -5.33 | -5.74 | -6.05 | -6.29 | -6.55 | -6.82 | -5.6 | -7.28 | -13.7
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Leading the Way | Headroom (MW) | Thermal | 6.71 | -1.62 | -1.7 | -1.79 | -1.93 | -2.01 | -2.31 | -2.75 | -3.21 | -3.32 | -8.38 | -8.66 | -8.95 | -9.27 | -4.1 | -12.55 | -10.83 | -10.96
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | Steady Progression | Headroom (MW) | Thermal | 6.71 | -1.59 | -1.64 | -1.69 | -1.72 | -1.77 | -2.98 | -4.15 | -5.28 | -6.33 | -7.26 | -8.04 | -8.44 | -8.74 | -8.91 | -9.15 | -9.47 | -9.85
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | System Transformation | Headroom (MW) | Thermal | 6.71 | -1.6 | -1.66 | -1.73 | -1.78 | -1.83 | -2.7 | -3.49 | -4.17 | -4.62 | -8.02 | -8.15 | -8.22 | -8.28 | -7.39 | -12.07 | -12.55 | -13.19
Chesterfield 132kV | Mansfield | SKEGBY LANE 33 11kV S STN | Primary | 11 | -1.2176 | 53.1378 | WPD Best View | Headroom (MW) | Thermal | 6.71 | -1.61 | -1.69 | -1.77 | -1.88 | -1.95 | -2.84 | -3.79 | -4.68 | -5.33 | -5.74 | -6.05 | -6.29 | -6.55 | -6.82 | -5.6 | -7.28 | -13.7
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Consumer Transformation | Headroom (MW) | N/A | 8.25 | 8.15 | 8.07 | 7.98 | 7.77 | 7.62 | 7.45 | 7.28 | 7.12 | 6.98 | 6.85 | 6.73 | 6.6 | 6.46 | 6.32 | 5.1 | 3.51 | 1.75
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Leading the Way | Headroom (MW) | N/A | 8.25 | 8.15 | 8.06 | 7.96 | 7.74 | 7.57 | 7.39 | 7.21 | 7.03 | 6.87 | 6.72 | 6.57 | 6.39 | 6.21 | 6 | 4.58 | 2.75 | 0.38
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | Steady Progression | Headroom (MW) | N/A | 8.25 | 8.19 | 8.16 | 8.14 | 8.11 | 8.08 | 8.05 | 8.01 | 7.98 | 7.94 | 7.91 | 7.89 | 7.87 | 7.85 | 7.83 | 7.82 | 7.6 | 7.24
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | System Transformation | Headroom (MW) | N/A | 8.25 | 8.17 | 8.12 | 8.07 | 7.98 | 7.91 | 7.82 | 7.73 | 7.64 | 7.56 | 7.5 | 7.44 | 7.39 | 7.34 | 7.3 | 7.01 | 6.24 | 5.48
Chesterfield 132kV | Mansfield | TEVERSAL 33 11kV S STN | Primary | 11 | -1.2919 | 53.1485 | WPD Best View | Headroom (MW) | N/A | 8.25 | 8.15 | 8.07 | 7.98 | 7.77 | 7.62 | 7.45 | 7.28 | 7.12 | 6.98 | 6.85 | 6.73 | 6.6 | 6.46 | 6.32 | 5.1 | 3.51 | 1.75
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Consumer Transformation | Headroom (MW) | N/A | 25.38 | 14.38 | 14.23 | 14.07 | 13.78 | 13.56 | 12.55 | 11.59 | 10.73 | 10.13 | 9.62 | 9.26 | 9 | 8.68 | 8.35 | 5.71 | 13.82 | 0.01
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Leading the Way | Headroom (MW) | Thermal | 25.38 | 14.37 | 14.22 | 14.05 | 13.74 | 13.51 | 13.03 | 12.57 | 12.11 | 11.93 | 11.69 | 11.46 | 11.22 | 10.9 | 10.56 | 18.65 | -0.72 | -3.97
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | Steady Progression | Headroom (MW) | N/A | 25.38 | 14.41 | 14.3 | 14.2 | 14.08 | 13.97 | 12.78 | 11.6 | 10.46 | 9.38 | 8.44 | 7.65 | 7.23 | 6.9 | 6.69 | 6.36 | 5.85 | 5.18
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | System Transformation | Headroom (MW) | N/A | 25.38 | 14.4 | 14.27 | 14.14 | 13.97 | 13.82 | 12.91 | 12.07 | 11.29 | 10.78 | 10.42 | 10.22 | 10.12 | 10 | 9.88 | 15.86 | 3.65 | 2.4
Chesterfield 132kV | Pinxton 132 11 | PINXTON 11kV S STN | Primary | 11 | -1.3031 | 53.106 | WPD Best View | Headroom (MW) | N/A | 25.38 | 14.38 | 14.23 | 14.07 | 13.78 | 13.56 | 12.55 | 11.59 | 10.73 | 10.13 | 9.62 | 9.26 | 9 | 8.68 | 8.35 | 5.71 | 13.82 | 0.01
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Consumer Transformation | Headroom (MW) | Thermal | 9.26 | 9.17 | 9.05 | 8.88 | 8.49 | 8.19 | 7.96 | 7.56 | 7.15 | 6.73 | 6.25 | 5.78 | 5.2 | 4.64 | 3.98 | 1.26 | -2.34 | -6.46
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Leading the Way | Headroom (MW) | Thermal | 9.26 | 9.16 | 9.02 | 8.85 | 8.42 | 8.1 | 7.88 | 7.59 | 7.31 | 7.04 | 6.77 | 6.56 | 6.04 | 5.48 | 4.86 | 1.65 | -2.61 | -7.17
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | Steady Progression | Headroom (MW) | N/A | 9.26 | 9.2 | 9.16 | 9.13 | 9.08 | 9.05 | 9.08 | 9.04 | 8.98 | 8.9 | 8.8 | 8.73 | 8.53 | 8.34 | 8.1 | 7.88 | 7.18 | 6.2
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | System Transformation | Headroom (MW) | N/A | 9.26 | 9.18 | 9.13 | 9.05 | 8.88 | 8.75 | 8.67 | 8.41 | 8.12 | 7.82 | 7.47 | 7.12 | 6.72 | 6.37 | 5.91 | 4.86 | 2.79 | 0.55
Chesterfield 132kV | Staveley | ECKINGTON 33 11kV S STN | Primary | 11 | -1.3663 | 53.3032 | WPD Best View | Headroom (MW) | Thermal | 9.26 | 9.18 | 9.1 | 8.99 | 8.7 | 8.47 | 8.31 | 7.99 | 7.64 | 7.27 | 6.85 | 6.43 | 5.95 | 5.47 | 4.89 | 2.81 | 0.03 | -3.28
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Consumer Transformation | Headroom (MW) | Fault level | -13.6855 | -13.7673 | -13.8564 | -13.9732 | -14.2452 | -14.5194 | -14.792 | -15.139 | -15.5092 | -15.8878 | -16.2286 | -16.6049 | -16.9931 | -17.3802 | -17.7656 | -19.4443 | -21.1636 | -22.9116
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Leading the Way | Headroom (MW) | Fault level | -18.7296 | -18.8431 | -18.969 | -19.1335 | -19.5126 | -19.9041 | -20.2933 | -20.6802 | -21.0756 | -21.4509 | -21.8625 | -22.3235 | -22.8641 | -23.4131 | -23.9367 | -26.4596 | -28.9994 | -31.5941
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | Steady Progression | Headroom (MW) | Fault level | -7.5497 | -7.5653 | -7.5728 | -7.5802 | -7.589 | -7.6086 | -7.631 | -7.6658 | -7.701 | -7.744 | -7.7801 | -7.8196 | -7.8722 | -7.9261 | -7.9852 | -8.1788 | -8.35 | -8.5256
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | System Transformation | Headroom (MW) | Fault level | -10.7885 | -10.8268 | -10.861 | -10.9015 | -10.9758 | -11.0665 | -11.1729 | -11.3383 | -11.5234 | -11.7155 | -11.8685 | -12.0434 | -12.2271 | -12.409 | -12.594 | -13.3071 | -13.9868 | -14.6691
Chesterfield 132kV | Staveley | STAVELEY 11kV S STN | Primary | 11 | -1.3851 | 53.2671 | WPD Best View | Headroom (MW) | Fault level | -11.2485 | -11.3158 | -11.389 | -11.485 | -11.7086 | -11.934 | -12.158 | -12.4432 | -12.7474 | -13.0586 | -13.3388 | -13.6481 | -13.9672 | -14.2853 | -14.6021 | -15.9818 | -17.395 | -18.8318
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Consumer Transformation | Headroom (MW) | Thermal | 3.96 | 4.04 | 4.13 | 4.03 | 3.78 | 3.56 | 3.33 | 3.1 | 2.89 | 2.69 | 2.49 | 2.25 | 2.04 | 1.82 | 1.58 | -0.68 | -2.72 | -4.99
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Leading the Way | Headroom (MW) | Thermal | 3.96 | 4.06 | 4.17 | 4.04 | 3.75 | 3.49 | 3.24 | 3 | 2.79 | 2.58 | 2.33 | 2.06 | 1.82 | 1.56 | 1.28 | -1.26 | -3.62 | -6.77
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | Steady Progression | Headroom (MW) | N/A | 3.96 | 4.08 | 4.22 | 4.23 | 4.24 | 4.23 | 4.22 | 4.2 | 4.18 | 4.14 | 4.1 | 4.06 | 4.04 | 4.02 | 4.01 | 3.97 | 3.71 | 3.23
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | System Transformation | Headroom (MW) | N/A | 3.96 | 4.07 | 4.21 | 4.17 | 4.1 | 4.01 | 3.9 | 3.77 | 3.66 | 3.55 | 3.45 | 3.35 | 3.28 | 3.2 | 3.11 | 2.28 | 1.28 | 0.31
Chesterfield 132kV | Whitwell | CLOWNE 33 11kV S STN | Primary | 11 | -1.2405 | 53.2791 | WPD Best View | Headroom (MW) | Thermal | 3.96 | 4.04 | 4.13 | 4.03 | 3.78 | 3.56 | 3.33 | 3.1 | 2.89 | 2.69 | 2.49 | 2.25 | 2.04 | 1.82 | 1.58 | -0.68 | -2.72 | -4.99
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Consumer Transformation | Headroom (MW) | Thermal | 3.6 | 3.45 | 3.33 | 3.19 | 2.92 | 2.69 | 1.81 | 0.46 | -0.54 | -1.45 | -2.36 | -3.18 | -3.95 | -4.78 | -5.69 | -12.77 | -18.93 | -25.44
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Leading the Way | Headroom (MW) | Thermal | 3.6 | 3.44 | 3.32 | 3.19 | 2.91 | 2.68 | 1.88 | 1.16 | 0.63 | -0.09 | -0.75 | -1.36 | -2.01 | -2.72 | -3.5 | -12.05 | -14.93 | -24.86
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | Steady Progression | Headroom (MW) | Thermal | 3.6 | 3.49 | 3.43 | 3.37 | 3.29 | 3.23 | 2.93 | 2.61 | 2.25 | 1.48 | 1.15 | 0.83 | 0.57 | 0.39 | 0.27 | 0.03 | -0.4 | -1.05
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | System Transformation | Headroom (MW) | Thermal | 3.6 | 3.47 | 3.39 | 3.3 | 3.17 | 3.05 | 2.78 | 2.49 | 1.84 | 1.46 | 1.09 | 0.8 | 0.55 | 0.37 | 0.19 | -2.95 | -2.2 | -6.68
Chesterfield 132kV | Whitwell | CRAGGS LANE 33 11kV S STN | Primary | 11 | -1.1997 | 53.2741 | WPD Best View | Headroom (MW) | Thermal | 3.6 | 3.45 | 3.33 | 3.19 | 2.93 | 2.7 | 1.83 | 0.48 | -0.5 | -1.4 | -2.3 | -3.12 | -3.88 | -4.71 | -5.61 | -12.57 | -18.72 | -25.19
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Consumer Transformation | Headroom (MW) | Thermal | 3.83 | 3.74 | 3.69 | 3.63 | 3.51 | 3.45 | 2.99 | 2.54 | 2.13 | 1.74 | 1.46 | 1.26 | 1.09 | 0.92 | 0.74 | -0.56 | -1.4 | -2.5
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Leading the Way | Headroom (MW) | Thermal | 3.83 | 3.73 | 3.67 | 3.61 | 3.45 | 3.39 | 3.21 | 3.02 | 2.79 | 2.61 | 2.43 | 2.25 | 2.05 | 1.85 | 1.63 | 0.25 | 5.05 | -6.06
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | Steady Progression | Headroom (MW) | Thermal | 3.83 | 3.76 | 3.72 | 3.68 | 3.62 | 3.59 | 2.98 | 2.35 | 1.74 | 1.17 | 0.66 | 0.23 | 0 | -0.17 | -0.29 | -0.46 | -0.7 | -0.94
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | System Transformation | Headroom (MW) | N/A | 3.83 | 3.75 | 3.7 | 3.66 | 3.57 | 3.53 | 3.08 | 2.64 | 2.26 | 1.99 | 1.82 | 1.74 | 1.69 | 1.64 | 1.59 | 1.34 | 7.05 | 0.28
Chesterfield 132kV | Whitwell | HALFWAY 33 11kV S STN | Primary | 11 | -1.3421 | 53.3283 | WPD Best View | Headroom (MW) | Thermal | 3.83 | 3.76 | 3.72 | 3.68 | 3.62 | 3.58 | 2.97 | 2.33 | 1.71 | 1.13 | 0.62 | 0.18 | -0.05 | -0.22 | -0.34 | -0.61 | -0.86 | -1.14
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Consumer Transformation | Headroom (MW) | N/A | 8.46 | 8.62 | 8.8 | 8.94 | 8.76 | 8.61 | 8.49 | 8.37 | 8.25 | 8.11 | 7.95 | 7.78 | 7.62 | 7.44 | 7.26 | 6.03 | 4.63 | 3.06
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Leading the Way | Headroom (MW) | N/A | 8.46 | 8.64 | 8.85 | 9.05 | 8.81 | 8.62 | 8.48 | 8.35 | 8.21 | 8.03 | 7.84 | 7.65 | 7.46 | 7.25 | 7.02 | 5.71 | 4.13 | 2.12
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | Steady Progression | Headroom (MW) | N/A | 8.46 | 8.63 | 8.83 | 9.01 | 9.02 | 9.02 | 9.04 | 9.07 | 9.09 | 9.07 | 9.06 | 9.04 | 9.02 | 9 | 8.97 | 8.92 | 8.66 | 8.29
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | System Transformation | Headroom (MW) | N/A | 8.46 | 8.64 | 8.85 | 9.03 | 8.98 | 8.93 | 8.89 | 8.84 | 8.8 | 8.73 | 8.65 | 8.57 | 8.49 | 8.42 | 8.34 | 7.98 | 7.28 | 6.59
Chesterfield 132kV | Whitwell | HOLME CARR 33 11kV S STN | Primary | 11 | -1.165 | 53.3133 | WPD Best View | Headroom (MW) | N/A | 8.46 | 8.62 | 8.8 | 8.94 | 8.76 | 8.61 | 8.49 | 8.37 | 8.25 | 8.11 | 7.95 | 7.78 | 7.62 | 7.44 | 7.26 | 6.03 | 4.63 | 3.06
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Consumer Transformation | Headroom (MW) | Thermal | 3.91 | 3.85 | 3.79 | -2.43 | -2.62 | -2.79 | -3.38 | -3.95 | -4.46 | -4.86 | -5.14 | -5.34 | -5.49 | -5.65 | -5.82 | -7.21 | -7.99 | -9.04
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Leading the Way | Headroom (MW) | Thermal | 3.91 | 3.84 | 3.78 | -2.45 | -2.66 | -2.85 | -3.17 | -3.49 | -3.83 | -4.04 | -4.23 | -4.42 | -4.62 | -4.83 | -5.05 | -6.45 | -4.52 | -3.54
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | Steady Progression | Headroom (MW) | Thermal | 3.91 | 3.89 | 3.87 | -2.29 | -2.32 | -2.34 | -2.98 | -3.61 | -4.22 | -4.8 | -5.31 | -5.73 | -5.95 | -6.11 | -6.21 | -6.25 | -6.53 | -6.81
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | System Transformation | Headroom (MW) | Thermal | 3.91 | 3.87 | 3.84 | -2.35 | -2.43 | -2.51 | -3.03 | -3.51 | -3.95 | -4.27 | -4.47 | -4.59 | -4.65 | -4.71 | -4.78 | -5.18 | -5.19 | -5.31
Chesterfield 132kV | Whitwell | SHIREBROOK 33 11kV S STN | Primary | 11 | -1.2442 | 53.1962 | WPD Best View | Headroom (MW) | Thermal | 3.91 | 3.85 | 3.79 | -2.43 | -2.62 | -2.79 | -3.38 | -3.95 | -4.46 | -4.86 | -5.14 | -5.34 | -5.49 | -5.65 | -5.82 | -7.21 | -7.99 | -9.04
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Consumer Transformation | Headroom (MW) | Thermal | 11.33 | 11.17 | 11.05 | 10.91 | 10.63 | 10.4 | 9.97 | 9.36 | 8.87 | 8.38 | 7.89 | 7.42 | 6.95 | 6.45 | 5.9 | 2.66 | -1.18 | -5.3
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Leading the Way | Headroom (MW) | Thermal | 11.33 | 11.16 | 11.04 | 10.9 | 10.59 | 10.35 | 9.89 | 9.49 | 9.13 | 8.64 | 8.21 | 7.78 | 7.32 | 6.83 | 6.28 | 3.3 | -0.32 | -4.52
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | Steady Progression | Headroom (MW) | N/A | 11.33 | 11.21 | 11.15 | 11.08 | 11.01 | 10.94 | 10.88 | 10.84 | 10.76 | 10.49 | 10.4 | 10.3 | 10.19 | 10.11 | 10.04 | 9.82 | 9.34 | 8.75
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | System Transformation | Headroom (MW) | N/A | 11.33 | 11.19 | 11.11 | 11.02 | 10.87 | 10.75 | 10.63 | 10.53 | 10.24 | 10.03 | 9.83 | 9.64 | 9.46 | 9.32 | 9.16 | 8.33 | 6.95 | 5.54
Chesterfield 132kV | Whitwell | WESTHORPE 33 11kV S STN | Primary | 11 | -1.3165 | 53.3089 | WPD Best View | Headroom (MW) | Thermal | 11.33 | 11.17 | 11.05 | 10.91 | 10.63 | 10.4 | 9.97 | 9.37 | 8.87 | 8.38 | 7.9 | 7.43 | 6.97 | 6.46 | 5.92 | 2.68 | -1.17 | -5.29
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Consumer Transformation | Headroom (MW) | Thermal | 11.6 | 12.02 | 12.48 | 12.88 | 13.22 | 13.42 | 13.53 | 13.11 | 12.57 | 11.72 | 10.55 | 9.16 | 7.64 | 6.23 | 4.47 | 1.31 | -2.64 | -7.47
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Leading the Way | Headroom (MW) | Thermal | 11.6 | 12.08 | 12.59 | 13.07 | 13.44 | 13.7 | 13.81 | 13.95 | 14.08 | 13.92 | 13.79 | 13.69 | 12.53 | 11.43 | 10.28 | 6.74 | 1.68 | -0.3
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | Steady Progression | Headroom (MW) | N/A | 11.6 | 11.99 | 12.43 | 12.83 | 13.24 | 13.53 | 13.75 | 13.83 | 13.91 | 13.82 | 13.66 | 13.42 | 12.68 | 11.92 | 10.88 | 9.64 | 7.83 | 5.92
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | System Transformation | Headroom (MW) | Thermal | 11.6 | 12.03 | 12.52 | 12.95 | 13.37 | 13.64 | 13.82 | 13.47 | 12.97 | 12.19 | 11.09 | 9.77 | 8.3 | 6.96 | 5.26 | 2.85 | -0.61 | -4.89
Coventry 132kV | Coventry North | ANSTY 33 11kV S STN | Primary | 11 | -1.401 | 52.4289 | WPD Best View | Headroom (MW) | N/A | 11.6 | 11.98 | 12.41 | 12.78 | 13.16 | 13.41 | 13.58 | 13.61 | 13.63 | 13.48 | 13.24 | 12.96 | 12.19 | 11.39 | 10.31 | 8.94 | 7.07 | 5.1
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Consumer Transformation | Headroom (MW) | N/A | 13.31 | 13.37 | 13.45 | 13.51 | 13.47 | 13.44 | 13.31 | 13.09 | 12.84 | 12.58 | 12.32 | 12.12 | 11.93 | 11.71 | 11.49 | 10.28 | 8.86 | 7.29
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Leading the Way | Headroom (MW) | N/A | 13.31 | 13.37 | 13.46 | 13.54 | 13.45 | 13.41 | 13.23 | 12.98 | 12.69 | 12.38 | 12.07 | 11.87 | 11.66 | 11.44 | 11.22 | 10 | 8.43 | 6.3
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | Steady Progression | Headroom (MW) | N/A | 13.31 | 13.37 | 13.45 | 13.52 | 13.52 | 13.53 | 13.54 | 13.54 | 13.54 | 13.53 | 13.52 | 13.51 | 13.49 | 13.47 | 13.45 | 13.38 | 13.21 | 13
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | System Transformation | Headroom (MW) | N/A | 13.31 | 13.38 | 13.46 | 13.54 | 13.52 | 13.51 | 13.51 | 13.49 | 13.47 | 13.35 | 13.19 | 13.08 | 12.98 | 12.88 | 12.78 | 12.39 | 11.69 | 10.94
Coventry 132kV | Coventry North | COVENTRY ARENA 33 11kV S STN | Primary | 11 | -1.4938 | 52.4499 | WPD Best View | Headroom (MW) | N/A | 13.31 | 13.37 | 13.46 | 13.53 | 13.45 | 13.42 | 13.26 | 13.03 | 12.77 | 12.49 | 12.21 | 11.99 | 11.78 | 11.53 | 11.27 | 9.88 | 8.27 | 6.19
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Consumer Transformation | Headroom (MW) | N/A | 14.96 | 14.87 | 14.76 | 14.62 | 14.21 | 13.94 | 13.68 | 13.43 | 13.2 | 12.97 | 12.76 | 12.55 | 12.33 | 12.09 | 11.84 | 9.94 | 7.41 | 4.63
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Leading the Way | Headroom (MW) | N/A | 14.96 | 14.85 | 14.73 | 14.59 | 14.1 | 13.82 | 13.55 | 13.29 | 13.03 | 12.79 | 12.55 | 12.3 | 12.04 | 11.75 | 11.43 | 9.27 | 6.39 | 2.67
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | Steady Progression | Headroom (MW) | N/A | 14.96 | 14.89 | 14.86 | 14.82 | 14.75 | 14.72 | 14.69 | 14.63 | 14.58 | 14.53 | 14.47 | 14.43 | 14.4 | 14.37 | 14.35 | 14.23 | 13.95 | 13.38
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | System Transformation | Headroom (MW) | N/A | 14.96 | 14.88 | 14.83 | 14.75 | 14.56 | 14.44 | 14.31 | 14.17 | 14.05 | 13.93 | 13.83 | 13.73 | 13.64 | 13.56 | 13.49 | 12.95 | 11.72 | 10.53
Coventry 132kV | Coventry North | COVENTRY NORTH 11kV S STN | Primary | 11 | -1.4675 | 52.4538 | WPD Best View | Headroom (MW) | N/A | 14.96 | 14.86 | 14.75 | 14.6 | 14.15 | 13.88 | 13.61 | 13.36 | 13.12 | 12.89 | 12.66 | 12.43 | 12.19 | 11.93 | 11.65 | 9.65 | 6.94 | 3.65
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Consumer Transformation | Headroom (MW) | N/A | 12.025 | 11.995 | 11.965 | 11.875 | 11.595 | 11.345 | 11.095 | 10.815 | 10.535 | 10.265 | 9.995 | 9.715 | 9.455 | 9.165 | 8.855 | 6.745 | 3.625 | 0.095
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Leading the Way | Headroom (MW) | Thermal | 12.025 | 11.995 | 11.965 | 11.895 | 11.605 | 11.345 | 11.075 | 10.785 | 10.485 | 10.185 | 9.865 | 9.545 | 9.225 | 8.855 | 8.445 | 5.815 | 2.175 | -2.745
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | Steady Progression | Headroom (MW) | N/A | 12.025 | 12.075 | 12.135 | 12.195 | 12.265 | 12.285 | 12.295 | 12.295 | 12.285 | 12.275 | 12.265 | 12.265 | 12.265 | 12.275 | 12.245 | 12.085 | 11.695 | 11.065
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | System Transformation | Headroom (MW) | N/A | 12.025 | 12.045 | 12.075 | 12.085 | 12.045 | 11.985 | 11.885 | 11.775 | 11.675 | 11.565 | 11.455 | 11.325 | 11.235 | 11.135 | 11.035 | 10.355 | 8.965 | 7.585
Coventry 132kV | Coventry North | NEWDIGATE 33 11kV S STN | Primary | 11 | -1.4991 | 52.486 | WPD Best View | Headroom (MW) | Thermal | 12.025 | 11.995 | 11.965 | 11.895 | 11.605 | 11.355 | 11.085 | 10.795 | 10.485 | 10.195 | 9.875 | 9.545 | 9.225 | 8.865 | 8.455 | 5.835 | 2.195 | -2.715
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Consumer Transformation | Headroom (MW) | N/A | 18.99 | 18.81 | 18.69 | 15.13 | 14.95 | 14.84 | 14.71 | 14.6 | 14.48 | 14.3 | 14.04 | 13.8 | 13.53 | 13.25 | 19.09 | 16.8 | 14.15 | 11.21
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Leading the Way | Headroom (MW) | Thermal | 18.99 | 24.95 | 24.83 | 21.25 | 21.04 | 20.92 | 20.79 | 20.66 | 20.53 | 20.33 | 20.04 | 19.74 | 19.42 | 19.06 | 18.64 | 15.91 | 4 | -0.27
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | Steady Progression | Headroom (MW) | N/A | 18.99 | 18.84 | 18.75 | 15.23 | 15.14 | 15.06 | 14.95 | 14.88 | 14.8 | 14.73 | 14.65 | 14.57 | 14.49 | 14.42 | 14.34 | 20.15 | 19.75 | 19.24
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | System Transformation | Headroom (MW) | N/A | 18.99 | 18.82 | 18.72 | 15.18 | 15.06 | 14.97 | 14.87 | 14.78 | 14.7 | 14.61 | 14.52 | 14.43 | 14.34 | 14.25 | 20.31 | 19.88 | 12.72 | 11.05
Coventry 132kV | Coventry North | WALSGRAVE 33 11kV S STN | Primary | 11 | -1.4463 | 52.4255 | WPD Best View | Headroom (MW) | N/A | 18.99 | 18.81 | 18.69 | 15.13 | 14.95 | 14.84 | 14.7 | 14.58 | 14.46 | 14.28 | 14.02 | 13.78 | 13.51 | 13.23 | 19.07 | 16.78 | 13.52 | 9.84
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Consumer Transformation | Headroom (MW) | N/A | 20.14 | 20.03 | 19.92 | 19.78 | 19.5 | 19.14 | 18.8 | 18.47 | 18.14 | 17.84 | 17.48 | 17.14 | 16.79 | 16.43 | 16.06 | 13.38 | 9.84 | 5.72
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Leading the Way | Headroom (MW) | N/A | 20.14 | 20.02 | 19.9 | 19.76 | 19.45 | 19 | 18.55 | 18.13 | 17.7 | 17.3 | 16.82 | 16.38 | 15.92 | 15.44 | 14.93 | 11.69 | 7.62 | 2.46
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | Steady Progression | Headroom (MW) | N/A | 20.14 | 20.04 | 19.98 | 19.93 | 19.86 | 19.8 | 19.74 | 19.68 | 19.62 | 19.56 | 19.5 | 19.44 | 19.38 | 19.31 | 19.25 | 18.95 | 18.6 | 18.21
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | System Transformation | Headroom (MW) | N/A | 20.14 | 20.03 | 19.97 | 19.88 | 19.74 | 19.62 | 19.49 | 19.31 | 19.08 | 18.96 | 18.81 | 18.69 | 18.58 | 18.48 | 18.38 | 17.81 | 15.95 | 13.85
Coventry 132kV | Coventry South 132 11 (GT3) | COVENTRY SOUTH 11kV S STN | Primary | 11 | -1.5387 | 52.4059 | WPD Best View | Headroom (MW) | N/A | 20.14 | 20.03 | 19.92 | 19.78 | 19.5 | 19.14 | 18.8 | 18.47 | 18.14 | 17.84 | 17.48 | 17.14 | 16.79 | 16.43 | 16.06 | 13.38 | 9.84 | 5.72
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Consumer Transformation | Headroom (MW) | Thermal | 14.56 | 14.49 | 14.34 | 14.22 | 13.97 | 13.84 | 12.09 | 8.59 | 5.89 | 3.31 | 0.55 | -2.12 | -4.75 | -7.53 | -10.62 | -24.38 | -42.44 | -61.38
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Leading the Way | Headroom (MW) | Thermal | 14.56 | 14.87 | 14.73 | 14.65 | 14.4 | 14.39 | 12.54 | 10.83 | 9.43 | 7.38 | 5.62 | 3.06 | 0.96 | -1.26 | -3.68 | -15.28 | -30.3 | -45.46
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | Steady Progression | Headroom (MW) | N/A | 14.56 | 14.54 | 14.49 | 14.5 | 14.6 | 14.72 | 14.79 | 14.76 | 14.45 | 12.84 | 12.5 | 12.08 | 11.38 | 10.87 | 10.35 | 9.46 | 8.46 | 6.86
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | System Transformation | Headroom (MW) | Thermal | 14.56 | 14.52 | 14.44 | 14.42 | 14.42 | 14.49 | 14.51 | 14.23 | 12.55 | 11.59 | 10.45 | 9.36 | 8.28 | 7.42 | 6.44 | 3.61 | -1.58 | -7.36
Coventry 132kV | Daventry | BRAUNSTON ROAD 33 11kV S STN | Primary | 11 | -1.1752 | 52.2612 | WPD Best View | Headroom (MW) | Thermal | 14.56 | 14.52 | 14.44 | 14.42 | 14.42 | 14.5 | 14.53 | 14.26 | 12.59 | 11.64 | 10.51 | 9.41 | 8.33 | 7.48 | 6.49 | 3.69 | -1.51 | -7.29
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Consumer Transformation | Headroom (MW) | Thermal | 10.73 | 10.64 | 10.57 | 8.93 | 8.76 | 8.69 | 8.53 | 8.05 | 7.49 | 6.84 | 6 | 5.03 | 3.97 | 2.97 | 1.29 | -5.61 | -7.75 | -10.27
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Leading the Way | Headroom (MW) | Thermal | 10.73 | 10.64 | 10.56 | 8.92 | 8.73 | 8.71 | 8.57 | 8.41 | 8.24 | 8.05 | 7.84 | 7.6 | 6.75 | 5.91 | 4.57 | 0.92 | -7.05 | -8.86
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | Steady Progression | Headroom (MW) | N/A | 10.73 | 10.68 | 10.66 | 9.1 | 9.09 | 9.14 | 9.12 | 9.05 | 8.98 | 8.89 | 8.76 | 8.58 | 8.14 | 7.7 | 7.08 | 6.5 | 4.4 | 3.2
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | System Transformation | Headroom (MW) | Thermal | 10.73 | 10.66 | 10.62 | 9.03 | 8.97 | 8.99 | 8.92 | 8.55 | 8.07 | 7.53 | 6.8 | 5.93 | 5 | 4.13 | 2.82 | 0.63 | -4.66 | -7.28
Coventry 132kV | Daventry | CRICK 33 11kV S STN | Primary | 11 | -1.1647 | 52.3521 | WPD Best View | Headroom (MW) | Thermal | 10.73 | 10.67 | 10.63 | 9.05 | 9.01 | 9.04 | 9 | 8.67 | 8.26 | 7.79 | 7.16 | 6.4 | 5.58 | 4.83 | 3.65 | 2.15 | -3.03 | -5.65
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Consumer Transformation | Headroom (MW) | Thermal | 16.16 | 16.07 | 15.95 | 15.78 | 15.39 | 15.08 | 14.76 | 14.31 | 13.94 | 13.44 | 12.81 | 12.1 | 11.28 | 10.5 | 9.57 | 6.73 | 3.07 | -1.09
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Leading the Way | Headroom (MW) | Thermal | 16.16 | 16.06 | 15.93 | 15.75 | 15.32 | 14.98 | 14.65 | 14.39 | 14.33 | 14.11 | 13.81 | 13.49 | 12.73 | 11.96 | 11.76 | 7.8 | 3.37 | -0.89
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | Steady Progression | Headroom (MW) | N/A | 16.16 | 16.09 | 16.06 | 16.03 | 15.98 | 15.95 | 15.89 | 15.82 | 15.83 | 15.8 | 15.72 | 15.63 | 15.37 | 15.11 | 14.76 | 14.52 | 14.6 | 13.54
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | System Transformation | Headroom (MW) | N/A | 16.16 | 16.08 | 16.04 | 15.94 | 15.77 | 15.62 | 15.45 | 15.14 | 14.92 | 14.58 | 14.11 | 13.56 | 12.95 | 12.39 | 11.71 | 10.8 | 8.62 | 6.03
Coventry 132kV | Daventry | DAVENTRY 11kV S STN | Primary | 11 | -1.1549 | 52.2596 | WPD Best View | Headroom (MW) | N/A | 16.16 | 16.08 | 16.04 | 15.94 | 15.77 | 15.62 | 15.45 | 15.14 | 14.92 | 14.58 | 14.11 | 13.56 | 12.95 | 12.39 | 11.71 | 10.8 | 8.62 | 6.03
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Consumer Transformation | Headroom (MW) | Thermal | 4.21 | 4.13 | 4.06 | 3.97 | 3.75 | 3.56 | 2.57 | 0.38 | -1.46 | -3.34 | -5.49 | -7.73 | -10.03 | -12.3 | -14.98 | -24.15 | -35 | -46.78
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Leading the Way | Headroom (MW) | Thermal | 4.21 | 4.12 | 4.06 | 3.98 | 3.75 | 3.55 | 2.47 | 1.56 | 0.85 | -0.18 | -1.05 | -1.87 | -3.62 | -5.41 | -7.35 | -15.42 | -25.36 | -33.26
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | Steady Progression | Headroom (MW) | Thermal | 4.21 | 4.16 | 4.14 | 4.11 | 4.07 | 4.04 | 4.01 | 3.86 | 3.58 | 2.62 | 2.25 | 1.79 | 0.87 | 0.06 | -0.96 | -2.39 | -3.98 | -5.69
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | System Transformation | Headroom (MW) | Thermal | 4.21 | 4.15 | 4.11 | 4.07 | 3.97 | 3.88 | 3.78 | 3.22 | 1.85 | 0.77 | -0.57 | -2.04 | -3.57 | -4.88 | -6.49 | -9.84 | -14.21 | -19.36
Coventry 132kV | Daventry | WEEDON 33 11kV S STN | Primary | 11 | -1.0811 | 52.2348 | WPD Best View | Headroom (MW) | Thermal | 4.21 | 4.14 | 4.1 | 4.05 | 3.92 | 3.8 | 3.68 | 3.27 | 2.11 | 1.27 | 0.26 | -0.81 | -2.24 | -3.48 | -4.94 | -8.6 | -13.4 | -17.91
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Consumer Transformation | Headroom (MW) | Thermal | 5.7 | 5.61 | 5.55 | 5.47 | 5.29 | 5.06 | 4.8 | 4.24 | 3.59 | 2.87 | 2.08 | 1.19 | 0.22 | -0.67 | -1.79 | -5.75 | -8.75 | -12.33
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Leading the Way | Headroom (MW) | Thermal | 5.7 | 5.61 | 5.54 | 5.45 | 5.26 | 4.95 | 4.62 | 4.27 | 3.9 | 3.51 | 3.33 | 3.14 | 2.34 | 1.57 | 0.74 | -3.31 | -7.05 | -9.25
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | Steady Progression | Headroom (MW) | N/A | 5.7 | 5.65 | 5.62 | 5.6 | 5.57 | 5.53 | 5.49 | 5.38 | 5.27 | 5.13 | 4.95 | 4.72 | 4.22 | 3.73 | 3.07 | 2.24 | 1.19 | 0.04
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | System Transformation | Headroom (MW) | Thermal | 5.7 | 5.63 | 5.59 | 5.54 | 5.46 | 5.32 | 5.16 | 4.69 | 4.11 | 3.48 | 2.76 | 1.92 | 1 | 0.19 | -0.83 | -2.99 | -5.27 | -7.98
Coventry 132kV | Daventry | WELTON 33 11kV S STN | Primary | 11 | -1.1295 | 52.305 | WPD Best View | Headroom (MW) | Thermal | 5.7 | 5.63 | 5.59 | 5.54 | 5.46 | 5.38 | 5.29 | 4.89 | 4.4 | 3.85 | 3.13 | 2.3 | 1.4 | 0.59 | -0.42 | -2.44 | -4.77 | -7.45
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Consumer Transformation | Headroom (MW) | Thermal | 1.725 | 1.645 | 1.585 | 1.505 | 1.325 | 1.185 | 1.055 | 0.235 | -0.765 | -1.935 | -3.495 | -5.315 | -7.285 | -9.075 | -11.345 | -15.865 | -20.575 | -26.435
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Leading the Way | Headroom (MW) | Thermal | 1.725 | 1.645 | 1.575 | 1.485 | 1.285 | 1.145 | 1.015 | 0.895 | 0.785 | 0.685 | 0.565 | 0.465 | -1.005 | -2.425 | -3.945 | -9.355 | -13.435 | -15.795
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | Steady Progression | Headroom (MW) | Thermal | 1.725 | 1.685 | 1.655 | 1.635 | 1.605 | 1.585 | 1.555 | 1.345 | 1.145 | 0.885 | 0.535 | 0.085 | -1.005 | -2.065 | -3.505 | -5.315 | -7.285 | -9.405
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | System Transformation | Headroom (MW) | Thermal | 1.725 | 1.665 | 1.625 | 1.575 | 1.495 | 1.435 | 1.365 | 0.605 | -0.385 | -1.505 | -3.025 | -4.805 | -6.725 | -8.445 | -10.635 | -14.265 | -18.425 | -23.575
Coventry 132kV | Daventry | WEST HADDON 33 11kV S STN | Primary | 11 | -1.0455 | 52.3547 | WPD Best View | Headroom (MW) | Thermal | 1.725 | 1.665 | 1.625 | 1.575 | 1.495 | 1.435 | 1.365 | 0.595 | -0.385 | -1.515 | -3.035 | -4.815 | -6.735 | -8.455 | -10.645 | -14.275 | -18.435 | -23.585
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Consumer Transformation | Headroom (MW) | Thermal | 6.07 | 5.96 | 5.86 | 5.76 | 5.51 | 5.27 | 5 | 4.71 | 4.45 | 4.21 | 3.92 | 3.64 | 3.36 | 3.06 | 2.73 | -0.43 | -3.31 | -6.45
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Leading the Way | Headroom (MW) | Thermal | 6.07 | 5.95 | 5.85 | 5.73 | 5.46 | 5.19 | 4.88 | 4.58 | 4.29 | 4 | 3.72 | 3.44 | 3.14 | 2.82 | 2.46 | -0.63 | -3.43 | -6.89
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | Steady Progression | Headroom (MW) | N/A | 6.07 | 6 | 5.97 | 5.94 | 5.9 | 5.86 | 5.82 | 5.78 | 5.73 | 5.66 | 5.61 | 5.56 | 5.51 | 5.47 | 5.45 | 5.42 | 5.15 | 4.72
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | System Transformation | Headroom (MW) | N/A | 6.07 | 5.98 | 5.92 | 5.86 | 5.75 | 5.63 | 5.5 | 5.37 | 5.21 | 5.09 | 4.96 | 4.85 | 4.75 | 4.67 | 4.59 | 3.62 | 2.59 | 1.56
Coventry 132kV | Daventry | WOODFORD HALSE 33 11kV S STN | Primary | 11 | -1.2078 | 52.1735 | WPD Best View | Headroom (MW) | Thermal | 6.07 | 5.97 | 5.89 | 5.8 | 5.63 | 5.47 | 5.31 | 5.15 | 4.97 | 4.83 | 4.66 | 4.51 | 4.36 | 4.21 | 4.05 | 2.63 | 1.16 | -0.58
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Consumer Transformation | Headroom (MW) | Thermal | 8.58 | 8.44 | 8.32 | 8.17 | 7.84 | 7.57 | 7.3 | 6.89 | 6.48 | 6.06 | 5.53 | 4.92 | 4.26 | 3.64 | 2.89 | 0.44 | -2.97 | -6.88
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Leading the Way | Headroom (MW) | Thermal | 8.58 | 8.43 | 8.3 | 8.15 | 7.8 | 7.51 | 7.23 | 6.97 | 6.78 | 6.59 | 6.35 | 6.11 | 5.55 | 4.95 | 4.31 | 1.31 | -2.75 | -6.83
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | Steady Progression | Headroom (MW) | N/A | 8.58 | 8.5 | 8.47 | 8.43 | 8.39 | 8.34 | 8.29 | 8.2 | 8.13 | 8.05 | 7.94 | 7.82 | 7.56 | 7.31 | 6.99 | 6.6 | 5.92 | 4.93
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | System Transformation | Headroom (MW) | Thermal | 8.58 | 8.47 | 8.4 | 8.32 | 8.19 | 8.06 | 7.93 | 7.64 | 7.34 | 7.03 | 6.6 | 6.12 | 5.62 | 5.19 | 4.63 | 3.48 | 1.41 | -0.87
Coventry 132kV | Hinckley 33 | BARWELL 33 11kV S STN | Primary | 11 | -1.3385 | 52.5827 | WPD Best View | Headroom (MW) | Thermal | 8.58 | 8.44 | 8.32 | 8.17 | 7.84 | 7.57 | 7.3 | 6.89 | 6.48 | 6.06 | 5.53 | 4.92 | 4.26 | 3.64 | 2.89 | 0.44 | -2.97 | -6.88
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Consumer Transformation | Headroom (MW) | Thermal | 5.065 | 4.935 | 4.775 | 4.585 | 4.025 | 3.555 | 3.095 | 2.395 | 1.625 | 0.775 | -0.255 | -1.385 | -2.605 | -3.795 | -5.185 | -10.555 | -16.915 | -23.225
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Leading the Way | Headroom (MW) | Thermal | 5.065 | 4.915 | 4.755 | 4.535 | 3.925 | 3.435 | 2.945 | 2.505 | 2.075 | 1.605 | 1.075 | 0.525 | -0.605 | -1.745 | -2.985 | -9.645 | -17.885 | -24.375
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | Steady Progression | Headroom (MW) | Thermal | 5.065 | 5.035 | 5.025 | 5.025 | 5.015 | 4.985 | 4.955 | 4.865 | 4.795 | 4.665 | 4.505 | 4.315 | 3.875 | 3.445 | 2.865 | 2.215 | 1.335 | -0.145
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | System Transformation | Headroom (MW) | Thermal | 5.065 | 4.985 | 4.915 | 4.835 | 4.645 | 4.475 | 4.265 | 3.815 | 3.295 | 2.685 | 1.905 | 1.015 | 0.075 | -0.795 | -1.845 | -4.665 | -8.775 | -12.395
Coventry 132kV | Hinckley 33 | MIDDLEFIELD 33 11kV S STN | Primary | 11 | -1.3744 | 52.5561 | WPD Best View | Headroom (MW) | Thermal | 5.065 | 4.935 | 4.775 | 4.585 | 4.025 | 3.555 | 3.095 | 2.395 | 1.625 | 0.775 | -0.255 | -1.385 | -2.605 | -3.795 | -5.185 | -10.555 | -16.915 | -23.225
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Consumer Transformation | Headroom (MW) | Thermal | 5.76 | 5.71 | 5.66 | 5.61 | 5.48 | 5.37 | 5.27 | 4.94 | 4.54 | 4.09 | 3.52 | 2.85 | 2.11 | 1.43 | 0.58 | -1.11 | -3.27 | -5.87
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Leading the Way | Headroom (MW) | Thermal | 5.76 | 5.7 | 5.66 | 5.6 | 5.46 | 5.35 | 5.24 | 5.15 | 5.07 | 4.99 | 4.91 | 4.82 | 4.26 | 3.72 | 3.12 | 1.16 | -1.55 | -3.14
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | Steady Progression | Headroom (MW) | N/A | 5.76 | 5.73 | 5.72 | 5.7 | 5.69 | 5.67 | 5.65 | 5.57 | 5.49 | 5.39 | 5.25 | 5.09 | 4.71 | 4.34 | 3.83 | 3.22 | 2.48 | 1.62
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | System Transformation | Headroom (MW) | Thermal | 5.76 | 5.72 | 5.69 | 5.66 | 5.61 | 5.56 | 5.51 | 5.21 | 4.85 | 4.44 | 3.9 | 3.26 | 2.57 | 1.96 | 1.19 | 0 | -1.7 | -3.74
Coventry 132kV | Nuneaton | ARLEY 33 11kV S STN | Primary | 11 | -1.5755 | 52.5021 | WPD Best View | Headroom (MW) | Thermal | 5.76 | 5.71 | 5.66 | 5.61 | 5.48 | 5.37 | 5.27 | 4.94 | 4.54 | 4.09 | 3.52 | 2.85 | 2.11 | 1.43 | 0.58 | -1.11 | -3.27 | -5.87
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Consumer Transformation | Headroom (MW) | N/A | 15.43 | 15.33 | 15.28 | 15.22 | 15.34 | 15.3 | 15.26 | 15.21 | 15.18 | 15.12 | 15.06 | 14.98 | 14.84 | 14.64 | 14.44 | 12.89 | 10.84 | 8.59
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Leading the Way | Headroom (MW) | N/A | 15.43 | 15.32 | 15.26 | 15.2 | 15.35 | 15.3 | 15.25 | 15.18 | 15.12 | 15.04 | 14.94 | 14.85 | 14.68 | 14.45 | 14.18 | 12.39 | 10.06 | 7.1
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | Steady Progression | Headroom (MW) | N/A | 15.43 | 15.35 | 15.31 | 15.26 | 15.43 | 15.4 | 15.38 | 15.35 | 15.33 | 15.31 | 15.28 | 15.25 | 15.23 | 15.18 | 15.14 | 14.93 | 14.68 | 14.39
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | System Transformation | Headroom (MW) | N/A | 15.43 | 15.34 | 15.29 | 15.24 | 15.41 | 15.38 | 15.35 | 15.31 | 15.29 | 15.26 | 15.23 | 15.18 | 15.13 | 15.07 | 15.02 | 14.74 | 14.27 | 13.18
Coventry 132kV | Nuneaton | COTON ROAD 33 11kV S STN | Primary | 11 | -1.4668 | 52.5213 | WPD Best View | Headroom (MW) | N/A | 15.43 | 15.32 | 15.26 | 15.2 | 15.35 | 15.3 | 15.25 | 15.18 | 15.12 | 15.04 | 14.94 | 14.85 | 14.68 | 14.45 | 14.18 | 12.39 | 10.06 | 7.1
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Consumer Transformation | Headroom (MW) | Thermal | 14.63 | 14.64 | 14.65 | 14.52 | 14.06 | 13.6 | 12.91 | 12 | 11.27 | 10.58 | 9.83 | 9.11 | 8.37 | 7.58 | 6.74 | 1.65 | -5.1 | -12.53
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Leading the Way | Headroom (MW) | Thermal | 14.63 | 14.64 | 14.65 | 14.52 | 14.01 | 13.46 | 12.66 | 11.93 | 11.29 | 10.57 | 9.83 | 9.11 | 8.34 | 7.5 | 6.6 | 1.2 | -5.69 | -14.19
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | Steady Progression | Headroom (MW) | N/A | 14.63 | 14.66 | 14.72 | 14.78 | 14.76 | 14.74 | 14.73 | 14.7 | 14.63 | 14.34 | 14.25 | 14.15 | 14.04 | 13.97 | 13.92 | 13.65 | 13.05 | 12.17
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | System Transformation | Headroom (MW) | N/A | 14.63 | 14.66 | 14.71 | 14.76 | 14.6 | 14.44 | 14.26 | 14.04 | 13.59 | 13.35 | 13.08 | 12.82 | 12.6 | 12.41 | 12.23 | 11.01 | 8.29 | 5.43
Coventry 132kV | Nuneaton | GIPSY LANE 33 11kV S STN | Primary | 11 | -1.4434 | 52.5013 | WPD Best View | Headroom (MW) | Thermal | 14.63 | 14.64 | 14.65 | 14.52 | 14.02 | 13.47 | 12.93 | 12.41 | 11.88 | 11.18 | 10.63 | 10.06 | 9.45 | 8.83 | 8.17 | 3.99 | -1.31 | -8.15
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Consumer Transformation | Headroom (MW) | N/A | 15.62 | 15.54 | 15.49 | 15.43 | 15.27 | 14.92 | 14.54 | 14.17 | 13.82 | 13.46 | 13.06 | 12.69 | 12.38 | 12.05 | 11.68 | 9.57 | 6.72 | 3.54
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Leading the Way | Headroom (MW) | N/A | 15.62 | 15.53 | 15.47 | 15.41 | 15.16 | 14.82 | 14.45 | 14.09 | 13.75 | 13.38 | 12.95 | 12.56 | 12.23 | 11.93 | 11.54 | 9.2 | 5.94 | 1.65
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | Steady Progression | Headroom (MW) | N/A | 15.62 | 15.56 | 15.54 | 15.51 | 15.49 | 15.51 | 15.52 | 15.53 | 15.56 | 15.58 | 15.61 | 15.63 | 15.68 | 15.73 | 15.74 | 15.73 | 15.42 | 14.96
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | System Transformation | Headroom (MW) | N/A | 15.62 | 15.55 | 15.52 | 15.48 | 15.42 | 15.45 | 15.46 | 15.35 | 15.2 | 15.04 | 14.86 | 14.69 | 14.57 | 14.46 | 14.32 | 13.74 | 12.34 | 10.92
Coventry 132kV | Nuneaton | LANGDALE DRIVE 33 11kV S STN | Primary | 11 | -1.4364 | 52.53 | WPD Best View | Headroom (MW) | N/A | 15.62 | 15.53 | 15.48 | 15.41 | 15.18 | 14.81 | 14.41 | 14.03 | 13.66 | 13.26 | 12.81 | 12.39 | 12.05 | 11.7 | 11.31 | 9.05 | 5.84 | 1.61
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Consumer Transformation | Headroom (MW) | N/A | 13.88 | 13.8 | 13.74 | 13.65 | 13.42 | 13.18 | 12.87 | 12.56 | 12.25 | 11.97 | 11.7 | 11.44 | 11.23 | 11.01 | 10.77 | 10.03 | 6.7 | 4.38
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Leading the Way | Headroom (MW) | N/A | 13.88 | 13.79 | 13.73 | 13.64 | 13.39 | 13.14 | 12.87 | 12.6 | 12.3 | 12.03 | 11.74 | 11.46 | 11.22 | 11.67 | 9.54 | 7.79 | 5.4 | 2.84
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | Steady Progression | Headroom (MW) | N/A | 13.88 | 13.81 | 13.81 | 13.82 | 13.83 | 13.8 | 13.66 | 13.5 | 13.34 | 13.19 | 13.06 | 12.94 | 12.86 | 12.79 | 12.75 | 12.64 | 12.39 | 11.89
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | System Transformation | Headroom (MW) | N/A | 13.88 | 13.8 | 13.8 | 13.78 | 13.71 | 13.6 | 13.39 | 13.19 | 13 | 12.82 | 12.66 | 12.52 | 12.43 | 12.47 | 11.15 | 10.69 | 9.65 | 8.71
Coventry 132kV | Nuneaton | NUNEATON 11kV S STN | Primary | 11 | -1.4883 | 52.5119 | WPD Best View | Headroom (MW) | N/A | 13.88 | 13.79 | 13.73 | 13.64 | 13.39 | 13.14 | 12.87 | 12.6 | 12.3 | 12.03 | 11.74 | 11.46 | 11.22 | 11.67 | 9.54 | 7.79 | 5.4 | 2.84
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Consumer Transformation | Headroom (MW) | Thermal | 12.41 | 12.25 | 12.06 | 11.56 | 11.09 | 10.68 | 10.29 | 9.92 | 9.57 | 9.23 | 8.91 | 8.59 | 8.22 | 8.4 | 4.98 | 2.09 | -1.81 | -5.49
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Leading the Way | Headroom (MW) | Thermal | 12.41 | 12.24 | 12.04 | 11.52 | 11.02 | 10.58 | 10.18 | 9.8 | 9.43 | 9.08 | 8.7 | 8.31 | 7.84 | 8.44 | 3.4 | -0.1 | -4.6 | -9.89
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | Steady Progression | Headroom (MW) | N/A | 12.41 | 12.33 | 12.29 | 12.23 | 12.16 | 12.09 | 11.98 | 11.9 | 11.83 | 11.76 | 11.69 | 11.63 | 11.58 | 11.53 | 11.49 | 11.47 | 10.9 | 10.01
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | System Transformation | Headroom (MW) | N/A | 12.41 | 12.3 | 12.19 | 12.06 | 11.86 | 11.67 | 11.46 | 11.26 | 11.08 | 10.9 | 10.74 | 10.58 | 10.42 | 10.57 | 7.46 | 6.56 | 4.65 | 2.85
Coventry 132kV | Nuneaton | WHITTLEFORD 33 11kV S STN | Primary | 11 | -1.515 | 52.5264 | WPD Best View | Headroom (MW) | Thermal | 12.41 | 12.24 | 12.04 | 11.53 | 11.03 | 10.61 | 10.2 | 9.83 | 9.47 | 9.13 | 8.77 | 8.41 | 7.97 | 8.08 | 4.56 | 1.09 | -3.33 | -8.39
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Consumer Transformation | Headroom (MW) | Thermal | 13.36 | 13.39 | 13.42 | 13.47 | 13.33 | 13.14 | 12.93 | 12.34 | 11.64 | 10.89 | 9.78 | 8.49 | 7.07 | 5.72 | 4.09 | -0.5 | -4.99 | -10.19
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Leading the Way | Headroom (MW) | Thermal | 13.36 | 13.4 | 13.43 | 13.49 | 13.34 | 13.17 | 12.96 | 12.75 | 12.5 | 12.31 | 11.93 | 11.52 | 10.34 | 9.16 | 7.88 | 2.74 | -2.7 | -6.62
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | Steady Progression | Headroom (MW) | N/A | 13.36 | 13.43 | 13.52 | 13.66 | 13.81 | 13.9 | 13.96 | 13.9 | 13.84 | 13.76 | 13.59 | 13.37 | 12.8 | 12.23 | 11.45 | 10.39 | 9.05 | 7.38
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | System Transformation | Headroom (MW) | Thermal | 13.36 | 13.42 | 13.49 | 13.61 | 13.68 | 13.67 | 13.61 | 13.18 | 12.62 | 12.03 | 11.09 | 9.97 | 8.77 | 7.67 | 6.3 | 3.49 | 0.24 | -3.52
Coventry 132kV | Pailton | LUTTERWORTH 33 11kV S STN | Primary | 11 | -1.2167 | 52.4554 | WPD Best View | Headroom (MW) | Thermal | 13.36 | 13.39 | 13.42 | 13.47 | 13.33 | 13.14 | 12.93 | 12.34 | 11.64 | 10.89 | 9.78 | 8.49 | 7.07 | 5.72 | 4.09 | -0.5 | -4.99 | -10.19
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Consumer Transformation | Headroom (MW) | Thermal | 14.3 | 14.04 | 13.51 | 13.45 | 13.35 | 13.25 | 12.19 | 9.91 | 8.18 | 6.53 | 4.63 | 2.72 | 0.77 | -1.22 | -3.51 | -11.89 | -23.4 | -35.64
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Leading the Way | Headroom (MW) | Thermal | 14.3 | 14.04 | 13.53 | 13.48 | 13.4 | 13.33 | 12.22 | 11.34 | 10.75 | 9.74 | 8.86 | 8.06 | 6.65 | 5.19 | 3.6 | -3.08 | -12.72 | -21.23
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | Steady Progression | Headroom (MW) | N/A | 14.3 | 14.04 | 14.01 | 13.51 | 13.47 | 13.44 | 13.44 | 13.39 | 13.18 | 12.11 | 11.87 | 11.56 | 10.96 | 10.5 | 9.95 | 9.41 | 8.26 | 6.98
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | System Transformation | Headroom (MW) | Thermal | 14.3 | 14.04 | 14 | 13.5 | 13.45 | 13.41 | 13.43 | 13.22 | 12.06 | 11.37 | 10.47 | 9.55 | 8.59 | 7.8 | 6.83 | 4.84 | 1.23 | -3.04
Coventry 132kV | Pailton | MAGNA PARK 33 11kV S STN | Primary | 11 | -1.2506 | 52.4492 | WPD Best View | Headroom (MW) | N/A | 14.3 | 14.04 | 13.54 | 13.51 | 13.46 | 13.42 | 13.45 | 13.42 | 13.23 | 12.18 | 11.96 | 11.67 | 11.06 | 10.59 | 10.03 | 9.44 | 8.24 | 6.91
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Consumer Transformation | Headroom (MW) | Thermal | 13.94 | 13.71 | 13.5 | 13.26 | 12.71 | 12.21 | 11.45 | 9.88 | 8.34 | 6.71 | 4.78 | 2.67 | 0.44 | -1.68 | -4.31 | -12.58 | -22.22 | -33.18
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Leading the Way | Headroom (MW) | Thermal | 13.94 | 13.69 | 13.48 | 13.23 | 12.64 | 12.1 | 11.26 | 10.51 | 9.82 | 9.03 | 8.33 | 7.64 | 5.8 | 3.96 | 2 | -6.44 | -17.06 | -25.59
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | Steady Progression | Headroom (MW) | N/A | 13.94 | 13.81 | 13.75 | 13.7 | 13.64 | 13.56 | 13.48 | 13.25 | 13 | 12.47 | 12.08 | 11.61 | 10.61 | 9.66 | 8.42 | 6.91 | 4.75 | 2.16
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | System Transformation | Headroom (MW) | Thermal | 13.94 | 13.76 | 13.64 | 13.52 | 13.31 | 13.08 | 12.81 | 11.99 | 10.77 | 9.56 | 8.06 | 6.37 | 4.58 | 3.01 | 1.06 | -2.72 | -8.22 | -14.56
Coventry 132kV | Pailton | SAPCOTE 33 11kV S STN | Primary | 11 | -1.2548 | 52.5363 | WPD Best View | Headroom (MW) | Thermal | 13.94 | 13.71 | 13.51 | 13.27 | 12.73 | 12.24 | 11.76 | 10.72 | 9.5 | 7.95 | 6.34 | 4.52 | 2.55 | 0.75 | -1.51 | -7.92 | -15.15 | -23.62
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Consumer Transformation | Headroom (MW) | Thermal | 14.43 | 14.32 | 14.24 | 14.14 | 13.91 | 13.45 | 12.74 | 11.62 | 10.62 | 9.67 | 8.49 | 7.25 | 5.95 | 4.63 | 3.11 | -2.65 | -10.22 | -18.65
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Leading the Way | Headroom (MW) | Thermal | 14.43 | 14.31 | 14.22 | 14.11 | 13.83 | 13.35 | 12.6 | 11.91 | 11.29 | 10.64 | 10 | 9.37 | 8.27 | 7.13 | 5.91 | -0.04 | -8.02 | -15.99
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | Steady Progression | Headroom (MW) | N/A | 14.43 | 14.35 | 14.31 | 14.27 | 14.22 | 14.18 | 14.14 | 14.1 | 14.02 | 13.72 | 13.62 | 13.51 | 13.09 | 12.68 | 12.17 | 11.51 | 10.31 | 8.64
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | System Transformation | Headroom (MW) | Thermal | 14.43 | 14.34 | 14.28 | 14.22 | 14.12 | 14.07 | 14.01 | 13.67 | 13.01 | 12.47 | 11.71 | 10.89 | 10.05 | 9.31 | 8.44 | 6.26 | 2.56 | -1.53
Coventry 132kV | Rugby | HILLMORTON 33 11kV S STN | Primary | 11 | -1.2204 | 52.3668 | WPD Best View | Headroom (MW) | Thermal | 14.43 | 14.35 | 14.3 | 14.25 | 14.18 | 14.13 | 13.83 | 13.27 | 12.86 | 12.23 | 11.45 | 10.64 | 9.75 | 8.86 | 7.82 | 4.9 | 0.75 | -4.16
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Consumer Transformation | Headroom (MW) | Thermal | 14.325 | 14.225 | 14.155 | 14.085 | 13.745 | 13.205 | 8.335 | 5.865 | 4.935 | 3.965 | 2.685 | 1.255 | -0.245 | -1.685 | -3.405 | -9.225 | -16.565 | -25.165
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Leading the Way | Headroom (MW) | Thermal | 14.325 | 14.215 | 14.145 | 14.055 | 9.265 | 7.015 | 6.455 | 5.865 | 5.295 | 4.755 | 4.085 | 2.445 | 1.045 | -0.335 | -1.865 | -8.865 | -16.595 | -25.135
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | Steady Progression | Headroom (MW) | N/A | 14.325 | 14.255 | 14.225 | 14.195 | 14.155 | 14.155 | 14.175 | 14.175 | 10.015 | 8.255 | 8.065 | 7.845 | 7.345 | 6.865 | 6.175 | 5.265 | 3.895 | 1.975
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | System Transformation | Headroom (MW) | Thermal | 14.325 | 14.235 | 14.195 | 14.145 | 14.065 | 14.075 | 9.675 | 7.475 | 6.745 | 6.065 | 5.165 | 4.145 | 3.035 | 2.015 | 0.735 | -1.875 | -6.515 | -11.815
Coventry 132kV | Rugby | LAWFORD 33 11kV S STN | Primary | 11 | -1.2882 | 52.3753 | WPD Best View | Headroom (MW) | N/A | 14.325 | 14.255 | 14.225 | 14.195 | 14.155 | 14.155 | 14.175 | 14.175 | 10.015 | 8.255 | 8.065 | 7.845 | 7.345 | 6.865 | 6.175 | 5.265 | 3.895 | 1.975
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Consumer Transformation | Headroom (MW) | N/A | 13.69 | 13.58 | 13.5 | 13.41 | 13.27 | 13.09 | 12.73 | 12.39 | 12.07 | 11.77 | 11.47 | 11.17 | 10.86 | 10.52 | 10.15 | 7.63 | 4.18 | 0.36
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Leading the Way | Headroom (MW) | Thermal | 13.69 | 13.57 | 13.48 | 13.38 | 13.21 | 13.01 | 12.63 | 12.28 | 11.95 | 11.64 | 11.29 | 10.94 | 10.56 | 10.14 | 9.67 | 6.59 | 2.65 | -2.56
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | Steady Progression | Headroom (MW) | N/A | 13.69 | 13.61 | 13.56 | 13.51 | 13.46 | 13.41 | 13.36 | 13.32 | 13.27 | 13.23 | 13.18 | 13.13 | 13.08 | 13.04 | 12.99 | 12.76 | 12.62 | 12.2
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | System Transformation | Headroom (MW) | N/A | 13.69 | 13.59 | 13.53 | 13.46 | 13.38 | 13.32 | 13.27 | 13.21 | 13.14 | 13.05 | 12.9 | 12.76 | 12.63 | 12.51 | 12.39 | 11.61 | 9.95 | 8.32
Coventry 132kV | Rugby | UNION STREET 33 11kV S STN | Primary | 11 | -1.2657 | 52.3689 | WPD Best View | Headroom (MW) | N/A | 13.69 | 13.61 | 13.56 | 13.51 | 13.46 | 13.41 | 13.36 | 13.32 | 13.27 | 13.23 | 13.18 | 13.13 | 13.08 | 13.04 | 12.99 | 12.76 | 12.62 | 12.2
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Consumer Transformation | Headroom (MW) | Thermal | 5.55 | 5.42 | 5.3 | 5.15 | 4.82 | 4.4 | 3.64 | 2.66 | 1.87 | 1.14 | 0.5 | -0.12 | -0.73 | -1.38 | -0.99 | -4.93 | -9.02 | -16.3
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Leading the Way | Headroom (MW) | Thermal | 5.55 | 5.4 | 5.28 | 5.13 | 4.77 | 4.24 | 3.41 | 2.75 | 2.18 | 1.61 | 1.06 | 0.53 | -0.04 | -0.66 | 0 | -3.62 | -6.46 | -28.4
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | Steady Progression | Headroom (MW) | N/A | 5.55 | 5.47 | 5.44 | 5.41 | 5.36 | 5.31 | 5.18 | 5.15 | 5.05 | 4.7 | 4.61 | 4.51 | 4.4 | 4.32 | 4.3 | 4.26 | 3.79 | 3.08
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | System Transformation | Headroom (MW) | Thermal | 5.55 | 5.45 | 5.38 | 5.3 | 5.17 | 5.03 | 4.85 | 4.67 | 4.16 | 3.94 | 3.7 | 3.48 | 3.28 | 3.13 | 3.15 | 2.98 | 6.8 | -5.39
Coventry 132kV | Rugby 132 11 | RUGBY 11kV S STN | Primary | 11 | -1.2626 | 52.3884 | WPD Best View | Headroom (MW) | Thermal | 5.55 | 5.47 | 5.43 | 5.39 | 5.33 | 5.24 | 4.75 | 4.06 | 3.54 | 3.06 | 2.56 | 2.11 | 1.67 | 1.2 | 0.73 | -1.95 | -5.32 | -9.16
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Consumer Transformation | Headroom (MW) | N/A | 15.95 | 15.83 | 15.75 | 15.66 | 15.5 | 15.4 | 15.15 | 14.85 | 14.59 | 14.35 | 14.13 | 13.92 | 13.69 | 13.45 | 13.17 | 10.79 | 7.63 | 4.04
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Leading the Way | Headroom (MW) | N/A | 15.95 | 15.82 | 15.73 | 15.63 | 15.41 | 15.3 | 15.02 | 14.7 | 14.42 | 14.16 | 13.89 | 13.62 | 13.33 | 12.99 | 12.6 | 9.81 | 6.1 | 1.22
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | Steady Progression | Headroom (MW) | N/A | 15.95 | 15.86 | 15.81 | 15.76 | 15.7 | 15.65 | 15.61 | 15.56 | 15.51 | 15.47 | 15.42 | 15.36 | 15.31 | 15.26 | 15.21 | 14.98 | 14.62 | 14.22
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | System Transformation | Headroom (MW) | N/A | 15.95 | 15.85 | 15.78 | 15.72 | 15.61 | 15.55 | 15.48 | 15.41 | 15.35 | 15.27 | 15.2 | 15.13 | 15.06 | 14.99 | 14.92 | 14.18 | 12.71 | 11.29
Coventry 132kV | Whitley | COPSEWOOD 33 11kV S STN | Primary | 11 | -1.4642 | 52.403 | WPD Best View | Headroom (MW) | N/A | 15.95 | 15.84 | 15.76 | 15.68 | 15.52 | 15.43 | 15.31 | 15.04 | 14.8 | 14.59 | 14.39 | 14.2 | 14 | 13.79 | 13.55 | 11.45 | 8.69 | 5.47
Berkswell 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Consumer Transformation | Headroom (MW) | Thermal | 13.7 | 13.58 | 13.5 | 13.4 | 13.24 | 13.09 | 12.81 | 12.4 | 12.01 | 11.65 | 11.26 | 10.86 | 10.46 | 10.03 | 9.55 | 6.03 | 1.11 | -4.57
Berkswell 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Leading the Way | Headroom (MW) | Thermal | 13.7 | 13.57 | 13.48 | 13.37 | 13.17 | 12.97 | 12.63 | 12.15 | 11.68 | 11.26 | 10.75 | 10.24 | 9.7 | 9.11 | 8.43 | 4.02 | -1.73 | -9.29
Berkswell 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | Steady Progression | Headroom (MW) | N/A | 13.7 | 13.61 | 13.57 | 13.53 | 13.48 | 13.46 | 13.45 | 13.41 | 13.37 | 13.33 | 13.29 | 13.25 | 13.2 | 13.16 | 13.12 | 12.91 | 12.54 | 12.04
Berkswell 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | System Transformation | Headroom (MW) | N/A | 13.7 | 13.6 | 13.53 | 13.47 | 13.38 | 13.37 | 13.36 | 13.27 | 13.14 | 13.07 | 12.98 | 12.9 | 12.81 | 12.72 | 12.63 | 11.64 | 9.27 | 6.91
Berkswell 132kV | Whitley | DILLOTFORD AVE 33 11kV S STN | Primary | 11 | -1.5066 | 52.3885 | WPD Best View | Headroom (MW) | Thermal | 13.7 | 13.58 | 13.5 | 13.4 | 13.24 | 13.09 | 12.81 | 12.4 | 12.01 | 11.65 | 11.26 | 10.86 | 10.46 | 10.03 | 9.55 | 6.03 | 1.11 | -4.57
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Consumer Transformation | Headroom (MW) | N/A | 14.26 | 14.18 | 14.14 | 14.1 | 14.01 | 13.96 | 13.91 | 13.85 | 13.79 | 13.73 | 13.67 | 13.62 | 13.51 | 13.38 | 13.24 | 12.23 | 10.88 | 9.4
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Leading the Way | Headroom (MW) | N/A | 14.26 | 14.18 | 14.14 | 14.09 | 13.96 | 13.92 | 13.87 | 13.81 | 13.75 | 13.69 | 13.63 | 13.56 | 13.43 | 13.28 | 13.11 | 11.96 | 10.55 | 8.66
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | Steady Progression | Headroom (MW) | N/A | 14.26 | 14.2 | 14.16 | 14.13 | 14.09 | 14.06 | 14.01 | 13.95 | 13.9 | 13.85 | 13.8 | 13.76 | 13.72 | 13.68 | 13.65 | 13.5 | 13.33 | 13.13
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | System Transformation | Headroom (MW) | N/A | 14.26 | 14.19 | 14.15 | 14.12 | 14.05 | 14.02 | 13.97 | 13.92 | 13.87 | 13.83 | 13.79 | 13.75 | 13.71 | 13.67 | 13.63 | 13.44 | 13.14 | 12.44
Coventry 132kV | Whitley | GULSON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.491 | 52.4077 | WPD Best View | Headroom (MW) | N/A | 14.26 | 14.18 | 14.14 | 14.1 | 14.01 | 13.96 | 13.91 | 13.85 | 13.79 | 13.73 | 13.67 | 13.62 | 13.51 | 13.38 | 13.24 | 12.23 | 10.88 | 9.4
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Consumer Transformation | Headroom (MW) | N/A | 12.82 | 12.8 | 12.79 | 12.78 | 12.72 | 12.66 | 12.57 | 12.48 | 12.38 | 12.28 | 12.21 | 12.15 | 12.09 | 12.03 | 11.97 | 11.55 | 11.19 | 10.8
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Leading the Way | Headroom (MW) | N/A | 12.82 | 12.8 | 12.79 | 12.78 | 12.71 | 12.63 | 12.53 | 12.42 | 12.29 | 12.16 | 12.1 | 12.04 | 11.97 | 11.91 | 11.85 | 11.48 | 11.07 | 10.58
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | Steady Progression | Headroom (MW) | N/A | 12.82 | 12.8 | 12.8 | 12.79 | 12.77 | 12.76 | 12.75 | 12.74 | 12.73 | 12.72 | 12.71 | 12.7 | 12.69 | 12.68 | 12.66 | 12.6 | 12.51 | 12.43
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | System Transformation | Headroom (MW) | N/A | 12.82 | 12.8 | 12.8 | 12.78 | 12.76 | 12.74 | 12.69 | 12.63 | 12.57 | 12.51 | 12.46 | 12.42 | 12.39 | 12.35 | 12.32 | 12.17 | 11.98 | 11.78
Coventry 132kV | Whitley | LONDON ROAD 33 6 6kV S STN | Primary | 6.6 | -1.5015 | 52.4032 | WPD Best View | Headroom (MW) | N/A | 12.82 | 12.8 | 12.79 | 12.78 | 12.72 | 12.66 | 12.57 | 12.48 | 12.38 | 12.28 | 12.21 | 12.15 | 12.09 | 12.03 | 11.97 | 11.55 | 11.19 | 10.8
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Consumer Transformation | Headroom (MW) | N/A | 10.54 | 10.97 | 11.44 | 11.74 | 12.13 | 12.39 | 12.43 | 12.34 | 12.35 | 12.39 | 12.43 | 12.48 | 12.42 | 12.34 | 12.24 | 11.24 | 9.13 | 6.25
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Leading the Way | Headroom (MW) | N/A | 10.54 | 11.03 | 11.52 | 11.89 | 12.33 | 12.66 | 12.72 | 12.82 | 12.97 | 13.07 | 13.22 | 13.4 | 13.35 | 13.29 | 13.21 | 12.51 | 10.28 | 7.56
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | Steady Progression | Headroom (MW) | N/A | 10.54 | 10.8374 | 10.8364 | 10.8355 | 10.8346 | 10.8297 | 10.8242 | 10.8181 | 10.7893 | 10.6448 | 10.6156 | 10.5807 | 10.5349 | 10.5074 | 10.4869 | 10.4372 | 10.3484 | 10.5888
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | System Transformation | Headroom (MW) | N/A | 10.54 | 10.98 | 11.45 | 11.76 | 12.17 | 12.44 | 12.65 | 12.85 | 12.94 | 13.13 | 13.32 | 13.52 | 13.63 | 13.75 | 13.85 | 14.29 | 13.88 | 13.08
Coventry 132kV | Whitley | RYTON 33 11kV S STN | Primary | 11 | -1.4483 | 52.3675 | WPD Best View | Headroom (MW) | N/A | 10.54 | 10.93 | 11.37 | 11.64 | 12.02 | 12.29 | 12.5 | 12.71 | 12.89 | 12.95 | 13.15 | 13.36 | 13.49 | 13.61 | 13.74 | 14.43 | 14.28 | 13.75
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Consumer Transformation | Headroom (MW) | N/A | 18.02 | 17.89 | 17.83 | 17.84 | 17.97 | 18.09 | 18.13 | 18.15 | 18.04 | 18.02 | 17.97 | 17.9 | 17.79 | 17.62 | 17.44 | 15.68 | 12.69 | 9.28
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Leading the Way | Headroom (MW) | N/A | 18.02 | 17.88 | 17.81 | 17.84 | 17.98 | 18.2 | 18.25 | 18.31 | 18.22 | 18.23 | 18.16 | 18.09 | 17.92 | 17.66 | 17.34 | 14.98 | 17.62 | 13.03
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | Steady Progression | Headroom (MW) | N/A | 18.02 | 17.92 | 17.87 | 17.9 | 18.09 | 18.2 | 18.24 | 18.28 | 18.34 | 18.44 | 18.52 | 18.6 | 18.68 | 18.71 | 18.73 | 18.82 | 18.45 | 17.95
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | System Transformation | Headroom (MW) | N/A | 18.02 | 17.91 | 17.85 | 17.88 | 18.07 | 18.21 | 18.27 | 18.33 | 18.41 | 18.57 | 18.66 | 18.74 | 18.78 | 18.79 | 18.79 | 18.72 | 17.31 | 15.65
Coventry 132kV | Whitley | WHITLEY 11kV S STN | Primary | 11 | -1.4832 | 52.3933 | WPD Best View | Headroom (MW) | N/A | 18.02 | 17.89 | 17.83 | 17.84 | 17.97 | 18.09 | 18.13 | 18.15 | 18.04 | 18.02 | 17.97 | 17.9 | 17.79 | 17.62 | 17.44 | 15.68 | 12.69 | 9.28
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Consumer Transformation | Headroom (MW) | N/A | 41.02 | 40.67 | 40.41 | 40.07 | 39.15 | 38.44 | 37.72 | 36.88 | 36.04 | 35.18 | 34.2 | 33.24 | 32.24 | 31.25 | 30.13 | 24.33 | 16.85 | 8.4
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Leading the Way | Headroom (MW) | N/A | 41.02 | 40.63 | 40.37 | 40.01 | 38.96 | 38.2 | 37.45 | 36.74 | 36.05 | 35.34 | 34.53 | 33.83 | 32.82 | 31.75 | 30.59 | 23.81 | 15.04 | 4.43
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | Steady Progression | Headroom (MW) | N/A | 41.02 | 40.84 | 40.8 | 40.76 | 40.66 | 40.56 | 40.47 | 40.34 | 40.22 | 40.08 | 39.93 | 39.79 | 39.54 | 39.31 | 39.03 | 38.61 | 37.55 | 35.76
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | System Transformation | Headroom (MW) | N/A | 41.02 | 40.76 | 40.63 | 40.47 | 40.1 | 39.8 | 39.46 | 38.99 | 38.45 | 37.9 | 37.32 | 36.76 | 36.16 | 35.59 | 34.93 | 32.91 | 29.04 | 24.94
Drakelow 132kV | Burton 132 11 (GT1A2) | Burton 11kV | Primary | 11 | -1.6235 | 52.8163 | WPD Best View | Headroom (MW) | N/A | 41.02 | 40.76 | 40.63 | 40.46 | 40.08 | 39.78 | 39.43 | 38.95 | 38.41 | 37.86 | 37.27 | 36.7 | 36.09 | 35.51 | 34.85 | 32.77 | 28.84 | 24.66
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Consumer Transformation | Headroom (MW) | Thermal | 8.87 | 8.7 | 8.44 | 8.26 | 7.87 | 7.52 | 7.19 | 6.85 | 6.51 | 6.19 | 5.79 | 5.36 | 4.88 | 4.41 | 3.87 | 1.13 | -2.58 | -6.81
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Leading the Way | Headroom (MW) | Thermal | 8.87 | 8.69 | 8.42 | 8.22 | 7.81 | 7.43 | 7.06 | 6.71 | 6.37 | 6.03 | 5.74 | 5.44 | 4.95 | 4.43 | 3.85 | 0.61 | -3.78 | -8.76
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | Steady Progression | Headroom (MW) | N/A | 8.87 | 8.78 | 8.73 | 8.68 | 8.64 | 8.58 | 8.52 | 8.45 | 8.39 | 8.32 | 8.24 | 8.15 | 8.01 | 7.88 | 7.72 | 7.53 | 6.8 | 5.9
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | System Transformation | Headroom (MW) | N/A | 8.87 | 8.74 | 8.65 | 8.44 | 8.29 | 8.13 | 7.95 | 7.76 | 7.56 | 7.37 | 7.1 | 6.82 | 6.52 | 6.26 | 5.94 | 4.97 | 2.92 | 0.76
Drakelow 132kV | Burton 33 | BRETBY 33 11kV S STN | Primary | 11 | -1.5749 | 52.7931 | WPD Best View | Headroom (MW) | Thermal | 8.87 | 8.7 | 8.45 | 8.28 | 7.92 | 7.6 | 7.28 | 6.96 | 6.64 | 6.32 | 5.94 | 5.53 | 5.08 | 4.62 | 4.1 | 1.58 | -1.91 | -5.86
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Consumer Transformation | Headroom (MW) | Thermal | 25.31 | 25.26 | 25.25 | 25.2 | 24.87 | 24.42 | 24 | 23.17 | 22.26 | 21.28 | 20.06 | 18.67 | 17.2 | 15.82 | 14.15 | 9.78 | 3.89 | -2.99
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Leading the Way | Headroom (MW) | Thermal | 25.31 | 25.25 | 25.23 | 24.94 | 24.36 | 23.9 | 23.46 | 23.07 | 22.69 | 22.34 | 21.95 | 16.73 | 15.52 | 14.31 | 13.01 | 7.85 | 0.72 | -5.16
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | Steady Progression | Headroom (MW) | N/A | 25.31 | 25.36 | 25.49 | 25.62 | 25.73 | 19.37 | 19.47 | 19.24 | 19.03 | 18.77 | 18.47 | 18.11 | 17.4 | 16.7 | 15.79 | 14.55 | 12.92 | 10.86
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | System Transformation | Headroom (MW) | Thermal | 25.31 | 25.32 | 25.39 | 25.44 | 25.41 | 25.19 | 18.49 | 17.83 | 17.07 | 16.23 | 15.15 | 13.91 | 12.6 | 11.43 | 10 | 7.52 | 3.51 | -1.18
Drakelow 132kV | Burton 33 | HATTON 33 11kV S STN | Primary | 11 | -1.6816 | 52.8638 | WPD Best View | Headroom (MW) | Thermal | 25.31 | 25.28 | 25.29 | 25.27 | 25.04 | 24.66 | 24.3 | 23.53 | 22.68 | 21.75 | 20.57 | 19.23 | 17.81 | 16.5 | 14.91 | 11.18 | 5.91 | -0.25
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Consumer Transformation | Headroom (MW) | Thermal | 5.56 | 5.52 | 5.47 | 5.42 | 5.31 | 5.1 | 4.89 | 4.54 | 4.14 | 3.71 | 3.16 | 2.56 | 1.91 | 1.29 | 0.57 | -1.78 | -4.83 | -8.48
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Leading the Way | Headroom (MW) | Thermal | 5.56 | 5.51 | 5.47 | 5.42 | 5.3 | 5 | 4.71 | 4.44 | 4.15 | 3.88 | 3.57 | 3.26 | 2.65 | 2.05 | 1.4 | -1.42 | -5.05 | -8.41
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | Steady Progression | Headroom (MW) | N/A | 5.56 | 5.54 | 5.53 | 5.51 | 5.5 | 5.48 | 5.46 | 5.4 | 5.34 | 5.27 | 5.17 | 5.06 | 4.81 | 4.57 | 4.25 | 3.83 | 3.31 | 2.69
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | System Transformation | Headroom (MW) | Thermal | 5.56 | 5.53 | 5.5 | 5.48 | 5.43 | 5.39 | 5.34 | 5.09 | 4.74 | 4.45 | 4.06 | 3.61 | 3.13 | 2.7 | 2.18 | 1.19 | -0.78 | -3.11
Drakelow 132kV | Burton 33 | TRENT ALLOYS 33 11kV S STN | Primary | 11 | -1.5644 | 52.8502 | WPD Best View | Headroom (MW) | Thermal | 5.56 | 5.52 | 5.47 | 5.42 | 5.31 | 5.1 | 4.89 | 4.54 | 4.14 | 3.71 | 3.16 | 2.56 | 1.91 | 1.29 | 0.57 | -1.78 | -4.83 | -8.48
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Consumer Transformation | Headroom (MW) | Thermal | 11.33 | 11.25 | 11.19 | 11.1 | 10.8 | 10.46 | 10.14 | 9.82 | 9.52 | 9.24 | 8.99 | 8.76 | 8.5 | 8.2 | 7.9 | 5.78 | 2.09 | -0.84
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Leading the Way | Headroom (MW) | Thermal | 11.33 | 11.24 | 11.17 | 10.99 | 10.58 | 10.22 | 9.87 | 9.53 | 9.2 | 8.87 | 8.6 | 8.33 | 8.01 | 7.66 | 7.28 | 4.84 | -0.24 | -4.16
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | Steady Progression | Headroom (MW) | N/A | 11.33 | 11.31 | 11.34 | 11.37 | 11.39 | 11.4 | 11.4 | 11.33 | 11.26 | 11.18 | 11.11 | 11.05 | 11 | 10.96 | 10.92 | 10.85 | 10.47 | 9.81
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | System Transformation | Headroom (MW) | N/A | 11.33 | 11.28 | 11.28 | 11.26 | 11.17 | 11 | 10.82 | 10.64 | 10.47 | 10.3 | 10.17 | 10.05 | 9.93 | 9.83 | 9.74 | 9.08 | 6.72 | 5.4
Drakelow 132kV | Burton 33 | WOODVILLE 33/11kV | Primary | 11 | -1.5316 | 52.7737 | WPD Best View | Headroom (MW) | Thermal | 11.33 | 11.25 | 11.19 | 11.1 | 10.8 | 10.46 | 10.14 | 9.82 | 9.52 | 9.24 | 8.99 | 8.76 | 8.5 | 8.2 | 7.9 | 5.78 | 2.09 | -0.84
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Consumer Transformation | Headroom (MW) | Thermal | 12.51 | 12.41 | 12.34 | 12.32 | 12.15 | 12.01 | 11.88 | 11.44 | 10.92 | 10.34 | 9.64 | 8.85 | 7.99 | 7.21 | 6.24 | 3.9 | 1.42 | -1.55
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Leading the Way | Headroom (MW) | N/A | 12.51 | 12.41 | 12.33 | 12.33 | 12.15 | 12 | 11.86 | 11.73 | 11.61 | 11.49 | 11.37 | 11.26 | 10.59 | 9.94 | 9.23 | 6.26 | 3.17 | 1.24
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | Steady Progression | Headroom (MW) | N/A | 12.51 | 12.44 | 12.41 | 12.44 | 12.4 | 12.36 | 12.33 | 12.21 | 12.1 | 11.96 | 11.79 | 11.59 | 11.13 | 10.68 | 10.09 | 9.31 | 8.45 | 7.43
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | System Transformation | Headroom (MW) | N/A | 12.51 | 12.43 | 12.38 | 12.39 | 12.32 | 12.25 | 12.17 | 11.78 | 11.3 | 10.76 | 10.11 | 9.37 | 8.56 | 7.84 | 6.95 | 5.24 | 3.29 | 1
Drakelow 132kV | Burton South | BARTON UNDER NEEDWOOD 33 11kV S STN | Primary | 11 | -1.7045 | 52.7582 | WPD Best View | Headroom (MW) | N/A | 12.51 | 12.43 | 12.38 | 12.39 | 12.3 | 12.22 | 12.14 | 11.74 | 11.25 | 10.7 | 10.05 | 9.3 | 8.49 | 7.77 | 6.86 | 5.08 | 3.06 | 0.68
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Consumer Transformation | Headroom (MW) | N/A | 15.21 | 15.12 | 15.08 | 15.03 | 14.97 | 14.91 | 14.82 | 14.64 | 14.47 | 14.28 | 14.09 | 13.95 | 13.8 | 13.64 | 13.48 | 12.38 | 11.32 | 10.21
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Leading the Way | Headroom (MW) | N/A | 15.21 | 15.12 | 15.07 | 15.02 | 14.94 | 14.88 | 14.76 | 14.57 | 14.36 | 14.13 | 13.92 | 13.76 | 13.59 | 13.42 | 13.23 | 12.2 | 11.04 | 9.74
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | Steady Progression | Headroom (MW) | N/A | 15.21 | 15.13 | 15.09 | 15.05 | 15.02 | 14.98 | 14.95 | 14.91 | 14.88 | 14.84 | 14.81 | 14.77 | 14.74 | 14.7 | 14.66 | 14.47 | 14.23 | 14.03
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | System Transformation | Headroom (MW) | N/A | 15.21 | 15.13 | 15.08 | 15.04 | 15 | 14.95 | 14.9 | 14.86 | 14.81 | 14.73 | 14.62 | 14.53 | 14.44 | 14.36 | 14.29 | 13.89 | 13.34 | 12.76
Drakelow 132kV | Burton South | STATION STREET 33 11kV S STN | Primary | 11 | -1.6321 | 52.8042 | WPD Best View | Headroom (MW) | N/A | 15.21 | 15.13 | 15.08 | 15.04 | 15 | 14.95 | 14.9 | 14.86 | 14.81 | 14.73 | 14.62 | 14.53 | 14.44 | 14.36 | 14.29 | 13.89 | 13.34 | 12.76
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Consumer Transformation | Headroom (MW) | N/A | 25.55 | 25.58 | 25.57 | 25.53 | 25.64 | 25.77 | 25.76 | 25.39 | 24.94 | 24.36 | 23.6 | 22.87 | 22.1 | 21.39 | 20.51 | 18.98 | 15.33 | 10.73
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Leading the Way | Headroom (MW) | N/A | 25.55 | 25.59 | 25.6 | 25.58 | 25.76 | 26.06 | 26.14 | 26.12 | 26.08 | 25.96 | 25.71 | 25.71 | 25.13 | 24.59 | 24.04 | 22.39 | 17.91 | 14.02
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | Steady Progression | Headroom (MW) | N/A | 25.55 | 25.61 | 25.67 | 25.72 | 26.07 | 26.3 | 26.46 | 26.6 | 26.74 | 26.82 | 26.86 | 26.88 | 26.72 | 26.55 | 26.24 | 27.08 | 25.93 | 24.25
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | System Transformation | Headroom (MW) | N/A | 25.55 | 25.61 | 25.65 | 25.68 | 25.99 | 26.26 | 26.42 | 26.22 | 25.94 | 25.56 | 25.01 | 24.43 | 23.81 | 23.27 | 22.58 | 22.31 | 19.7 | 16.42
Drakelow 132kV | Burton South | WELLINGTON ST 33 11kV S STN | Primary | 11 | -1.6527 | 52.8023 | WPD Best View | Headroom (MW) | N/A | 25.55 | 25.61 | 25.65 | 25.68 | 25.99 | 26.26 | 26.42 | 26.23 | 25.95 | 25.58 | 25.02 | 24.45 | 23.83 | 23.29 | 22.6 | 22.33 | 19.72 | 16.44
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Consumer Transformation | Headroom (MW) | Thermal | 11.15 | 11.05 | 10.98 | 11.24 | 11.04 | 10.86 | 10.2 | 8.99 | 8.22 | 7.37 | 6.42 | 5.51 | 4.61 | 3.63 | 2.63 | -2.78 | -9.6 | -16.14
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Leading the Way | Headroom (MW) | Thermal | 11.15 | 11.04 | 10.98 | 11.35 | 11.15 | 10.97 | 10.27 | 9.63 | 9.32 | 8.54 | 7.8 | 7.09 | 6.33 | 5.5 | 4.69 | -0.27 | -6.49 | -12.18
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | Steady Progression | Headroom (MW) | N/A | 11.15 | 11.07 | 11.06 | 11.34 | 11.33 | 11.3 | 11.33 | 11.33 | 11.32 | 10.79 | 10.71 | 10.6 | 10.42 | 10.3 | 10.22 | 10.02 | 9.6 | 9.01
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | System Transformation | Headroom (MW) | N/A | 11.15 | 11.06 | 11.03 | 11.34 | 11.27 | 11.2 | 11.19 | 11.14 | 10.76 | 10.49 | 10.15 | 9.83 | 9.52 | 9.27 | 9.05 | 7.55 | 5.32 | 3.48
Drakelow 132kV | Gresley | ASHBY 33 11kV S STN | Primary | 11 | -1.4809 | 52.7584 | WPD Best View | Headroom (MW) | Thermal | 11.15 | 11.05 | 10.98 | 11.24 | 11.04 | 10.86 | 10.2 | 8.99 | 8.22 | 7.37 | 6.42 | 5.51 | 4.61 | 3.63 | 2.63 | -2.78 | -9.6 | -16.14
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Consumer Transformation | Headroom (MW) | Thermal | 23.87 | 23.81 | 23.69 | 23.61 | 23.29 | 22.79 | 22.32 | 21.55 | 20.65 | 19.71 | 18.58 | 17.32 | 15.95 | 14.64 | 13.12 | 7.17 | 0.97 | -6.19
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Leading the Way | Headroom (MW) | Thermal | 23.87 | 23.79 | 23.67 | 23.42 | 22.91 | 22.34 | 21.8 | 21.27 | 20.67 | 20.1 | 19.5 | 18.85 | 17.57 | 16.29 | 14.95 | 7.49 | 0.16 | -6.87
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | Steady Progression | Headroom (MW) | N/A | 23.87 | 23.9 | 23.99 | 24.07 | 24.16 | 24.21 | 24.25 | 24.08 | 23.91 | 23.71 | 23.47 | 23.2 | 22.66 | 22.13 | 21.45 | 20.45 | 19.2 | 17.5
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | System Transformation | Headroom (MW) | N/A | 23.87 | 23.86 | 23.89 | 23.83 | 23.79 | 23.59 | 23.38 | 22.82 | 22.1 | 21.41 | 20.54 | 19.55 | 18.52 | 17.59 | 16.47 | 13.18 | 9.25 | 4.83
Drakelow 132kV | Gresley | GRESLEY 11kV S STN | Primary | 11 | -1.5895 | 52.7583 | WPD Best View | Headroom (MW) | Thermal | 23.87 | 23.82 | 23.71 | 23.64 | 23.36 | 22.89 | 22.44 | 21.69 | 20.81 | 19.89 | 18.78 | 17.55 | 16.22 | 14.93 | 13.45 | 7.79 | 1.9 | -4.88
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Consumer Transformation | Headroom (MW) | Thermal | -3.58 | -3.69 | -3.77 | -3.87 | -4.1 | -4.32 | -4.55 | -4.8 | -5.07 | -5.34 | -5.69 | -6.07 | -6.48 | -6.88 | -7.34 | -9.34 | -11.91 | -13.84
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Leading the Way | Headroom (MW) | Thermal | -3.58 | -3.7 | -3.79 | -3.89 | -4.13 | -4.39 | -4.65 | -4.92 | -5.2 | -5.49 | -5.71 | -5.94 | -6.37 | -6.79 | -7.21 | -9.18 | -11.03 | -16.43
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | Steady Progression | Headroom (MW) | Thermal | -3.58 | -3.65 | -3.68 | -3.72 | -3.76 | -3.8 | -3.85 | -3.9 | -3.95 | -4 | -4.09 | -4.18 | -4.34 | -4.5 | -4.69 | -4.88 | -5.47 | -6.13
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | System Transformation | Headroom (MW) | Thermal | -3.58 | -3.67 | -3.72 | -3.78 | -3.88 | -4 | -4.14 | -4.3 | -4.47 | -4.65 | -4.92 | -5.22 | -5.53 | -5.8 | -6.12 | -6.91 | -6.96 | -10.47
Drakelow 132kV | Gresley | MOIRA 33 11kV S STN | Primary | 11 | -1.5531 | 52.7408 | WPD Best View | Headroom (MW) | Thermal | -3.58 | -3.69 | -3.77 | -3.87 | -4.1 | -4.29 | -4.47 | -4.68 | -4.89 | -5.1 | -5.44 | -5.8 | -6.19 | -6.57 | -7.01 | -8.49 | -11 | -12.74
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Consumer Transformation | Headroom (MW) | Thermal | 7.02 | 6.84 | 6.68 | 6.49 | 6.23 | 5.88 | 5.56 | 5.25 | 5.13 | 4.9 | 4.67 | 4.44 | 4.21 | 3.93 | 3.61 | 1.06 | -3.57 | -7.07
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Leading the Way | Headroom (MW) | Thermal | 7.02 | 6.83 | 6.66 | 6.45 | 6.21 | 5.84 | 5.49 | 5.15 | 5.1 | 4.84 | 4.56 | 4.29 | 3.97 | 3.59 | 3.17 | 0.12 | -6.02 | -10.78
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | Steady Progression | Headroom (MW) | N/A | 7.02 | 6.92 | 6.87 | 6.83 | 6.91 | 6.86 | 6.8 | 6.75 | 6.8 | 6.76 | 6.74 | 6.72 | 6.72 | 6.71 | 6.72 | 6.88 | 6.49 | 5.72
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | System Transformation | Headroom (MW) | N/A | 7.02 | 6.89 | 6.79 | 6.68 | 6.68 | 6.53 | 6.35 | 6.19 | 6.22 | 6.1 | 6 | 5.9 | 5.81 | 5.74 | 5.68 | 4.99 | 2.2 | 0.68
Drakelow 132kV | Gresley | WILLESLEY 33 11kV S STN | Primary | 11 | -1.4998 | 52.733 | WPD Best View | Headroom (MW) | Thermal | 7.02 | 6.84 | 6.68 | 6.49 | 6.23 | 5.88 | 5.56 | 5.25 | 5.13 | 4.9 | 4.67 | 4.44 | 4.21 | 3.93 | 3.61 | 1.06 | -3.57 | -7.07
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Consumer Transformation | Headroom (MW) | N/A | 19.38 | 19.19 | 19.07 | 19.05 | 18.82 | 18.69 | 18.13 | 17.61 | 17.47 | 17.31 | 16.99 | 16.66 | 16.31 | 15.95 | 15.55 | 12.73 | 9.65 | 6.01
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Leading the Way | Headroom (MW) | N/A | 19.38 | 19.17 | 19.05 | 19.04 | 18.73 | 18.58 | 18.43 | 18.26 | 18.07 | 17.84 | 17.46 | 17.06 | 16.64 | 16.17 | 16.09 | 12.72 | 14.95 | 0.17
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | Steady Progression | Headroom (MW) | N/A | 19.38 | 19.22 | 19.14 | 19.14 | 19.03 | 18.96 | 18.27 | 17.59 | 16.92 | 16.3 | 15.74 | 15.26 | 14.99 | 14.9 | 14.82 | 14.44 | 14.57 | 14.02
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | System Transformation | Headroom (MW) | N/A | 19.38 | 19.2 | 19.1 | 19.11 | 18.95 | 18.85 | 18.32 | 17.83 | 17.73 | 17.63 | 17.53 | 17.44 | 17.33 | 17.23 | 17.12 | 16.66 | 21.36 | 13.25
East Claydon 132kV | Bletchley | BLETCHLEY 11kV S STN | Primary | 11 | -0.7443 | 52.0115 | WPD Best View | Headroom (MW) | N/A | 19.38 | 19.17 | 19.05 | 19.04 | 18.73 | 18.58 | 18.43 | 18.26 | 18.07 | 17.84 | 17.46 | 17.06 | 16.64 | 16.17 | 16.09 | 12.72 | 14.95 | 0.17
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Consumer Transformation | Headroom (MW) | N/A | 12.78 | 12.73 | 12.7 | 12.66 | 12.63 | 12.6 | 12.57 | 12.54 | 12.51 | 12.48 | 12.45 | 12.42 | 12.39 | 12.36 | 12.34 | 12.19 | 12.06 | 11.93
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Leading the Way | Headroom (MW) | N/A | 12.78 | 12.73 | 12.69 | 12.66 | 12.62 | 12.59 | 12.56 | 12.53 | 12.5 | 12.47 | 12.44 | 11.27 | 11.23 | 11.19 | 11.15 | 10.95 | 10.75 | 10.55
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | Steady Progression | Headroom (MW) | N/A | 12.78 | 12.73 | 12.7 | 12.67 | 12.63 | 12.6 | 12.57 | 12.54 | 12.51 | 12.48 | 12.46 | 12.43 | 12.4 | 12.37 | 12.34 | 12.21 | 12.09 | 11.97
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | System Transformation | Headroom (MW) | N/A | 12.78 | 12.73 | 12.7 | 12.66 | 12.63 | 12.6 | 12.57 | 12.54 | 12.51 | 12.48 | 12.45 | 12.42 | 12.4 | 12.37 | 12.34 | 12.21 | 12.08 | 11.96
East Claydon 132kV | Bletchley | FEN FARM 33 11kV S STN | Primary | 11 | -0.6772 | 52.0345 | WPD Best View | Headroom (MW) | N/A | 12.78 | 12.73 | 12.69 | 12.66 | 12.62 | 12.59 | 12.56 | 12.53 | 12.5 | 12.47 | 12.44 | 11.27 | 11.23 | 11.19 | 11.15 | 10.95 | 10.75 | 10.55
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Consumer Transformation | Headroom (MW) | Thermal | 13.79 | 13.68 | 13.6 | 13.52 | 13.41 | 13.31 | 13 | 12.41 | 11.83 | 11.31 | 10.8 | 10.31 | 9.8 | 9.24 | 8.65 | 4.96 | 2.54 | -0.11
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Leading the Way | Headroom (MW) | Thermal | 13.79 | 13.67 | 13.59 | 13.5 | 13.36 | 13.24 | 13 | 12.46 | 11.92 | 11.41 | 10.88 | 10.32 | 9.7 | 9.05 | 8.37 | 7.38 | 0.12 | -3.75
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | Steady Progression | Headroom (MW) | N/A | 13.79 | 13.7 | 13.64 | 13.59 | 13.55 | 13.51 | 13.19 | 12.87 | 12.56 | 12.27 | 12.01 | 11.79 | 11.66 | 11.57 | 11.5 | 11.33 | 10.96 | 10.54
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | System Transformation | Headroom (MW) | N/A | 13.79 | 13.69 | 13.62 | 13.56 | 13.49 | 13.43 | 13.16 | 12.91 | 12.67 | 12.48 | 12.23 | 11.93 | 11.64 | 11.32 | 10.99 | 11.13 | 6.88 | 5.55
East Claydon 132kV | Bletchley | FOX MILNE 33 11kV S STN | Primary | 11 | -0.7068 | 52.048 | WPD Best View | Headroom (MW) | Thermal | 13.79 | 13.67 | 13.59 | 13.5 | 13.36 | 13.24 | 13 | 12.46 | 11.92 | 11.41 | 10.88 | 10.32 | 9.7 | 9.05 | 8.37 | 7.38 | 0.12 | -3.75
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Consumer Transformation | Headroom (MW) | N/A | 15.36 | 15.28 | 15.25 | 15.19 | 15.12 | 15.06 | 15.01 | 14.96 | 14.91 | 14.85 | 14.8 | 14.74 | 14.69 | 14.63 | 14.58 | 13.87 | 12.87 | 11.78
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Leading the Way | Headroom (MW) | N/A | 15.36 | 15.27 | 15.24 | 15.18 | 15.1 | 15.04 | 14.98 | 14.93 | 14.87 | 14.81 | 14.75 | 14.68 | 14.62 | 14.55 | 14.48 | 13.61 | 12.48 | 11.04
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | Steady Progression | Headroom (MW) | N/A | 15.36 | 15.28 | 15.26 | 15.22 | 15.17 | 15.13 | 15.09 | 15.05 | 15.01 | 14.97 | 14.93 | 14.88 | 14.84 | 14.8 | 14.76 | 14.57 | 14.36 | 14.14
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | System Transformation | Headroom (MW) | N/A | 15.36 | 15.28 | 15.25 | 15.21 | 15.15 | 15.11 | 15.06 | 15.02 | 14.97 | 14.93 | 14.88 | 14.84 | 14.79 | 14.75 | 14.71 | 14.49 | 14.2 | 13.71
East Claydon 132kV | Bletchley | KINGSTON 33 11kV S STN | Primary | 11 | -0.6874 | 52.0413 | WPD Best View | Headroom (MW) | N/A | 15.36 | 15.27 | 15.24 | 15.18 | 15.1 | 15.04 | 14.98 | 14.93 | 14.87 | 14.81 | 14.75 | 14.68 | 14.62 | 14.55 | 14.48 | 13.61 | 12.48 | 11.04
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Consumer Transformation | Headroom (MW) | Fault level | -17.1106 | -17.1918 | -17.281 | -17.4108 | -17.711 | -18.01 | -18.3079 | -18.8936 | -19.5578 | -20.2998 | -21.2314 | -22.2871 | -23.415 | -24.4634 | -25.7099 | -28.521 | -31.7762 | -35.4929
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Leading the Way | Headroom (MW) | Fault level | -23.4171 | -23.533 | -23.6573 | -23.8418 | -24.2604 | -24.6897 | -25.1137 | -25.4952 | -25.8797 | -26.2697 | -26.6914 | -27.1269 | -28.391 | -29.6096 | -30.8753 | -35.1967 | -40.5582 | -43.4989
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | Steady Progression | Headroom (MW) | Fault level | -9.4392 | -9.4492 | -9.4554 | -9.4644 | -9.4763 | -9.4996 | -9.5251 | -9.5943 | -9.6618 | -9.7496 | -9.861 | -9.9952 | -10.2816 | -10.5654 | -10.9405 | -11.5413 | -12.1536 | -12.7705
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | System Transformation | Headroom (MW) | Fault level | -13.4886 | -13.5229 | -13.5553 | -13.6012 | -13.6866 | -13.7884 | -13.9063 | -14.2573 | -14.683 | -15.1571 | -15.7741 | -16.4871 | -17.2562 | -17.9617 | -18.8242 | -20.434 | -22.3351 | -24.5801
East Claydon 132kV | Bletchley | NEWTON ROAD 33 11kV S STN | Primary | 11 | -0.753 | 51.9905 | WPD Best View | Headroom (MW) | Fault level | -14.0637 | -14.1333 | -14.2079 | -14.3188 | -14.5702 | -14.828 | -15.0826 | -15.3117 | -15.5427 | -15.7769 | -16.0301 | -16.2917 | -17.0509 | -17.7828 | -18.5429 | -21.1382 | -24.3582 | -26.1243
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Consumer Transformation | Headroom (MW) | N/A | 5.27 | 5.23 | 5.21 | 5.22 | 5.2 | 5.18 | 5.16 | 5.15 | 5.13 | 5.11 | 5.09 | 5.07 | 5.05 | 5.03 | 5.01 | 4.88 | 4.99 | 4.6
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Leading the Way | Headroom (MW) | N/A | 5.27 | 5.23 | 5.21 | 5.23 | 5.2 | 5.18 | 5.16 | 5.15 | 5.12 | 5.1 | 5.08 | 5.05 | 5.03 | 5.01 | 4.98 | 5.29 | 4.89 | 4.41
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | Steady Progression | Headroom (MW) | N/A | 5.27 | 5.23 | 5.21 | 5.22 | 5.2 | 5.19 | 5.17 | 5.16 | 5.15 | 5.13 | 5.12 | 5.1 | 5.08 | 5.06 | 5.05 | 4.96 | 4.88 | 5.22
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | System Transformation | Headroom (MW) | N/A | 5.27 | 5.23 | 5.21 | 5.22 | 5.2 | 5.18 | 5.17 | 5.16 | 5.14 | 5.13 | 5.11 | 5.09 | 5.07 | 5.05 | 5.03 | 4.94 | 5.27 | 5.17
East Claydon 132kV | Bletchley | SECKLOW GATE 33 11kV S STN | Primary | 11 | -0.7463 | 52.0414 | WPD Best View | Headroom (MW) | N/A | 5.27 | 5.23 | 5.21 | 5.23 | 5.2 | 5.18 | 5.16 | 5.15 | 5.12 | 5.1 | 5.08 | 5.05 | 5.03 | 5.01 | 4.98 | 5.29 | 4.89 | 4.41
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Consumer Transformation | Headroom (MW) | Thermal | 15.44 | 10.83 | 10.79 | 10.57 | 10.36 | 10.07 | 9.27 | 8.51 | 7.83 | 7.29 | 6.84 | 6.48 | 6.17 | 5.84 | 5.5 | 3.15 | 0.77 | -2.02
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Leading the Way | Headroom (MW) | Thermal | 15.44 | 10.82 | 10.77 | 10.54 | 10.22 | 9.91 | 9.39 | 8.89 | 8.4 | 8.07 | 7.73 | 7.39 | 7.04 | 6.67 | 6.25 | 6.12 | 3.81 | -0.08
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | Steady Progression | Headroom (MW) | N/A | 14.584 | 7.1046 | 7.0931 | 6.8749 | 6.8643 | 6.8422 | 6.8173 | 6.7899 | 6.553 | 5.8617 | 5.2441 | 4.7292 | 4.4643 | 4.266 | 4.149 | 4.0092 | 3.8648 | 3.7182
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | System Transformation | Headroom (MW) | N/A | 15.44 | 10.85 | 10.82 | 10.62 | 10.48 | 10.45 | 9.98 | 9.52 | 8.99 | 8.61 | 8.32 | 8.12 | 7.97 | 7.84 | 7.71 | 8.69 | 6.24 | 5.3
East Claydon 132kV | Bletchley | VICTORIA ROAD 33 11kV S STN | Primary | 11 | -0.7186 | 51.9975 | WPD Best View | Headroom (MW) | Thermal | 15.44 | 10.82 | 10.77 | 10.54 | 10.22 | 9.91 | 9.39 | 8.89 | 8.4 | 8.07 | 7.73 | 7.39 | 7.04 | 6.67 | 6.25 | 6.12 | 3.81 | -0.08
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Consumer Transformation | Headroom (MW) | N/A | 35.1 | 34.92 | 34.73 | 34.54 | 34.28 | 34.04 | 33.55 | 32.82 | 32.06 | 31.29 | 30.65 | 29.98 | 29.35 | 28.72 | 28.07 | 24.51 | 21.21 | 17.68
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Leading the Way | Headroom (MW) | N/A | 35.1 | 34.94 | 34.75 | 34.54 | 34.23 | 33.94 | 33.31 | 32.45 | 31.56 | 30.65 | 29.93 | 29.19 | 28.49 | 27.84 | 27.21 | 23.82 | 20.15 | 15.61
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | Steady Progression | Headroom (MW) | N/A | 35.1 | 34.92 | 34.76 | 34.59 | 34.42 | 34.28 | 34.13 | 33.99 | 33.83 | 33.67 | 33.51 | 33.35 | 33.19 | 33.02 | 32.85 | 32.02 | 31.08 | 30.12
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | System Transformation | Headroom (MW) | N/A | 35.1 | 34.94 | 34.76 | 34.58 | 34.38 | 34.18 | 33.97 | 33.75 | 33.53 | 33.04 | 32.61 | 32.16 | 31.75 | 31.35 | 30.94 | 29.18 | 27.18 | 25.25
East Claydon 132kV | Bletchley | WAVENDON GATE 33 11kV S STN | Primary | 11 | -0.6881 | 52.0241 | WPD Best View | Headroom (MW) | N/A | 35.1 | 34.94 | 34.75 | 34.54 | 34.23 | 33.94 | 33.31 | 32.45 | 31.56 | 30.65 | 29.93 | 29.19 | 28.49 | 27.84 | 27.21 | 23.82 | 20.15 | 15.61
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Consumer Transformation | Headroom (MW) | Thermal | 15.1 | 14.96 | 14.86 | 14.74 | 14.41 | 14.11 | 13.35 | 11.9 | 10.64 | 9.34 | 8.01 | 6.6 | 5.16 | 3.75 | 2.08 | -3.89 | -10.65 | -18.04
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Leading the Way | Headroom (MW) | Thermal | 15.1 | 14.95 | 14.86 | 14.74 | 14.36 | 14.01 | 13.16 | 12.39 | 11.73 | 10.88 | 10.26 | 9.66 | 8.5 | 7.32 | 6.06 | 0.67 | -5.93 | -11.49
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | Steady Progression | Headroom (MW) | N/A | 15.1 | 15 | 14.96 | 14.92 | 14.85 | 14.79 | 14.72 | 14.58 | 14.37 | 13.78 | 13.52 | 13.22 | 12.64 | 12.13 | 11.48 | 10.51 | 9.33 | 7.98
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | System Transformation | Headroom (MW) | Thermal | 15.1 | 14.98 | 14.92 | 14.85 | 14.7 | 14.53 | 14.34 | 13.88 | 12.95 | 12.19 | 11.33 | 10.38 | 9.39 | 8.53 | 7.48 | 5.3 | 2.22 | -1.32
East Claydon 132kV | Brackley | BRACKLEY TOWN 33 11kV S STN | Primary | 11 | -1.1377 | 52.0273 | WPD Best View | Headroom (MW) | Thermal | 15.1 | 14.95 | 14.86 | 14.74 | 14.36 | 14.01 | 13.16 | 12.39 | 11.73 | 10.88 | 10.26 | 9.66 | 8.5 | 7.32 | 6.06 | 0.67 | -5.93 | -11.49
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Consumer Transformation | Headroom (MW) | Thermal | 7.01 | 6.9 | 6.78 | 6.65 | 6.42 | 6.21 | 5.87 | 5.2 | 4.56 | 3.9 | 3.18 | 2.42 | 1.63 | 0.83 | -0.11 | -4.14 | -8.84 | -12.9
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Leading the Way | Headroom (MW) | Thermal | 7.01 | 6.9 | 6.78 | 6.64 | 6.39 | 6.18 | 5.81 | 5.49 | 5.21 | 4.88 | 4.58 | 4.31 | 3.64 | 2.95 | 2.21 | -2.9 | -8.93 | -12.33
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | Steady Progression | Headroom (MW) | N/A | 7.01 | 6.94 | 6.89 | 6.83 | 6.78 | 6.72 | 6.66 | 6.54 | 6.41 | 6.13 | 5.97 | 5.77 | 5.41 | 5.08 | 4.65 | 4.06 | 3.24 | 2.27
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | System Transformation | Headroom (MW) | Thermal | 7.01 | 6.92 | 6.84 | 6.76 | 6.65 | 6.54 | 6.42 | 6.1 | 5.59 | 5.12 | 4.58 | 3.99 | 3.38 | 2.83 | 2.17 | -0.2 | -3.25 | -5.47
East Claydon 132kV | Brackley | Brackley 11kv | Primary | 11 | -1.1455 | 52.049 | WPD Best View | Headroom (MW) | Thermal | 7.01 | 6.9 | 6.78 | 6.64 | 6.39 | 6.18 | 5.81 | 5.49 | 5.21 | 4.88 | 4.58 | 4.31 | 3.64 | 2.95 | 2.21 | -2.9 | -8.93 | -12.33
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Consumer Transformation | Headroom (MW) | N/A | 25.45 | 25.66 | 25.75 | 25.92 | 26.29 | 26.5 | 26.58 | 26.45 | 25.87 | 25.19 | 24.3 | 23.17 | 21.94 | 20.83 | 19.42 | 16.74 | 13.3 | 9.17
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Leading the Way | Headroom (MW) | N/A | 25.45 | 25.7 | 25.81 | 26.01 | 26.44 | 26.75 | 26.86 | 26.91 | 26.9 | 26.9 | 26.89 | 26.84 | 26.06 | 25.13 | 24.15 | 21.07 | 16.97 | 14.96
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | Steady Progression | Headroom (MW) | N/A | 25.45 | 25.63 | 25.71 | 25.86 | 26.22 | 26.41 | 26.48 | 26.53 | 26.54 | 26.55 | 26.56 | 26.43 | 25.8 | 25.15 | 24.28 | 23.06 | 21.49 | 19.8
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | System Transformation | Headroom (MW) | N/A | 25.45 | 25.67 | 25.77 | 25.94 | 26.34 | 26.56 | 26.65 | 26.69 | 26.19 | 25.57 | 24.73 | 23.65 | 22.48 | 21.42 | 20.06 | 17.92 | 14.93 | 11.33
East Claydon 132kV | Brackley | SILVERSTONE 33 11kV S STN | Primary | 11 | -1.0311 | 52.0748 | WPD Best View | Headroom (MW) | N/A | 25.45 | 25.7 | 25.81 | 26.01 | 26.44 | 26.75 | 26.86 | 26.91 | 26.9 | 26.9 | 26.89 | 26.84 | 26.06 | 25.13 | 24.15 | 21.07 | 16.97 | 14.96
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Consumer Transformation | Headroom (MW) | Thermal | 5.5 | 5.39 | 5.3 | 4.96 | 4.7 | 4.41 | 4.13 | 3.15 | 2 | 0.68 | -0.91 | -2.74 | -4.71 | -6.55 | -8.8 | -14.26 | -20.23 | -27.46
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Leading the Way | Headroom (MW) | Thermal | 5.5 | 5.38 | 5.28 | 4.94 | 4.65 | 4.29 | 3.94 | 3.61 | 3.29 | 2.99 | 2.64 | 2.3 | 0.72 | -0.84 | -2.5 | -9.47 | -16.87 | -21.66
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | Steady Progression | Headroom (MW) | Thermal | 5.5 | 5.44 | 5.41 | 5.38 | 5.35 | 5.3 | 5.26 | 5.04 | 4.82 | 4.54 | 4.21 | 3.79 | 2.81 | 1.83 | 0.52 | -1.14 | -2.92 | -4.92
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | System Transformation | Headroom (MW) | Thermal | 5.5 | 5.42 | 5.36 | 5.3 | 5.19 | 5.1 | 5 | 4.15 | 3.06 | 1.89 | 0.46 | -1.21 | -3 | -4.6 | -6.61 | -10.37 | -14.91 | -20.4
East Claydon 132kV | Brackley | THENFORD 33 11kV S STN | Primary | 11 | -1.2411 | 52.0774 | WPD Best View | Headroom (MW) | Thermal | 5.5 | 5.38 | 5.28 | 4.94 | 4.65 | 4.29 | 3.94 | 3.61 | 3.29 | 2.99 | 2.64 | 2.3 | 0.72 | -0.84 | -2.5 | -9.47 | -16.87 | -21.66
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Consumer Transformation | Headroom (MW) | Thermal | 19.94 | 19.81 | 20.26 | 20.71 | 21.04 | 20.93 | 20.81 | 20.11 | 19.29 | 18.34 | 17.14 | 15.65 | 14.04 | 12.54 | 10.69 | 6.25 | 1.12 | -4.91
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Leading the Way | Headroom (MW) | Thermal | 19.94 | 19.8 | 20.32 | 20.93 | 21.4 | 21.29 | 21.11 | 20.9 | 20.7 | 20.49 | 20.22 | 15.17 | 13.85 | 12.56 | 11.17 | 5.97 | -0.33 | -4.71
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | Steady Progression | Headroom (MW) | N/A | 19.94 | 19.88 | 20.34 | 20.84 | 21.4 | 21.52 | 21.61 | 21.57 | 21.54 | 21.42 | 21.26 | 21.01 | 20.3 | 19.55 | 18.54 | 17.21 | 15.57 | 13.56
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | System Transformation | Headroom (MW) | N/A | 19.94 | 19.85 | 20.35 | 20.88 | 21.43 | 21.48 | 21.5 | 20.94 | 20.23 | 19.41 | 18.34 | 16.98 | 15.52 | 14.19 | 12.53 | 9.7 | 5.83 | 1.32
East Claydon 132kV | Brackley | TOWCESTER 33 11kV S STN | Primary | 11 | -0.9797 | 52.1246 | WPD Best View | Headroom (MW) | Thermal | 19.94 | 19.8 | 20.32 | 20.93 | 21.4 | 21.29 | 21.11 | 20.9 | 20.7 | 20.49 | 20.22 | 15.17 | 13.85 | 12.56 | 11.17 | 5.97 | -0.33 | -4.71
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Consumer Transformation | Headroom (MW) | N/A | 18.78 | 18.64 | 18.55 | 18.45 | 18.29 | 18.18 | 18.04 | 17.92 | 17.8 | 17.66 | 17.48 | 17.19 | 16.89 | 16.59 | 16.28 | 14.28 | 13.04 | 11.74
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Leading the Way | Headroom (MW) | N/A | 18.78 | 18.64 | 18.54 | 18.43 | 18.24 | 18.11 | 17.98 | 17.83 | 17.67 | 17.5 | 17.3 | 16.97 | 16.64 | 16.29 | 15.91 | 19.79 | 7.86 | 4.37
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | Steady Progression | Headroom (MW) | N/A | 18.78 | 18.66 | 18.59 | 18.52 | 18.43 | 18.36 | 18.24 | 18.17 | 18.1 | 18.03 | 17.96 | 17.88 | 17.81 | 17.73 | 17.66 | 17.32 | 16.97 | 16.53
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | System Transformation | Headroom (MW) | N/A | 18.78 | 18.65 | 18.57 | 18.49 | 18.38 | 18.29 | 18.18 | 18.08 | 17.99 | 17.89 | 17.8 | 17.72 | 17.63 | 17.55 | 17.45 | 20.48 | 13.15 | 11.87
East Claydon 132kV | Bradwell Abbey | CHILDS WAY 33 11kV S STN | Primary | 11 | -0.7647 | 52.0336 | WPD Best View | Headroom (MW) | N/A | 18.78 | 18.64 | 18.54 | 18.43 | 18.24 | 18.11 | 17.98 | 17.83 | 17.67 | 17.5 | 17.3 | 16.97 | 16.64 | 16.29 | 15.91 | 19.79 | 7.86 | 4.37
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Consumer Transformation | Headroom (MW) | Thermal | 8.87 | 8.81 | 8.75 | 8.69 | 8.56 | 8.43 | 7.46 | 5.45 | 3.86 | 2.28 | 0.77 | -0.75 | -2.3 | -3.86 | -5.65 | -12.15 | -19.66 | -27.69
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Leading the Way | Headroom (MW) | Thermal | 8.87 | 8.81 | 8.76 | 8.71 | 8.59 | 8.47 | 7.43 | 6.59 | 5.95 | 4.99 | 4.26 | -0.48 | -1.67 | -2.89 | -4.21 | -9.71 | -16.28 | -22.08
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | Steady Progression | Headroom (MW) | N/A | 8.87 | 8.82 | 8.78 | 8.75 | 8.71 | 8.68 | 8.64 | 8.61 | 8.38 | 7.43 | 7.18 | 6.88 | 6.32 | 5.86 | 5.3 | 4.41 | 3.51 | 2.51
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | System Transformation | Headroom (MW) | Thermal | 8.87 | 8.81 | 8.78 | 8.74 | 8.69 | 8.65 | 8.61 | 8.27 | 7.16 | 6.4 | 5.57 | 4.7 | 3.82 | 3.06 | 2.16 | 0.15 | -2.51 | -5.57
East Claydon 132kV | Bradwell Abbey | HANSLOPE PARK 33 11kV S STN | Primary | 11 | -0.8058 | 52.1067 | WPD Best View | Headroom (MW) | Thermal | 8.87 | 8.81 | 8.76 | 8.71 | 8.59 | 8.47 | 7.43 | 6.59 | 5.95 | 4.99 | 4.26 | -0.48 | -1.67 | -2.89 | -4.21 | -9.71 | -16.28 | -22.08
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Consumer Transformation | Headroom (MW) | N/A | 16.19 | 16.13 | 16.05 | 15.95 | 15.82 | 15.73 | 15.58 | 15.27 | 14.99 | 14.73 | 14.46 | 14.19 | 13.91 | 13.61 | 13.29 | 10.95 | 7.63 | 3.9
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Leading the Way | Headroom (MW) | N/A | 16.19 | 16.13 | 16.03 | 15.93 | 15.75 | 15.65 | 15.47 | 15.15 | 14.85 | 14.57 | 14.25 | 13.93 | 13.59 | 13.2 | 12.76 | 9.89 | 6.07 | 0.96
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | Steady Progression | Headroom (MW) | N/A | 16.19 | 16.15 | 16.1 | 16.05 | 16.01 | 15.96 | 15.91 | 15.87 | 15.82 | 15.77 | 15.72 | 15.66 | 15.61 | 15.56 | 15.5 | 15.25 | 14.91 | 14.48
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | System Transformation | Headroom (MW) | N/A | 16.19 | 16.14 | 16.08 | 16.01 | 15.93 | 15.88 | 15.82 | 15.75 | 15.69 | 15.63 | 15.56 | 15.49 | 15.42 | 15.34 | 15.23 | 14.51 | 12.85 | 11.2
East Claydon 132kV | Bradwell Abbey | MARLBOROUGH STREET 33 11kV S STN | Primary | 11 | -0.7589 | 52.0622 | WPD Best View | Headroom (MW) | N/A | 16.19 | 16.13 | 16.03 | 15.93 | 15.75 | 15.65 | 15.47 | 15.15 | 14.85 | 14.57 | 14.25 | 13.93 | 13.59 | 13.2 | 12.76 | 9.89 | 6.07 | 0.96
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Consumer Transformation | Headroom (MW) | Thermal | 11.78 | 11.6 | 11.51 | 11.34 | 11.44 | 11.42 | 11.15 | 10.89 | 10.64 | 10.41 | 10.17 | 9.89 | 9.61 | 9.3 | 8.98 | 6.73 | 2.95 | -0.31
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Leading the Way | Headroom (MW) | Thermal | 11.78 | 11.58 | 11.5 | 11.3 | 11.51 | 11.62 | 11.33 | 11.01 | 10.7 | 10.41 | 10.07 | 9.75 | 9.39 | 9 | 8.58 | 5.92 | 0.87 | -3.55
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | Steady Progression | Headroom (MW) | N/A | 11.78 | 11.68 | 11.69 | 11.64 | 12.05 | 12.26 | 12.26 | 12.26 | 12.27 | 12.27 | 12.27 | 12.28 | 12.29 | 12.28 | 12.28 | 12.31 | 11.92 | 11.16
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | System Transformation | Headroom (MW) | N/A | 11.78 | 11.64 | 11.61 | 11.52 | 11.88 | 12.05 | 11.93 | 11.83 | 11.72 | 11.62 | 11.52 | 11.4 | 11.31 | 11.22 | 11.11 | 10.4 | 8.08 | 6.6
East Claydon 132kV | Bradwell Abbey | NEWPORT PAGNELL 33 11kV S STN | Primary | 11 | -0.7259 | 52.076 | WPD Best View | Headroom (MW) | Thermal | 11.78 | 11.58 | 11.5 | 11.3 | 11.51 | 11.62 | 11.33 | 11.01 | 10.7 | 10.41 | 10.07 | 9.75 | 9.39 | 9 | 8.58 | 5.92 | 0.87 | -3.55
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Consumer Transformation | Headroom (MW) | N/A | 13.99 | 13.92 | 13.92 | 13.88 | 13.78 | 13.59 | 13.37 | 13.14 | 12.93 | 12.75 | 12.57 | 12.39 | 12.21 | 12.03 | 11.84 | 10.69 | 9.4 | 8.01
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Leading the Way | Headroom (MW) | N/A | 13.99 | 13.92 | 13.93 | 13.88 | 13.74 | 13.53 | 13.29 | 13.03 | 12.78 | 12.58 | 12.39 | 12.2 | 12 | 11.8 | 11.59 | 10.38 | 8.94 | 7.15
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | Steady Progression | Headroom (MW) | N/A | 13.99 | 13.93 | 13.94 | 13.91 | 13.86 | 13.83 | 13.81 | 13.78 | 13.75 | 13.72 | 13.68 | 13.65 | 13.61 | 13.58 | 13.54 | 13.36 | 13.14 | 12.82
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | System Transformation | Headroom (MW) | N/A | 13.99 | 13.93 | 13.94 | 13.9 | 13.84 | 13.8 | 13.72 | 13.59 | 13.46 | 13.35 | 13.24 | 13.14 | 13.04 | 12.95 | 12.86 | 12.42 | 11.74 | 11.05
East Claydon 132kV | Bradwell Abbey | PORTWAY 33 11kV S STN | Primary | 11 | -0.7618 | 52.0451 | WPD Best View | Headroom (MW) | N/A | 13.99 | 13.92 | 13.93 | 13.88 | 13.74 | 13.53 | 13.29 | 13.03 | 12.78 | 12.58 | 12.39 | 12.2 | 12 | 11.8 | 11.59 | 10.38 | 8.94 | 7.15
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Consumer Transformation | Headroom (MW) | Fault level | -16.9094 | -16.9675 | -17.0126 | -17.0758 | -17.2316 | -17.3952 | -17.56 | -17.7292 | -17.903 | -18.0949 | -18.2737 | -18.4481 | -18.6247 | -18.803 | -18.9808 | -19.8644 | -20.4315 | -21.3518
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Leading the Way | Headroom (MW) | Fault level | -23.1417 | -22.7587 | -22.8228 | -22.9131 | -23.1271 | -23.361 | -23.595 | -23.8398 | -24.0931 | -24.3796 | -24.6368 | -24.8839 | -25.1348 | -25.3897 | -25.6437 | -26.9056 | -28.2353 | -29.5883
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | Steady Progression | Headroom (MW) | Fault level | -9.3282 | -9.3447 | -9.3481 | -9.3525 | -9.3559 | -9.3681 | -9.3818 | -9.3973 | -9.4132 | -9.4341 | -9.454 | -9.4736 | -9.4935 | -9.5134 | -9.5318 | -9.6202 | -9.7133 | -9.6202
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | System Transformation | Headroom (MW) | Fault level | -13.33 | -13.3625 | -13.3794 | -13.4021 | -13.4421 | -13.4964 | -13.5608 | -13.6276 | -13.6961 | -13.7753 | -13.846 | -13.9149 | -13.9852 | -14.0568 | -14.1289 | -14.4803 | -14.5644 | -14.9184
East Claydon 132kV | Bradwell Abbey | WOLVERTON 33 11kV S STN | Primary | 11 | -0.8221 | 52.0634 | WPD Best View | Headroom (MW) | Fault level | -13.8983 | -13.6683 | -13.7068 | -13.761 | -13.8895 | -14.03 | -14.1706 | -14.3176 | -14.4697 | -14.6418 | -14.7962 | -14.9446 | -15.0953 | -15.2484 | -15.401 | -16.1588 | -16.9574 | -17.7699
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Consumer Transformation | Headroom (MW) | Thermal | 14.18 | 14.07 | 13.85 | 13.72 | 13.33 | 13.01 | 12.68 | 11.79 | 10.77 | 9.62 | 8.17 | 6.51 | 4.72 | 3.02 | 0.91 | -3.84 | -9.66 | -16.6
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Leading the Way | Headroom (MW) | Thermal | 14.18 | 14.06 | 13.84 | 13.7 | 13.28 | 12.92 | 12.56 | 12.23 | 11.9 | 11.59 | 11.29 | 10.99 | 9.56 | 8.17 | 6.67 | 1.25 | -5.98 | -10.69
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | Steady Progression | Headroom (MW) | N/A | 14.18 | 14.13 | 14.12 | 14.1 | 14.06 | 14.02 | 13.97 | 13.78 | 13.59 | 13.36 | 13.04 | 12.64 | 11.73 | 10.84 | 9.65 | 8.21 | 6.32 | 4.11
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | System Transformation | Headroom (MW) | Thermal | 14.18 | 14.11 | 14.06 | 13.88 | 13.73 | 13.58 | 13.41 | 12.67 | 11.75 | 10.72 | 9.39 | 7.85 | 6.19 | 4.7 | 2.83 | -0.23 | -4.61 | -9.8
East Claydon 132kV | Stony Stratford | BUCKINGHAM 33 11kV S STN | Primary | 11 | -0.9758 | 51.9963 | WPD Best View | Headroom (MW) | Thermal | 14.18 | 14.06 | 13.84 | 13.7 | 13.28 | 12.92 | 12.56 | 12.23 | 11.9 | 11.59 | 11.29 | 10.99 | 9.56 | 8.17 | 6.67 | 1.25 | -5.98 | -10.69
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Consumer Transformation | Headroom (MW) | Thermal | 2.975 | 2.945 | 2.915 | 2.895 | 2.825 | 2.715 | 2.455 | 1.905 | 1.405 | 0.875 | 0.315 | -0.275 | -0.915 | -1.525 | -2.255 | -4.665 | -7.285 | -10.195
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Leading the Way | Headroom (MW) | Thermal | 2.975 | 2.935 | 2.915 | 2.895 | 2.815 | 2.675 | 2.365 | 2.065 | 1.795 | 1.455 | 1.245 | 1.035 | 0.525 | 0.025 | -0.515 | -2.655 | -5.255 | -7.095
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | Steady Progression | Headroom (MW) | Thermal | 2.975 | 2.955 | 2.945 | 2.945 | 2.935 | 2.915 | 2.905 | 2.845 | 2.775 | 2.565 | 2.455 | 2.315 | 2.045 | 1.785 | 1.455 | 1.005 | 0.465 | -0.085
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | System Transformation | Headroom (MW) | Thermal | 2.975 | 2.945 | 2.935 | 2.925 | 2.895 | 2.835 | 2.755 | 2.545 | 2.155 | 1.805 | 1.405 | 0.965 | 0.495 | 0.085 | -0.425 | -1.395 | -2.665 | -4.175
East Claydon 132kV | Stony Stratford | CALVERT 33 11kV S STN | Primary | 11 | -0.9916 | 51.9284 | WPD Best View | Headroom (MW) | Thermal | 2.975 | 2.935 | 2.915 | 2.895 | 2.815 | 2.675 | 2.365 | 2.065 | 1.795 | 1.455 | 1.245 | 1.035 | 0.525 | 0.025 | -0.515 | -2.655 | -5.255 | -7.095
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Consumer Transformation | Headroom (MW) | N/A | 13.53 | 13.5 | 13.77 | 13.91 | 13.93 | 13.93 | 13.93 | 13.92 | 13.9 | 13.88 | 13.85 | 13.82 | 13.79 | 13.76 | 13.72 | 13.42 | 13.09 | 12.76
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Leading the Way | Headroom (MW) | N/A | 13.53 | 13.51 | 13.81 | 13.98 | 14.01 | 13.99 | 13.96 | 13.93 | 13.9 | 13.87 | 13.84 | 13.8 | 13.77 | 13.74 | 13.71 | 13.41 | 13.06 | 12.67
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | Steady Progression | Headroom (MW) | N/A | 13.53 | 13.5 | 13.74 | 13.85 | 13.88 | 13.89 | 13.89 | 13.89 | 13.9 | 13.88 | 13.87 | 13.85 | 13.83 | 13.8 | 13.78 | 13.65 | 13.52 | 13.4
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | System Transformation | Headroom (MW) | N/A | 13.53 | 13.5 | 13.78 | 13.91 | 13.94 | 13.94 | 13.94 | 13.93 | 13.91 | 13.9 | 13.87 | 13.85 | 13.82 | 13.79 | 13.76 | 13.63 | 13.48 | 13.31
East Claydon 132kV | Stony Stratford | ELDERGATE 33 11kV S STN | Primary | 11 | -0.7715 | 52.0409 | WPD Best View | Headroom (MW) | N/A | 13.53 | 13.51 | 13.81 | 13.98 | 14.01 | 13.99 | 13.96 | 13.93 | 13.9 | 13.87 | 13.84 | 13.8 | 13.77 | 13.74 | 13.71 | 13.41 | 13.06 | 12.67
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Consumer Transformation | Headroom (MW) | N/A | 15.06 | 14.9 | 14.8 | 14.61 | 14.11 | 13.74 | 13.36 | 12.95 | 12.57 | 12.16 | 11.73 | 11.26 | 10.88 | 10.48 | 10.07 | 7.62 | 4.86 | 1.83
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Leading the Way | Headroom (MW) | Thermal | 15.06 | 14.88 | 14.78 | 14.57 | 13.98 | 13.57 | 13.17 | 12.74 | 12.32 | 11.87 | 11.37 | 10.85 | 10.44 | 10.04 | 9.63 | 7.13 | 3.98 | -0.06
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | Steady Progression | Headroom (MW) | N/A | 15.06 | 14.97 | 14.97 | 14.94 | 14.88 | 14.83 | 14.77 | 14.71 | 14.65 | 14.58 | 14.52 | 14.45 | 14.39 | 14.32 | 14.27 | 14.13 | 13.79 | 13.11
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | System Transformation | Headroom (MW) | N/A | 15.06 | 14.94 | 14.9 | 14.8 | 14.58 | 14.41 | 14.21 | 14 | 13.79 | 13.58 | 13.34 | 13.09 | 12.89 | 12.7 | 12.52 | 11.71 | 10.31 | 8.91
East Claydon 132kV | Stony Stratford | KILN FARM 33 11kV S STN | Primary | 11 | -0.8255 | 52.0494 | WPD Best View | Headroom (MW) | Thermal | 15.06 | 14.88 | 14.78 | 14.57 | 13.98 | 13.57 | 13.17 | 12.74 | 12.32 | 11.87 | 11.37 | 10.85 | 10.44 | 10.04 | 9.63 | 7.13 | 3.98 | -0.06
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Consumer Transformation | Headroom (MW) | N/A | 14.36 | 14.28 | 14.21 | 14.14 | 14 | 13.83 | 13.54 | 13.27 | 13.02 | 12.8 | 12.54 | 12.3 | 12.04 | 11.77 | 11.48 | 9.38 | 6.58 | 3.46
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Leading the Way | Headroom (MW) | N/A | 14.36 | 14.27 | 14.19 | 14.11 | 13.93 | 13.73 | 13.43 | 13.16 | 12.89 | 12.66 | 12.37 | 12.07 | 11.77 | 11.42 | 11.04 | 8.53 | 5.3 | 0.98
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | Steady Progression | Headroom (MW) | N/A | 14.36 | 14.31 | 14.27 | 14.24 | 14.19 | 14.16 | 14.13 | 14.1 | 14.07 | 14.03 | 14 | 13.97 | 13.93 | 13.89 | 13.86 | 13.7 | 13.45 | 13.04
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | System Transformation | Headroom (MW) | N/A | 14.36 | 14.29 | 14.24 | 14.19 | 14.11 | 14.07 | 14.03 | 13.98 | 13.93 | 13.88 | 13.76 | 13.64 | 13.54 | 13.44 | 13.35 | 12.66 | 11.33 | 10.05
East Claydon 132kV | Stony Stratford | SHENLEY WOOD 33 11kV S STN | Primary | 11 | -0.7948 | 52.019 | WPD Best View | Headroom (MW) | N/A | 14.36 | 14.27 | 14.19 | 14.11 | 13.93 | 13.73 | 13.43 | 13.16 | 12.89 | 12.66 | 12.37 | 12.07 | 11.77 | 11.42 | 11.04 | 8.53 | 5.3 | 0.98
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Consumer Transformation | Headroom (MW) | Thermal | 6.79 | 1.6 | 1.54 | 1.46 | 1.31 | 1.18 | 1.06 | 0.54 | -0.08 | -0.79 | -1.67 | -2.69 | -3.82 | -4.86 | -6.16 | -8.57 | -11.62 | -15.32
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Leading the Way | Headroom (MW) | Thermal | 6.79 | 1.6 | 1.53 | 1.45 | 1.29 | 1.15 | 1.03 | 0.91 | 0.81 | 0.71 | 0.6 | 0.49 | -0.35 | -1.16 | -2.07 | -4.9 | -8.75 | -10.86
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | Steady Progression | Headroom (MW) | N/A | 6.79 | 6.76 | 6.74 | 6.72 | 6.71 | 6.69 | 6.66 | 6.54 | 6.42 | 6.27 | 6.07 | 5.82 | 5.23 | 4.65 | 3.87 | 2.9 | 1.81 | 0.57
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | System Transformation | Headroom (MW) | Thermal | 6.79 | 6.74 | 6.71 | 6.66 | 6.6 | 6.55 | 6.49 | 6.02 | 5.44 | 4.77 | 3.94 | 2.95 | 1.89 | 0.94 | -0.26 | -2.06 | -4.52 | -7.48
East Claydon 132kV | Stony Stratford | WICKEN 33 11kV S STN | Primary | 11 | -0.9047 | 52.048 | WPD Best View | Headroom (MW) | Thermal | 6.79 | 1.6 | 1.53 | 1.45 | 1.29 | 1.15 | 1.03 | 0.91 | 0.81 | 0.71 | 0.6 | 0.49 | -0.35 | -1.16 | -2.07 | -4.9 | -8.75 | -10.86
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Consumer Transformation | Headroom (MW) | Thermal | 7.38 | 7.31 | 7.25 | 7.18 | 6.98 | 6.68 | 6.38 | 5.34 | 4.11 | 2.7 | 0.89 | -1.23 | -3.52 | -5.63 | -8.24 | -13.78 | -20.46 | -28.63
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Leading the Way | Headroom (MW) | Thermal | 7.38 | 7.3 | 7.24 | 7.17 | 6.96 | 6.55 | 6.14 | 5.74 | 5.34 | 4.92 | 4.55 | 4.17 | 2.35 | 0.61 | -1.29 | -7.65 | -16.03 | -20.74
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | Steady Progression | Headroom (MW) | Thermal | 7.38 | 7.34 | 7.33 | 7.33 | 7.31 | 7.29 | 7.26 | 7.05 | 6.83 | 6.55 | 6.17 | 5.68 | 4.54 | 3.41 | 1.87 | -0.1 | -2.32 | -4.68
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | System Transformation | Headroom (MW) | Thermal | 7.38 | 7.33 | 7.3 | 7.27 | 7.2 | 7.1 | 7 | 6.09 | 4.92 | 3.68 | 2.03 | 0.09 | -2.01 | -3.89 | -6.27 | -9.91 | -15.2 | -21.68
East Claydon 132kV | Stony Stratford | WINSLOW 33 11kV S STN | Primary | 11 | -0.8839 | 51.9518 | WPD Best View | Headroom (MW) | Thermal | 7.38 | 7.3 | 7.24 | 7.17 | 6.96 | 6.55 | 6.14 | 5.74 | 5.34 | 4.92 | 4.55 | 4.17 | 2.35 | 0.61 | -1.29 | -7.65 | -16.03 | -20.74
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Consumer Transformation | Headroom (MW) | N/A | 15.11 | 15.12 | 15.07 | 15.01 | 14.79 | 14.41 | 14.01 | 13.6 | 13.17 | 12.76 | 12.35 | 11.91 | 11.46 | 10.98 | 10.48 | 7.56 | 4.39 | 0.95
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Leading the Way | Headroom (MW) | Thermal | 15.11 | 15.13 | 15.07 | 15 | 14.73 | 14.31 | 13.89 | 13.43 | 12.96 | 12.49 | 12.01 | 11.5 | 10.96 | 10.39 | 9.79 | 6.65 | 3.07 | -1.56
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | Steady Progression | Headroom (MW) | N/A | 15.11 | 15.13 | 15.11 | 15.08 | 15.05 | 15.03 | 15.01 | 14.98 | 14.96 | 14.93 | 14.89 | 14.86 | 14.82 | 14.79 | 14.76 | 14.57 | 14.15 | 13.4
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | System Transformation | Headroom (MW) | N/A | 15.11 | 15.13 | 15.1 | 15.06 | 15.01 | 14.96 | 14.85 | 14.63 | 14.4 | 14.18 | 13.95 | 13.71 | 13.48 | 13.24 | 13.01 | 12 | 10.41 | 8.9
Enderby 132kV | Coalville | BARDON 33 11kV S STN | Primary | 11 | -1.3478 | 52.7138 | WPD Best View | Headroom (MW) | N/A | 15.11 | 15.12 | 15.07 | 15.01 | 14.79 | 14.41 | 14.01 | 13.6 | 13.17 | 12.76 | 12.35 | 11.91 | 11.46 | 10.98 | 10.48 | 7.56 | 4.39 | 0.95
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Consumer Transformation | Headroom (MW) | Thermal | 9.62 | 9.51 | 9.46 | 9.01 | 8.81 | 8.61 | 8.42 | 8.07 | 7.72 | 7.34 | 6.88 | 6.37 | 5.8 | 5.24 | 4.56 | 2.57 | -1.26 | -4.1
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Leading the Way | Headroom (MW) | Thermal | 9.62 | 9.51 | 9.45 | 8.97 | 8.73 | 8.53 | 8.33 | 8.14 | 8.02 | 7.92 | 7.81 | 7.7 | 7.23 | 6.73 | 6.2 | 3.87 | -1.87 | -4.34
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | Steady Progression | Headroom (MW) | N/A | 9.62 | 9.55 | 9.55 | 9.53 | 9.51 | 9.48 | 9.45 | 9.35 | 9.27 | 9.19 | 9.08 | 8.96 | 8.71 | 8.44 | 8.08 | 7.65 | 6.94 | 6.05
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | System Transformation | Headroom (MW) | Thermal | 9.62 | 9.53 | 9.51 | 9.46 | 9.38 | 9.28 | 9.18 | 8.9 | 8.61 | 8.29 | 7.89 | 7.44 | 6.96 | 6.51 | 5.96 | 4.86 | 1.79 | -0.11
Enderby 132kV | Coalville | COALVILLE 11kV S STN | Primary | 11 | -1.3276 | 52.6882 | WPD Best View | Headroom (MW) | Thermal | 9.62 | 9.51 | 9.46 | 9.01 | 8.81 | 8.61 | 8.42 | 8.07 | 7.72 | 7.34 | 6.88 | 6.37 | 5.8 | 5.24 | 4.56 | 2.57 | -1.26 | -4.1
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Consumer Transformation | Headroom (MW) | Thermal | 7.56 | 7.34 | 7.14 | 6.91 | 6.44 | 6.03 | 5.65 | 5.01 | 4.36 | 3.66 | 2.71 | 1.61 | 0.44 | -0.67 | -1.99 | -7.09 | -13.32 | -19.38
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Leading the Way | Headroom (MW) | Thermal | 7.56 | 7.32 | 7.12 | 6.88 | 6.38 | 5.95 | 5.54 | 5.16 | 4.83 | 4.5 | 4.15 | 0.49 | -0.53 | -1.53 | -2.63 | -8.43 | -16.78 | -22.37
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | Steady Progression | Headroom (MW) | N/A | 7.56 | 7.43 | 7.37 | 7.31 | 7.25 | 7.17 | 7.09 | 6.95 | 6.82 | 6.66 | 6.44 | 6.19 | 5.68 | 5.19 | 4.53 | 3.66 | 2.34 | 0.61
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | System Transformation | Headroom (MW) | Thermal | 7.56 | 7.39 | 7.27 | 7.14 | 6.96 | 6.77 | 6.57 | 6.1 | 5.59 | 5.03 | 4.24 | 3.34 | 2.38 | 1.51 | 0.42 | -2.22 | -6.66 | -10.52
Enderby 132kV | Coalville | DESFORD 33 11kV S STN | Primary | 11 | -1.2715 | 52.6395 | WPD Best View | Headroom (MW) | Thermal | 7.56 | 7.34 | 7.14 | 6.91 | 6.44 | 6.03 | 5.65 | 5.01 | 4.36 | 3.66 | 2.71 | 1.61 | 0.44 | -0.67 | -1.99 | -7.09 | -13.32 | -19.38
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Consumer Transformation | Headroom (MW) | N/A | 13.68 | 13.64 | 13.61 | 13.59 | 13.56 | 13.53 | 13.51 | 13.48 | 13.45 | 13.42 | 13.39 | 13.37 | 13.34 | 13.31 | 13.29 | 13.17 | 13.07 | 12.91
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Leading the Way | Headroom (MW) | N/A | 13.68 | 13.64 | 13.61 | 13.59 | 13.55 | 13.53 | 13.5 | 13.47 | 13.44 | 13.41 | 13.38 | 13.35 | 13.32 | 13.3 | 13.27 | 13.16 | 13.06 | 12.9
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | Steady Progression | Headroom (MW) | N/A | 13.68 | 13.64 | 13.61 | 13.59 | 13.56 | 13.54 | 13.52 | 13.49 | 13.47 | 13.45 | 13.42 | 13.4 | 13.38 | 13.36 | 13.34 | 13.23 | 13.13 | 13.04
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | System Transformation | Headroom (MW) | N/A | 13.68 | 13.64 | 13.61 | 13.59 | 13.56 | 13.54 | 13.51 | 13.49 | 13.46 | 13.44 | 13.41 | 13.39 | 13.36 | 13.34 | 13.32 | 13.21 | 13.11 | 13.02
Enderby 132kV | Coalville | INTERLINK PARK 33 11kV S STN | Primary | 11 | -1.3464 | 52.699 | WPD Best View | Headroom (MW) | N/A | 13.68 | 13.64 | 13.61 | 13.59 | 13.56 | 13.53 | 13.51 | 13.48 | 13.45 | 13.42 | 13.39 | 13.37 | 13.34 | 13.31 | 13.29 | 13.17 | 13.07 | 12.91
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Consumer Transformation | Headroom (MW) | Thermal | 16.63 | 16.49 | 16.27 | 16.11 | 15.5 | 14.99 | 13.41 | 10.6 | 8.38 | 6.23 | 3.85 | 1.48 | -0.98 | -3.5 | -6.35 | -20.07 | -35.77 | -52.52
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Leading the Way | Headroom (MW) | Thermal | 16.63 | 16.47 | 16.26 | 16.2 | 15.56 | 15.03 | 13.31 | 11.85 | 10.67 | 9.07 | 7.6 | 6.2 | 4.22 | 2.13 | -0.16 | -12.58 | -26.83 | -41.15
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | Steady Progression | Headroom (MW) | N/A | 16.63 | 16.52 | 16.46 | 16.71 | 16.63 | 16.55 | 16.46 | 16.31 | 15.99 | 14.77 | 14.4 | 13.97 | 13.22 | 12.63 | 11.96 | 10.86 | 9.25 | 7.2
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | System Transformation | Headroom (MW) | Thermal | 16.63 | 16.51 | 16.4 | 16.6 | 16.36 | 16.14 | 15.9 | 15.42 | 13.97 | 13.01 | 11.84 | 10.66 | 9.49 | 8.5 | 7.32 | 3.16 | -2.35 | -8.43
Enderby 132kV | Coalville | MANTLE LANE COALVILLE 33 11kV S STN | Primary | 11 | -1.3751 | 52.7266 | WPD Best View | Headroom (MW) | Thermal | 16.63 | 16.49 | 16.27 | 16.11 | 15.5 | 14.99 | 13.41 | 10.6 | 8.38 | 6.23 | 3.85 | 1.48 | -0.98 | -3.5 | -6.35 | -20.07 | -35.77 | -52.52
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Consumer Transformation | Headroom (MW) | Thermal | 3.8 | 3.73 | 3.63 | 3.52 | 3.27 | 3.04 | 1.61 | -1.14 | -3.18 | -5.09 | -7.19 | -9.26 | -11.3 | -13.45 | -15.87 | -27.07 | -41.83 | -56.57
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Leading the Way | Headroom (MW) | Thermal | 3.8 | 3.72 | 3.64 | 3.53 | 3.28 | 3.08 | 1.55 | 0.31 | -0.6 | -2 | -3.24 | -4.44 | -6.05 | -7.77 | -9.65 | -18.93 | -32.1 | -43.76
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | Steady Progression | Headroom (MW) | Thermal | 3.8 | 3.77 | 3.75 | 3.74 | 3.71 | 3.68 | 3.68 | 3.63 | 3.38 | 2.11 | 1.84 | 1.5 | 0.93 | 0.53 | 0.11 | -0.51 | -1.53 | -2.71
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | System Transformation | Headroom (MW) | Thermal | 3.8 | 3.75 | 3.71 | 3.66 | 3.58 | 3.49 | 3.44 | 3.24 | 1.96 | 1.26 | 0.4 | -0.46 | -1.29 | -1.95 | -2.71 | -5.31 | -10.02 | -14.41
Enderby 132kV | Coalville | NAILSTONE 33 11kV S STN | Primary | 11 | -1.3617 | 52.6763 | WPD Best View | Headroom (MW) | Thermal | 3.8 | 3.73 | 3.63 | 3.52 | 3.27 | 3.04 | 1.61 | -1.14 | -3.18 | -5.09 | -7.19 | -9.26 | -11.3 | -13.45 | -15.87 | -27.07 | -41.83 | -56.57
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Consumer Transformation | Headroom (MW) | Thermal | 5.66 | 5.56 | 5.47 | 5.36 | 5.11 | 4.9 | 4.69 | 4.19 | 3.61 | 2.98 | 2.17 | 1.23 | 0.21 | -0.72 | -1.87 | -6.4 | -9.78 | -13.8
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Leading the Way | Headroom (MW) | Thermal | 5.66 | 5.56 | 5.46 | 5.35 | 5.09 | 4.85 | 4.63 | 4.46 | 4.28 | 4.11 | 3.92 | 3.73 | 2.9 | 2.1 | 1.24 | -3.73 | -7.91 | -10.85
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | Steady Progression | Headroom (MW) | N/A | 5.66 | 5.62 | 5.59 | 5.57 | 5.54 | 5.51 | 5.47 | 5.37 | 5.26 | 5.12 | 4.94 | 4.72 | 4.22 | 3.74 | 3.09 | 2.27 | 1.23 | 0.01
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | System Transformation | Headroom (MW) | Thermal | 5.66 | 5.59 | 5.54 | 5.48 | 5.39 | 5.29 | 5.18 | 4.77 | 4.26 | 3.7 | 2.97 | 2.12 | 1.22 | 0.42 | -0.6 | -3.2 | -5.66 | -8.53
Enderby 132kV | Coalville | OSBASTON 33 11kV S STN | Primary | 11 | -1.3777 | 52.629 | WPD Best View | Headroom (MW) | Thermal | 5.66 | 5.56 | 5.47 | 5.36 | 5.11 | 4.9 | 4.69 | 4.19 | 3.61 | 2.98 | 2.17 | 1.23 | 0.21 | -0.72 | -1.87 | -6.4 | -9.78 | -13.8
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Consumer Transformation | Headroom (MW) | Thermal | 4.13 | 4.05 | 3.98 | 3.91 | 3.75 | 3.6 | 3.45 | 2.89 | 2.22 | 1.47 | 0.49 | -0.64 | -1.87 | -3 | -4.4 | -7.49 | -10.74 | -14.7
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Leading the Way | Headroom (MW) | Thermal | 4.13 | 4.05 | 3.98 | 3.89 | 3.73 | 3.56 | 3.4 | 3.24 | 3.08 | 2.93 | 2.8 | 2.67 | 1.7 | 0.77 | -0.21 | -3.92 | -8.05 | -10.04
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | Steady Progression | Headroom (MW) | Thermal | 4.13 | 4.08 | 4.06 | 4.03 | 4.01 | 3.97 | 3.94 | 3.8 | 3.67 | 3.5 | 3.27 | 2.99 | 2.33 | 1.69 | 0.82 | -0.3 | -1.6 | -2.97
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | System Transformation | Headroom (MW) | Thermal | 4.13 | 4.07 | 4.02 | 3.98 | 3.91 | 3.83 | 3.75 | 3.25 | 2.62 | 1.91 | 0.98 | -0.1 | -1.27 | -2.31 | -3.62 | -5.94 | -8.61 | -11.84
Enderby 132kV | Coalville | WORTHINGTON 33 11kV S STN | Primary | 11 | -1.3794 | 52.7825 | WPD Best View | Headroom (MW) | Thermal | 4.13 | 4.05 | 3.98 | 3.91 | 3.75 | 3.6 | 3.45 | 2.89 | 2.22 | 1.47 | 0.49 | -0.64 | -1.87 | -3 | -4.4 | -7.49 | -10.74 | -14.7
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Consumer Transformation | Headroom (MW) | Thermal | 4.55 | 4.18 | 3.86 | 3.47 | 2.63 | 2.03 | -0.4 | -3.62 | -6.19 | -8.4 | -10.47 | -12.49 | -14.54 | -16.69 | -19.07 | -31.49 | -44.59 | -58.53
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Leading the Way | Headroom (MW) | Thermal | 4.55 | 4.16 | 3.83 | 3.44 | 2.56 | 2 | 0.07 | -1.58 | -2.89 | -4.46 | -6.01 | -7.5 | -9.44 | -11.49 | -13.72 | -25.68 | -17.55 | -69.65
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | Steady Progression | Headroom (MW) | Thermal | 4.55 | 4.33 | 4.2 | 4.09 | 3.96 | 4 | 2.64 | 1.37 | 0.04 | -1.9 | -3.06 | -4.09 | -4.91 | -5.5 | -5.99 | -6.51 | -8.03 | -10.21
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | System Transformation | Headroom (MW) | Thermal | 4.55 | 4.26 | 4.05 | 3.84 | 3.49 | 3.39 | 2.25 | 1.05 | -0.76 | -1.83 | -2.72 | -3.57 | -4.41 | -5.11 | -5.91 | -8.84 | 6.92 | -23.02
Enderby 132kV | Hinckley 132 11 | HINCKLEY 11kV S STN | Primary | 11 | -1.396 | 52.5289 | WPD Best View | Headroom (MW) | Thermal | 4.55 | 4.19 | 3.89 | 3.55 | 2.77 | 2.35 | 0.96 | -0.34 | -1.58 | -3.23 | -3.87 | -4.55 | -5.45 | -6.28 | -7.18 | -11.7 | -15.1 | -18.53
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Consumer Transformation | Headroom (MW) | Thermal | 16.42 | 16.29 | 16.21 | 16.13 | 15.97 | 15.6 | 15.11 | 14.62 | 14.13 | 13.61 | 13.09 | 12.54 | 12.03 | 11.55 | 11.04 | 7.49 | 3.11 | -1.76
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Leading the Way | Headroom (MW) | Thermal | 16.42 | 16.28 | 16.2 | 16.1 | 15.91 | 15.52 | 15 | 14.48 | 13.94 | 13.34 | 12.72 | 12.05 | 11.43 | 10.86 | 10.25 | 6.34 | 1.32 | -5.28
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | Steady Progression | Headroom (MW) | N/A | 16.42 | 16.33 | 16.29 | 16.25 | 16.21 | 16.21 | 16.2 | 16.19 | 16.19 | 16.17 | 16.16 | 16.13 | 16.1 | 16.07 | 16.03 | 15.83 | 15.34 | 14.62
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | System Transformation | Headroom (MW) | N/A | 16.42 | 16.31 | 16.25 | 16.2 | 16.12 | 16.1 | 16.07 | 16.03 | 15.79 | 15.51 | 15.24 | 14.96 | 14.72 | 14.53 | 14.35 | 13.33 | 11.19 | 9.08
Enderby 132kV | Leicester | BRAUNSTONE 33 11kV S STN | Primary | 11 | -1.1626 | 52.61 | WPD Best View | Headroom (MW) | Thermal | 16.42 | 16.29 | 16.21 | 16.13 | 15.97 | 15.61 | 15.13 | 14.64 | 14.16 | 13.65 | 13.14 | 12.59 | 12.09 | 11.61 | 11.12 | 7.79 | 3.48 | -1.3
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Consumer Transformation | Headroom (MW) | Thermal | 10.91 | 10.8 | 10.75 | 10.66 | 10.39 | 10.03 | 9.85 | 9.67 | 9.53 | 9.41 | 9.31 | 9.07 | 8.83 | 8.57 | 8.3 | 6.25 | 2.9 | -0.92
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Leading the Way | Headroom (MW) | Thermal | 10.91 | 10.8 | 10.75 | 10.65 | 10.34 | 9.95 | 9.82 | 9.7 | 9.62 | 9.55 | 9.47 | 9.15 | 8.83 | 8.47 | 8.1 | 5.46 | 1.55 | -3.65
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | Steady Progression | Headroom (MW) | N/A | 10.91 | 10.83 | 10.81 | 10.76 | 10.71 | 10.67 | 10.69 | 10.74 | 10.8 | 10.88 | 10.96 | 10.99 | 11.02 | 11.05 | 11.08 | 11.18 | 10.83 | 10.33
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | System Transformation | Headroom (MW) | N/A | 10.91 | 10.82 | 10.79 | 10.72 | 10.64 | 10.58 | 10.62 | 10.62 | 10.63 | 10.67 | 10.73 | 10.66 | 10.6 | 10.55 | 10.51 | 10.2 | 8.57 | 6.87
Enderby 132kV | Leicester | Hockley Farm Road 33 11kV S STN | Primary | 11 | -1.1877 | 52.6304 | WPD Best View | Headroom (MW) | Thermal | 10.91 | 10.8 | 10.75 | 10.66 | 10.39 | 10.03 | 9.85 | 9.67 | 9.53 | 9.41 | 9.31 | 9.07 | 8.83 | 8.57 | 8.3 | 6.25 | 2.9 | -0.92
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Consumer Transformation | Headroom (MW) | N/A | 19.1 | 19.01 | 18.94 | 18.89 | 18.72 | 18.51 | 18.29 | 18.07 | 17.87 | 17.68 | 17.49 | 17.31 | 17.12 | 16.92 | 16.71 | 15.16 | 13.02 | 10.58
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Leading the Way | Headroom (MW) | N/A | 19.1 | 19 | 18.93 | 18.87 | 18.68 | 18.48 | 18.24 | 18.02 | 17.8 | 17.59 | 17.38 | 17.16 | 16.93 | 16.67 | 16.39 | 14.55 | 12.11 | 8.83
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | Steady Progression | Headroom (MW) | N/A | 19.1 | 19.02 | 18.98 | 18.95 | 18.94 | 18.92 | 18.89 | 18.86 | 18.83 | 18.79 | 18.76 | 18.72 | 18.69 | 18.65 | 18.61 | 18.42 | 18.17 | 17.88
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | System Transformation | Headroom (MW) | N/A | 19.1 | 19.01 | 18.96 | 18.92 | 18.89 | 18.88 | 18.76 | 18.65 | 18.53 | 18.43 | 18.33 | 18.24 | 18.16 | 18.09 | 18.02 | 17.57 | 16.5 | 15.44
Enderby 132kV | Leicester | JUPITER 33 11kV S STN | Primary | 11 | -1.1645 | 52.6265 | WPD Best View | Headroom (MW) | N/A | 19.1 | 19.01 | 18.94 | 18.89 | 18.72 | 18.51 | 18.29 | 18.07 | 17.87 | 17.68 | 17.49 | 17.31 | 17.12 | 16.92 | 16.71 | 15.16 | 13.02 | 10.58
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Consumer Transformation | Headroom (MW) | Fault level | 0.34029 | 0.27766 | 0.20205 | 0.097095 | -0.19463 | -0.49312 | -0.79443 | -1.1036 | -1.3863 | -1.6775 | -1.998 | -2.3179 | -2.6424 | -2.9696 | -3.2975 | -4.8215 | -6.4421 | -8.0401
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Leading the Way | Headroom (MW) | Fault level | 0.46571 | 0.37691 | 0.27034 | 0.1213 | -0.27949 | -0.7073 | -1.1351 | -1.5799 | -1.9761 | -2.3884 | -2.8456 | -3.3028 | -3.7669 | -4.2341 | -4.7067 | -6.9284 | -9.1362 | -11.4907
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | Steady Progression | Headroom (MW) | Fault level | 0.18772 | 0.18056 | 0.17465 | 0.16749 | 0.15846 | 0.13699 | 0.11271 | 0.084691 | 0.0601 | 0.028972 | -0.0034006 | -0.035151 | -0.066901 | -0.098652 | -0.12947 | -0.17678 | -0.34332 | -0.5167
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | System Transformation | Headroom (MW) | Fault level | 0.26826 | 0.2429 | 0.21443 | 0.17751 | 0.099227 | 3.3524e-05 | -0.11784 | -0.24017 | -0.3487 | -0.46168 | -0.58668 | -0.71167 | -0.83933 | -0.96877 | -1.0995 | -1.6502 | -2.2765 | -2.9513
Enderby 132kV | Leicester | LEICESTER 11kV S STN | Primary | 11 | -1.1435 | 52.6468 | WPD Best View | Headroom (MW) | Fault level | 0.27969 | 0.22821 | 0.16607 | 0.079805 | -0.15997 | -0.40531 | -0.65297 | -0.90712 | -1.1395 | -1.3788 | -1.6422 | -1.9052 | -2.1718 | -2.4408 | -2.7103 | -3.963 | -5.2949 | -6.6084
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Consumer Transformation | Headroom (MW) | N/A | 24.28 | 24.2 | 24.18 | 24.13 | 24 | 23.94 | 23.87 | 23.64 | 23.38 | 23.07 | 22.74 | 22.4 | 22.05 | 21.8 | 21.56 | 20.09 | 18.95 | 17.79
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Leading the Way | Headroom (MW) | N/A | 24.28 | 24.2 | 24.18 | 24.13 | 23.95 | 23.88 | 23.8 | 23.53 | 23.25 | 22.87 | 22.51 | 22.13 | 21.72 | 21.47 | 21.24 | 20.1 | 18.93 | 17.62
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | Steady Progression | Headroom (MW) | N/A | 24.28 | 24.21 | 24.18 | 24.14 | 24.07 | 24.03 | 23.98 | 23.94 | 23.92 | 23.89 | 23.86 | 23.82 | 23.8 | 23.76 | 23.73 | 23.49 | 23.2 | 22.92
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | System Transformation | Headroom (MW) | N/A | 24.28 | 24.21 | 24.19 | 24.14 | 24.04 | 23.99 | 23.93 | 23.87 | 23.85 | 23.78 | 23.58 | 23.36 | 23.13 | 22.98 | 22.84 | 22.18 | 21.54 | 20.86
Enderby 132kV | Leicester | MANSFIELD ST 33 11kV S STN | Primary | 11 | -1.1334 | 52.6388 | WPD Best View | Headroom (MW) | N/A | 24.28 | 24.2 | 24.18 | 24.13 | 24 | 23.94 | 23.87 | 23.64 | 23.38 | 23.07 | 22.74 | 22.4 | 22.05 | 21.8 | 21.56 | 20.09 | 18.95 | 17.79
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Consumer Transformation | Headroom (MW) | N/A | 24.59 | 24.46 | 24.4 | 24.34 | 24.15 | 24.09 | 24.02 | 23.95 | 23.87 | 23.78 | 23.69 | 23.54 | 23.29 | 23.03 | 22.77 | 21.05 | 19.07 | 16.94
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Leading the Way | Headroom (MW) | N/A | 24.59 | 24.45 | 24.38 | 24.32 | 24.06 | 23.99 | 23.92 | 23.84 | 23.74 | 23.64 | 23.53 | 23.34 | 23.08 | 22.8 | 22.51 | 20.73 | 18.56 | 15.91
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | Steady Progression | Headroom (MW) | N/A | 24.59 | 24.48 | 24.43 | 24.38 | 24.29 | 24.24 | 24.18 | 24.13 | 24.08 | 24.02 | 23.96 | 23.91 | 23.85 | 23.8 | 23.74 | 23.47 | 23.16 | 22.83
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | System Transformation | Headroom (MW) | N/A | 24.59 | 24.48 | 24.42 | 24.36 | 24.23 | 24.18 | 24.12 | 24.06 | 24 | 23.93 | 23.87 | 23.81 | 23.74 | 23.67 | 23.6 | 23.25 | 22.52 | 21.43
Enderby 132kV | Leicester | REDCROSS STREET 33 11kV S STN | Primary | 11 | -1.1384 | 52.634 | WPD Best View | Headroom (MW) | N/A | 24.59 | 24.46 | 24.4 | 24.34 | 24.15 | 24.09 | 24.02 | 23.95 | 23.87 | 23.78 | 23.69 | 23.54 | 23.29 | 23.03 | 22.77 | 21.05 | 19.07 | 16.94
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Consumer Transformation | Headroom (MW) | N/A | 15.73 | 15.63 | 15.59 | 15.54 | 15.48 | 15.34 | 15.05 | 14.75 | 14.44 | 14.11 | 13.8 | 13.48 | 13.13 | 12.74 | 12.32 | 9.16 | 7.33 | 5.41
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Leading the Way | Headroom (MW) | N/A | 15.73 | 15.63 | 15.59 | 15.53 | 15.46 | 15.25 | 14.91 | 14.53 | 14.12 | 13.68 | 13.3 | 12.89 | 12.44 | 11.96 | 11.45 | 8.35 | 6.32 | 4.1
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | Steady Progression | Headroom (MW) | N/A | 15.73 | 15.65 | 15.61 | 15.58 | 15.56 | 15.53 | 15.5 | 15.47 | 15.44 | 15.4 | 15.36 | 15.33 | 15.29 | 15.25 | 15.2 | 15 | 14.52 | 14.04
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | System Transformation | Headroom (MW) | N/A | 15.73 | 15.64 | 15.6 | 15.56 | 15.53 | 15.46 | 15.37 | 15.29 | 15.12 | 14.92 | 14.74 | 14.54 | 14.34 | 14.1 | 13.85 | 12.49 | 11.56 | 10.68
Enderby 132kV | Leicester East | HAMILTON 33 11kV S STN | Primary | 11 | -1.0785 | 52.6589 | WPD Best View | Headroom (MW) | N/A | 15.73 | 15.63 | 15.59 | 15.54 | 15.48 | 15.34 | 15.05 | 14.75 | 14.44 | 14.11 | 13.8 | 13.48 | 13.13 | 12.74 | 12.32 | 9.16 | 7.33 | 5.41
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Consumer Transformation | Headroom (MW) | N/A | 12.4 | 12.31 | 12.27 | 12.21 | 12.12 | 12.17 | 12.12 | 12.07 | 12.03 | 11.98 | 11.94 | 11.89 | 11.84 | 11.8 | 11.75 | 11.38 | 10.96 | 10.44
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Leading the Way | Headroom (MW) | N/A | 12.4 | 12.31 | 12.26 | 12.21 | 12.08 | 12.19 | 12.15 | 12.1 | 12.05 | 12 | 11.94 | 11.88 | 11.81 | 11.74 | 11.68 | 14.52 | 8.32 | 6.72
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | Steady Progression | Headroom (MW) | N/A | 12.4 | 12.32 | 12.28 | 12.23 | 12.18 | 12.22 | 12.16 | 12.12 | 12.09 | 12.06 | 12.02 | 11.99 | 11.95 | 11.92 | 11.89 | 11.72 | 11.53 | 11.3
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | System Transformation | Headroom (MW) | N/A | 12.4 | 12.31 | 12.27 | 12.23 | 12.15 | 12.21 | 12.16 | 12.13 | 12.09 | 12.05 | 12.01 | 11.98 | 11.94 | 11.9 | 11.86 | 13.49 | 9.9 | 9.65
Enderby 132kV | Leicester East | HIGHFIELDS 33 11kV S STN | Primary | 11 | -1.1214 | 52.6293 | WPD Best View | Headroom (MW) | N/A | 12.4 | 12.31 | 12.27 | 12.21 | 12.12 | 12.17 | 12.12 | 12.07 | 12.03 | 11.98 | 11.94 | 11.89 | 11.84 | 11.8 | 11.75 | 11.38 | 10.96 | 10.44
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Consumer Transformation | Headroom (MW) | N/A | 15.84 | 15.69 | 15.61 | 15.52 | 15.01 | 14.68 | 14.37 | 14.08 | 13.8 | 13.54 | 13.28 | 13.03 | 12.77 | 12.51 | 12.22 | 10.01 | 7.19 | 4.04
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Leading the Way | Headroom (MW) | N/A | 15.84 | 15.67 | 15.59 | 15.48 | 14.86 | 14.52 | 14.2 | 13.9 | 13.6 | 13.31 | 13.02 | 12.74 | 12.43 | 12.11 | 11.73 | 9.36 | 6.22 | 2.13
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | Steady Progression | Headroom (MW) | N/A | 15.84 | 15.72 | 15.67 | 15.61 | 15.5 | 15.44 | 15.39 | 15.33 | 15.28 | 15.22 | 15.15 | 15.09 | 15.04 | 15.01 | 14.96 | 14.7 | 14.38 | 13.95
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | System Transformation | Headroom (MW) | N/A | 15.84 | 15.71 | 15.64 | 15.57 | 15.37 | 15.21 | 15.04 | 14.87 | 14.72 | 14.59 | 14.46 | 14.34 | 14.24 | 14.15 | 14.06 | 13.53 | 12.16 | 10.8
Enderby 132kV | Leicester East | LEICESTER EAST 6 6kV S STN | Primary | 6.6 | -1.1017 | 52.6295 | WPD Best View | Headroom (MW) | N/A | 15.84 | 15.69 | 15.61 | 15.52 | 15.01 | 14.68 | 14.37 | 14.08 | 13.8 | 13.54 | 13.28 | 13.03 | 12.77 | 12.51 | 12.22 | 10.01 | 7.19 | 4.04
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Consumer Transformation | Headroom (MW) | Thermal | 16.57 | 16.42 | 16.34 | 16.24 | 15.79 | 15.34 | 14.9 | 14.49 | 14.1 | 13.72 | 13.39 | 13.06 | 12.71 | 12.35 | 11.95 | 8.74 | 4.5 | -0.16
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Leading the Way | Headroom (MW) | Thermal | 16.57 | 16.4 | 16.31 | 16.2 | 15.66 | 15.17 | 14.7 | 14.26 | 13.83 | 13.42 | 13.02 | 12.62 | 12.19 | 11.72 | 11.18 | 7.57 | 2.75 | -3.39
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | Steady Progression | Headroom (MW) | N/A | 16.57 | 16.46 | 16.41 | 16.35 | 16.25 | 16.19 | 16.14 | 16.08 | 16.02 | 15.96 | 15.9 | 15.83 | 15.76 | 15.69 | 15.63 | 15.33 | 14.87 | 14.14
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | System Transformation | Headroom (MW) | N/A | 16.57 | 16.44 | 16.38 | 16.3 | 16.14 | 16.06 | 15.83 | 15.61 | 15.39 | 15.19 | 15.02 | 14.87 | 14.74 | 14.62 | 14.51 | 13.66 | 11.65 | 9.69
Enderby 132kV | Leicester East | SALUTATION 33 6 6kV S STN | Primary | 6.6 | -1.099 | 52.6465 | WPD Best View | Headroom (MW) | Thermal | 16.57 | 16.42 | 16.34 | 16.24 | 15.79 | 15.34 | 14.9 | 14.49 | 14.1 | 13.72 | 13.39 | 13.06 | 12.71 | 12.35 | 11.95 | 8.74 | 4.5 | -0.16
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Consumer Transformation | Headroom (MW) | Thermal | 13.8 | 13.68 | 13.59 | 13.49 | 13.26 | 12.79 | 12.33 | 11.89 | 11.49 | 11.11 | 10.72 | 10.36 | 9.98 | 9.56 | 9.12 | 5.83 | 1.78 | -2.75
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Leading the Way | Headroom (MW) | Thermal | 13.8 | 13.67 | 13.56 | 13.45 | 13.18 | 12.66 | 12.15 | 11.68 | 11.23 | 10.79 | 10.34 | 9.89 | 9.42 | 8.91 | 8.33 | 4.54 | -0.15 | -6.29
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | Steady Progression | Headroom (MW) | N/A | 13.8 | 13.72 | 13.67 | 13.62 | 13.57 | 13.53 | 13.48 | 13.44 | 13.4 | 13.35 | 13.3 | 13.25 | 13.19 | 13.14 | 13.08 | 12.83 | 12.38 | 11.68
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | System Transformation | Headroom (MW) | N/A | 13.8 | 13.69 | 13.63 | 13.56 | 13.47 | 13.39 | 13.31 | 13.16 | 12.94 | 12.74 | 12.55 | 12.38 | 12.22 | 12.09 | 11.96 | 10.88 | 9.01 | 7.19
Enderby 132kV | Leicester East | STONEYGATE 33 6 6kV S STN | Primary | 6.6 | -1.1014 | 52.6161 | WPD Best View | Headroom (MW) | Thermal | 13.8 | 13.68 | 13.59 | 13.49 | 13.33 | 12.91 | 12.48 | 12.08 | 11.7 | 11.35 | 11 | 10.66 | 10.32 | 9.95 | 9.54 | 6.66 | 2.88 | -1.3
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Consumer Transformation | Headroom (MW) | N/A | 12.28 | 12.09 | 11.95 | 11.79 | 11.39 | 11.16 | 10.99 | 10.8 | 10.63 | 10.47 | 10.32 | 10.19 | 10.06 | 9.9 | 9.71 | 7.1 | 4.8 | 2.25
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Leading the Way | Headroom (MW) | Thermal | 12.28 | 12.07 | 11.93 | 11.76 | 11.29 | 11.08 | 10.93 | 10.76 | 10.61 | 10.44 | 10.27 | 10.13 | 9.93 | 9.7 | 9.44 | 5.55 | 2.92 | -0.48
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | Steady Progression | Headroom (MW) | N/A | 12.28 | 12.14 | 12.07 | 12 | 11.9 | 11.87 | 11.84 | 11.79 | 11.77 | 11.73 | 11.7 | 11.68 | 11.67 | 11.68 | 11.69 | 11.8 | 11.51 | 10.92
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | System Transformation | Headroom (MW) | N/A | 12.28 | 12.12 | 12.02 | 11.91 | 11.71 | 11.62 | 11.55 | 11.46 | 11.38 | 11.31 | 11.23 | 11.18 | 11.13 | 11.1 | 11.09 | 9.81 | 8.65 | 7.45
Enderby 132kV | Leicester East | THURMASTON 33 11kV S STN | Primary | 11 | -1.0941 | 52.6644 | WPD Best View | Headroom (MW) | N/A | 12.28 | 12.09 | 11.95 | 11.79 | 11.39 | 11.16 | 10.99 | 10.8 | 10.63 | 10.47 | 10.32 | 10.19 | 10.06 | 9.9 | 9.71 | 7.1 | 4.8 | 2.25
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Consumer Transformation | Headroom (MW) | Thermal | 11.25 | 11 | 10.76 | 10.47 | 9.88 | 9.24 | 8.59 | 7.69 | 6.72 | 5.76 | 4.71 | 3.54 | 2.31 | 1.17 | -0.18 | -5.67 | -12.39 | -19.6
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Leading the Way | Headroom (MW) | Thermal | 11.25 | 10.99 | 10.74 | 10.43 | 9.8 | 9.05 | 8.29 | 7.5 | 6.7 | 5.95 | 5.32 | 4.65 | 3.46 | 2.31 | 1.07 | -5.02 | -13.37 | -21.09
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | Steady Progression | Headroom (MW) | N/A | 11.25 | 11.13 | 11.06 | 10.99 | 10.93 | 10.84 | 10.74 | 10.58 | 10.43 | 10.27 | 10.06 | 9.83 | 9.38 | 8.94 | 8.38 | 7.63 | 6.37 | 4.59
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | System Transformation | Headroom (MW) | Thermal | 11.25 | 11.07 | 10.93 | 10.77 | 10.55 | 10.23 | 9.86 | 9.24 | 8.54 | 7.83 | 7.06 | 6.2 | 5.3 | 4.47 | 3.47 | 1.17 | -2.97 | -6.99
Enderby 132kV | Leicester East | THURNBY 33 11kV S STN | Primary | 11 | -1.0525 | 52.6348 | WPD Best View | Headroom (MW) | Thermal | 11.25 | 11.01 | 10.78 | 10.49 | 9.93 | 9.31 | 8.68 | 7.79 | 6.84 | 5.88 | 4.86 | 3.7 | 2.49 | 1.37 | 0.04 | -5.26 | -11.79 | -18.78
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Consumer Transformation | Headroom (MW) | N/A | 21.54 | 21.35 | 21.21 | 21.08 | 20.77 | 20.51 | 20.45 | 20.42 | 20.24 | 20.08 | 19.93 | 19.78 | 19.63 | 19.46 | 19.27 | 17.84 | 15.9 | 13.76
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Leading the Way | Headroom (MW) | N/A | 21.54 | 21.34 | 21.19 | 21.07 | 20.72 | 20.46 | 20.47 | 20.54 | 20.35 | 20.17 | 19.99 | 19.8 | 19.6 | 19.37 | 19.11 | 17.26 | 16.56 | 9.99
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | Steady Progression | Headroom (MW) | N/A | 21.54 | 21.4 | 21.32 | 21.28 | 21.2 | 21.12 | 21.13 | 21.19 | 21.16 | 21.13 | 21.11 | 21.09 | 21.08 | 21.07 | 21.07 | 21.12 | 20.83 | 20.19
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | System Transformation | Headroom (MW) | N/A | 21.54 | 21.38 | 21.27 | 21.19 | 21.04 | 20.91 | 20.95 | 21.01 | 20.92 | 20.84 | 20.78 | 20.72 | 20.67 | 20.63 | 20.59 | 20.29 | 20.81 | 17.53
Enderby 132kV | Leicester North | BEAUMONT LEYS 33 11kV S STN | Primary | 11 | -1.1544 | 52.6694 | WPD Best View | Headroom (MW) | N/A | 21.54 | 21.35 | 21.21 | 21.08 | 20.77 | 20.51 | 20.45 | 20.42 | 20.24 | 20.08 | 19.93 | 19.78 | 19.63 | 19.46 | 19.27 | 17.84 | 15.9 | 13.76
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Consumer Transformation | Headroom (MW) | N/A | 14.86 | 14.89 | 15.13 | 15.3 | 15.23 | 15.05 | 15.03 | 14.82 | 14.63 | 14.29 | 13.95 | 13.57 | 13.2 | 12.78 | 12.33 | 8.91 | 4.75 | 0.14
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Leading the Way | Headroom (MW) | Thermal | 14.86 | 14.9 | 15.18 | 15.43 | 15.4 | 15.24 | 15.27 | 15.02 | 14.78 | 14.27 | 13.8 | 13.31 | 12.79 | 12.22 | 11.6 | 7.73 | 2.94 | -3.08
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | Steady Progression | Headroom (MW) | N/A | 14.86 | 14.95 | 15.28 | 15.57 | 15.89 | 16.08 | 16.28 | 16.41 | 16.56 | 16.63 | 16.69 | 16.75 | 16.78 | 16.8 | 16.81 | 16.86 | 16.29 | 15.51
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | System Transformation | Headroom (MW) | N/A | 14.86 | 14.94 | 15.26 | 15.53 | 15.76 | 15.84 | 16.04 | 16.06 | 16.09 | 15.97 | 15.85 | 15.72 | 15.59 | 15.47 | 15.34 | 14.66 | 12.64 | 10.57
Enderby 132kV | Leicester North | BIRSTALL 33 11kV S STN | Primary | 11 | -1.1295 | 52.6697 | WPD Best View | Headroom (MW) | N/A | 14.86 | 14.89 | 15.13 | 15.3 | 15.23 | 15.05 | 15.03 | 14.82 | 14.63 | 14.29 | 13.95 | 13.57 | 13.2 | 12.78 | 12.33 | 8.91 | 4.75 | 0.14
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Consumer Transformation | Headroom (MW) | Thermal | 14.39 | 14.16 | 13.96 | 13.73 | 13.26 | 12.85 | 12.47 | 12.12 | 11.8 | 11.53 | 11.26 | 10.94 | 10.55 | 10.15 | 9.77 | 6.88 | 2.45 | -2.11
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Leading the Way | Headroom (MW) | Thermal | 14.39 | 14.14 | 13.93 | 13.69 | 13.19 | 12.76 | 12.36 | 11.99 | 11.68 | 11.38 | 11.04 | 10.64 | 10.15 | 9.63 | 9.1 | 5.53 | 0.15 | -6.2
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | Steady Progression | Headroom (MW) | N/A | 14.39 | 14.26 | 14.19 | 14.13 | 14.08 | 14.02 | 13.95 | 13.89 | 13.83 | 13.78 | 13.74 | 13.7 | 13.67 | 13.65 | 13.64 | 13.71 | 13.22 | 12.3
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | System Transformation | Headroom (MW) | N/A | 14.39 | 14.21 | 14.09 | 13.96 | 13.78 | 13.61 | 13.42 | 13.23 | 13.06 | 12.92 | 12.79 | 12.65 | 12.51 | 12.4 | 12.31 | 11.51 | 9.23 | 7.26
Enderby 132kV | Leicester North | GROBY ROAD 33 11kV S STN | Primary | 11 | -1.1729 | 52.6508 | WPD Best View | Headroom (MW) | Thermal | 14.39 | 14.16 | 13.96 | 13.73 | 13.26 | 12.85 | 12.47 | 12.12 | 11.8 | 11.53 | 11.26 | 10.94 | 10.55 | 10.15 | 9.77 | 6.88 | 2.45 | -2.11
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Consumer Transformation | Headroom (MW) | N/A | 59.83 | 59.73 | 59.63 | 59.51 | 59.21 | 58.96 | 58.72 | 58.5 | 58.3 | 58.13 | 57.96 | 57.77 | 57.59 | 57.39 | 57.19 | 55.53 | 53.16 | 50.51
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Leading the Way | Headroom (MW) | N/A | 59.83 | 59.72 | 59.61 | 59.49 | 59.14 | 58.88 | 58.63 | 58.41 | 58.21 | 58.02 | 57.82 | 57.61 | 57.39 | 57.14 | 56.86 | 54.86 | 52.14 | 48.51
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | Steady Progression | Headroom (MW) | N/A | 59.83 | 59.79 | 59.76 | 59.74 | 59.72 | 59.68 | 59.64 | 59.61 | 59.57 | 59.54 | 59.51 | 59.49 | 59.47 | 59.46 | 59.46 | 59.48 | 59.22 | 58.73
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | System Transformation | Headroom (MW) | N/A | 59.83 | 59.76 | 59.7 | 59.64 | 59.53 | 59.42 | 59.3 | 59.19 | 59.08 | 58.99 | 58.91 | 58.84 | 58.8 | 58.75 | 58.69 | 58.26 | 57.15 | 56.08
Enderby 132kV | Leicester North | LEICESTER NORTH 11kV S STN | Primary | 11 | -1.1433 | 52.6467 | WPD Best View | Headroom (MW) | N/A | 59.83 | 59.73 | 59.63 | 59.51 | 59.21 | 58.96 | 58.72 | 58.5 | 58.3 | 58.13 | 57.96 | 57.77 | 57.59 | 57.39 | 57.19 | 55.53 | 53.16 | 50.51
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Consumer Transformation | Headroom (MW) | N/A | 15.57 | 15.49 | 15.45 | 15.42 | 15.31 | 15.31 | 15.27 | 15.23 | 15.11 | 14.92 | 14.74 | 14.56 | 14.37 | 14.18 | 13.98 | 12.63 | 11.34 | 10
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Leading the Way | Headroom (MW) | N/A | 15.57 | 15.48 | 15.44 | 15.41 | 15.24 | 15.26 | 15.22 | 15.17 | 14.97 | 14.77 | 14.58 | 14.38 | 14.18 | 13.98 | 13.76 | 14.02 | 9.82 | 7.7
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | Steady Progression | Headroom (MW) | N/A | 15.57 | 15.51 | 15.47 | 15.44 | 15.42 | 15.42 | 15.38 | 15.36 | 15.33 | 15.29 | 15.26 | 15.23 | 15.2 | 15.16 | 15.12 | 14.94 | 14.71 | 14.47
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | System Transformation | Headroom (MW) | N/A | 15.57 | 15.5 | 15.47 | 15.43 | 15.38 | 15.39 | 15.35 | 15.32 | 15.29 | 15.25 | 15.21 | 15.17 | 15.12 | 15.07 | 15.02 | 15.59 | 13.14 | 12.27
Enderby 132kV | Leicester North | LERO 33 6 6kV S STN | Primary | 6.6 | -1.1276 | 52.6444 | WPD Best View | Headroom (MW) | N/A | 15.57 | 15.49 | 15.45 | 15.42 | 15.31 | 15.31 | 15.27 | 15.23 | 15.11 | 14.92 | 14.74 | 14.56 | 14.37 | 14.18 | 13.98 | 12.63 | 11.34 | 10
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Consumer Transformation | Headroom (MW) | N/A | 22.19 | 21.93 | 21.69 | 21.41 | 20.74 | 20.2 | 19.69 | 19.22 | 18.79 | 18.41 | 18.06 | 17.63 | 17.19 | 16.74 | 16.26 | 12.64 | 7.03 | 1.46
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Leading the Way | Headroom (MW) | Thermal | 22.19 | 21.9 | 21.66 | 21.36 | 20.62 | 20.05 | 19.51 | 19.02 | 18.57 | 18.18 | 17.73 | 17.22 | 16.69 | 16.11 | 15.47 | 11.11 | 4.12 | -3.5
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | Steady Progression | Headroom (MW) | N/A | 22.19 | 22.05 | 21.97 | 21.9 | 21.81 | 21.72 | 21.62 | 21.52 | 21.43 | 21.34 | 21.26 | 21.19 | 21.14 | 21.12 | 21.1 | 21.14 | 20.55 | 19.45
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | System Transformation | Headroom (MW) | N/A | 22.19 | 21.99 | 21.85 | 21.7 | 21.42 | 21.18 | 20.9 | 20.65 | 20.42 | 20.21 | 20.02 | 19.87 | 19.73 | 19.62 | 19.47 | 18.49 | 15.52 | 13.12
Enderby 132kV | Wigston 132 11 | WIGSTON 11kV S STN | Primary | 11 | -1.1445 | 52.5775 | WPD Best View | Headroom (MW) | N/A | 22.19 | 21.94 | 21.73 | 21.47 | 20.9 | 20.44 | 19.99 | 19.57 | 19.2 | 18.86 | 18.55 | 18.22 | 17.84 | 17.46 | 17.06 | 14.23 | 9.31 | 4.54
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Consumer Transformation | Headroom (MW) | Thermal | 9.77 | 9.63 | 9.53 | 9.42 | 9.11 | 8.87 | 8.63 | 8.39 | 8.14 | 7.91 | 7.55 | 7.16 | 6.75 | 6.35 | 5.86 | 3.57 | 0.34 | -2.81
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Leading the Way | Headroom (MW) | Thermal | 9.77 | 9.62 | 9.52 | 9.41 | 9.06 | 8.8 | 8.56 | 8.33 | 8.1 | 7.9 | 7.67 | 7.45 | 7.06 | 6.65 | 6.2 | 3.57 | -0.16 | -3.57
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | Steady Progression | Headroom (MW) | N/A | 9.77 | 3.54 | 3.51 | 3.49 | 3.44 | 3.39 | 3.29 | 3.23 | 3.18 | 3.12 | 3.04 | 2.95 | 2.79 | 2.65 | 2.46 | 2.24 | 1.78 | 0.97
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | System Transformation | Headroom (MW) | N/A | 9.77 | 9.66 | 9.6 | 9.55 | 9.42 | 9.3 | 9.17 | 9.03 | 8.88 | 8.74 | 8.47 | 8.18 | 7.88 | 7.62 | 7.32 | 6.35 | 4.47 | 2.67
Enderby 132kV | Wigston 33 | ALLIANCE AND LEICESTER 33 11kV S STN | Primary | 11 | -1.2071 | 52.5829 | WPD Best View | Headroom (MW) | Thermal | 9.77 | 9.63 | 9.53 | 9.42 | 9.11 | 8.87 | 8.63 | 8.39 | 8.14 | 7.91 | 7.55 | 7.16 | 6.75 | 6.35 | 5.86 | 3.57 | 0.34 | -2.81
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Consumer Transformation | Headroom (MW) | Thermal | 14.17 | 14.03 | 13.91 | 13.75 | 13.35 | 13 | 12.65 | 12.18 | 11.7 | 11.21 | 10.68 | 10.12 | 9.52 | 8.92 | 8.21 | 5.2 | 1.65 | -2.38
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Leading the Way | Headroom (MW) | Thermal | 14.17 | 14.01 | 13.9 | 13.73 | 13.28 | 12.89 | 12.49 | 12.1 | 11.71 | 11.33 | 11.01 | 10.69 | 10.11 | 9.51 | 8.87 | 5.54 | 1.36 | -3.03
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | Steady Progression | Headroom (MW) | Thermal | 14.17 | 14.1 | 14.08 | 14.05 | 6.25 | 6.2 | 5.36 | 4.5 | 3.67 | 2.88 | 2.15 | 1.52 | 1.05 | 0.65 | 0.28 | -0.06 | -0.79 | -1.79
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | System Transformation | Headroom (MW) | N/A | 14.17 | 14.06 | 14.01 | 13.93 | 13.76 | 13.6 | 13.4 | 13.09 | 12.74 | 12.39 | 12 | 11.57 | 11.12 | 10.73 | 10.26 | 9.05 | 7 | 4.78
Enderby 132kV | Wigston 33 | WHETSTONE 33 11kV S STN | Primary | 11 | -1.1848 | 52.5677 | WPD Best View | Headroom (MW) | Thermal | 14.17 | 14.03 | 13.91 | 13.75 | 13.35 | 13 | 12.65 | 12.18 | 11.7 | 11.21 | 10.68 | 10.12 | 9.52 | 8.92 | 8.21 | 5.2 | 1.65 | -2.38
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Consumer Transformation | Headroom (MW) | Thermal | 22.09 | 21.67 | 21.27 | 20.77 | 19.64 | 18.73 | 17.88 | 17.07 | 16.33 | 15.7 | 14.98 | 14.23 | 13.47 | 12.67 | 11.84 | 5.92 | -2.36 | -11.62
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Leading the Way | Headroom (MW) | Thermal | 22.09 | 21.64 | 21.21 | 20.67 | 19.45 | 18.52 | 17.63 | 16.8 | 16.06 | 15.44 | 14.61 | 13.75 | 12.84 | 11.85 | 10.75 | 3.45 | -6.12 | -18.95
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | Steady Progression | Headroom (MW) | N/A | 22.09 | 21.91 | 21.81 | 21.72 | 21.62 | 21.51 | 21.39 | 21.27 | 21.17 | 21.09 | 20.99 | 20.91 | 20.87 | 20.84 | 20.84 | 20.47 | 19.27 | 17.48
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | System Transformation | Headroom (MW) | N/A | 22.09 | 21.8 | 21.57 | 21.32 | 20.89 | 20.53 | 20.12 | 19.72 | 19.37 | 19.09 | 18.78 | 18.5 | 18.26 | 18.03 | 17.77 | 15.97 | 12.07 | 8.36
Enderby 132kV | Wigston 33 | WIGSTON MAGNA 33 11kV S STN | Primary | 11 | -1.1021 | 52.5848 | WPD Best View | Headroom (MW) | N/A | 22.09 | 21.77 | 21.51 | 21.2 | 20.64 | 20.17 | 19.67 | 19.19 | 18.77 | 18.43 | 18.04 | 17.69 | 17.36 | 16.99 | 16.61 | 14.03 | 9.33 | 4.43
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Consumer Transformation | Headroom (MW) | N/A | 14.82 | 14.74 | 14.71 | 14.67 | 14.62 | 14.76 | 14.91 | 15.11 | 15.38 | 15.62 | 15.81 | 15.89 | 15.97 | 16.02 | 16.06 | 16.05 | 15.58 | 15.01
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Leading the Way | Headroom (MW) | N/A | 14.82 | 14.73 | 14.7 | 14.66 | 14.57 | 14.8 | 15.02 | 15.33 | 15.71 | 16.04 | 16.28 | 16.36 | 16.44 | 16.45 | 16.47 | 16.29 | 15.71 | 15.12
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | Steady Progression | Headroom (MW) | N/A | 14.82 | 14.75 | 14.72 | 14.69 | 14.67 | 14.78 | 14.86 | 14.98 | 15.15 | 15.33 | 15.5 | 15.63 | 15.78 | 15.89 | 15.99 | 16.45 | 16.29 | 16.01
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | System Transformation | Headroom (MW) | N/A | 14.82 | 14.75 | 14.71 | 14.68 | 14.65 | 14.79 | 14.94 | 15.14 | 15.41 | 15.67 | 15.9 | 16.03 | 16.17 | 16.26 | 16.36 | 16.62 | 16.3 | 15.9
Grendon 132kV | Corby | CORBY CENTRAL 33 11kV S STN | Primary | 11 | -0.6724 | 52.498 | WPD Best View | Headroom (MW) | N/A | 14.82 | 14.73 | 14.7 | 14.66 | 14.57 | 14.8 | 15.02 | 15.33 | 15.71 | 16.04 | 16.28 | 16.36 | 16.44 | 16.45 | 16.47 | 16.29 | 15.71 | 15.12
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Consumer Transformation | Headroom (MW) | Thermal | 21.86 | 21.69 | 21.42 | 21.27 | 20.88 | 20.71 | 20.42 | 19.57 | 18.79 | 18.16 | 17.33 | 16.36 | 15.33 | 14.41 | 13.28 | 10.54 | 4.41 | -3.39
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Leading the Way | Headroom (MW) | Thermal | 21.86 | 21.67 | 21.39 | 21.22 | 20.75 | 20.65 | 20.36 | 19.81 | 19.52 | 19.61 | 19.58 | 19.5 | 18.75 | 18.12 | 17.52 | 14.25 | 6.76 | -0.46
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | Steady Progression | Headroom (MW) | N/A | 21.86 | 21.77 | 21.73 | 15.56 | 15.56 | 15.75 | 15.2 | 14.46 | 13.85 | 13.42 | 13.03 | 12.65 | 12.29 | 12.02 | 11.65 | 13.26 | 12.11 | 10.17
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | System Transformation | Headroom (MW) | N/A | 21.86 | 21.73 | 21.65 | 21.45 | 21.31 | 21.47 | 21.49 | 20.89 | 20.31 | 20 | 19.51 | 18.84 | 18.13 | 17.56 | 16.8 | 16.92 | 13.05 | 7.85
Grendon 132kV | Corby | CORBY No2 11kV S STN | Primary | 11 | -0.6686 | 52.4918 | WPD Best View | Headroom (MW) | Thermal | 21.86 | 21.68 | 21.55 | 21.24 | 20.8 | 20.72 | 20.45 | 19.67 | 19.11 | 18.86 | 18.46 | 17.93 | 17.06 | 16.35 | 15.58 | 12.62 | 5.54 | -2.35
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Consumer Transformation | Headroom (MW) | N/A | 16.78 | 16.66 | 16.6 | 16.54 | 16.41 | 16.35 | 16.39 | 16.43 | 16.54 | 16.74 | 16.94 | 16.86 | 16.65 | 16.46 | 16.22 | 15.7 | 14.52 | 13.09
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Leading the Way | Headroom (MW) | N/A | 16.78 | 16.65 | 16.59 | 16.52 | 16.35 | 16.29 | 16.38 | 16.46 | 16.64 | 16.98 | 17.28 | 17.35 | 17.37 | 17.37 | 17.2 | 16.51 | 15.02 | 14.05
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | Steady Progression | Headroom (MW) | N/A | 16.78 | 16.67 | 16.61 | 16.55 | 16.47 | 16.42 | 16.42 | 16.43 | 16.48 | 16.6 | 16.73 | 16.79 | 16.83 | 16.87 | 16.91 | 17.02 | 16.48 | 15.81
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | System Transformation | Headroom (MW) | N/A | 16.78 | 16.67 | 16.61 | 16.54 | 16.44 | 16.38 | 16.43 | 16.47 | 16.58 | 16.8 | 17 | 17.06 | 16.93 | 16.77 | 16.56 | 16.35 | 15.39 | 14.2
Grendon 132kV | Corby | EARLSTREES 33 11kV S STN | Primary | 11 | -0.6969 | 52.5109 | WPD Best View | Headroom (MW) | N/A | 16.78 | 16.65 | 16.59 | 16.52 | 16.35 | 16.29 | 16.38 | 16.46 | 16.64 | 16.98 | 17.28 | 17.35 | 17.37 | 17.37 | 17.2 | 16.51 | 15.02 | 14.05
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Consumer Transformation | Headroom (MW) | Fault level | 9.4163 | 9.3385 | 9.2232 | 9.0635 | 8.7089 | 8.3499 | 7.2712 | 5.3889 | 3.8575 | 2.3571 | 0.67769 | -0.93082 | -2.5463 | -4.2148 | -6.043 | -13.6409 | -23.0051 | -32.781
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Leading the Way | Headroom (MW) | Fault level | 12.8869 | 12.7781 | 12.6324 | 12.4241 | 11.9636 | 11.4624 | 9.8845 | 8.4613 | 7.2399 | 5.6056 | 4.02 | 2.6019 | 0.7514 | -1.1552 | -3.1491 | -12.1201 | -23.3475 | -33.9023
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | Steady Progression | Headroom (MW) | N/A | 5.1946 | 5.1875 | 5.1798 | 5.1699 | 5.157 | 5.1304 | 5.0995 | 5.0455 | 4.9256 | 4.4825 | 4.3397 | 4.1758 | 3.9179 | 3.7095 | 3.4831 | 2.9885 | 2.4501 | 1.906
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | System Transformation | Headroom (MW) | Fault level | 7.4231 | 7.3933 | 7.3549 | 7.3036 | 7.2109 | 7.0955 | 6.9557 | 6.6982 | 5.9365 | 5.4128 | 4.7742 | 4.1605 | 3.5416 | 3.0024 | 2.3907 | 0.44453 | -2.0246 | -4.7579
Grendon 132kV | Corby | HAZELWOOD 33 11kV S STN | Primary | 11 | -0.7131 | 52.4854 | WPD Best View | Headroom (MW) | Fault level | 7.7396 | 7.6746 | 7.5876 | 7.4635 | 7.1878 | 6.8929 | 5.9489 | 5.0979 | 4.368 | 3.3935 | 2.4468 | 1.6025 | 0.49857 | -0.64279 | -1.8379 | -7.2145 | -13.9458 | -20.2732
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Consumer Transformation | Headroom (MW) | N/A | 13.35 | 13.27 | 13.19 | 13.1 | 12.9 | 12.74 | 12.77 | 12.82 | 12.71 | 12.61 | 12.51 | 12.42 | 12.32 | 12.22 | 12.1 | 11.16 | 9.58 | 7.78
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Leading the Way | Headroom (MW) | N/A | 13.35 | 13.26 | 13.18 | 13.08 | 12.85 | 12.68 | 12.78 | 12.92 | 12.8 | 12.69 | 12.55 | 12.43 | 12.3 | 12.15 | 11.99 | 10.7 | 8.84 | 6.39
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | Steady Progression | Headroom (MW) | N/A | 13.35 | 13.31 | 13.29 | 13.26 | 13.24 | 13.22 | 13.3 | 13.4 | 13.42 | 13.44 | 13.46 | 13.48 | 13.51 | 13.54 | 13.56 | 13.6 | 13.45 | 13.09
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | System Transformation | Headroom (MW) | N/A | 13.35 | 13.29 | 13.24 | 13.2 | 13.11 | 13.04 | 13.15 | 13.27 | 13.24 | 13.21 | 13.18 | 13.16 | 13.15 | 13.13 | 13.12 | 13 | 12.22 | 11.41
Grendon 132kV | Corby | OAKLEY 33 11kV S STN | Primary | 11 | -0.7307 | 52.4639 | WPD Best View | Headroom (MW) | N/A | 13.35 | 13.26 | 13.18 | 13.08 | 12.85 | 12.68 | 12.78 | 12.92 | 12.8 | 12.69 | 12.55 | 12.43 | 12.3 | 12.15 | 11.99 | 10.7 | 8.84 | 6.39
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Consumer Transformation | Headroom (MW) | Thermal | 7.5 | 7.41 | 7.32 | 7.22 | 6.96 | 6.76 | 6.57 | 5.65 | 4.57 | 3.31 | 1.91 | 0.28 | -1.49 | -3.12 | -5.15 | -8.9 | -13.27 | -18.55
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Leading the Way | Headroom (MW) | Thermal | 7.5 | 7.4 | 7.31 | 7.2 | 6.9 | 6.7 | 6.5 | 6.32 | 6.16 | 6.01 | 5.84 | 5.67 | 4.34 | 3.05 | 1.65 | -2.67 | -8.18 | -11.08
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | Steady Progression | Headroom (MW) | Thermal | 7.5 | 7.45 | 7.43 | 7.41 | 7.38 | 7.35 | 7.32 | 7.1 | 6.89 | 6.62 | 6.31 | 5.92 | 4.99 | 4.09 | 2.85 | 1.3 | -0.29 | -2.07
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | System Transformation | Headroom (MW) | Thermal | 7.5 | 7.43 | 7.39 | 7.33 | 7.23 | 7.14 | 7.05 | 6.22 | 5.17 | 3.99 | 2.65 | 1.09 | -0.59 | -2.09 | -3.98 | -6.81 | -10.34 | -14.62
Grendon 132kV | Corby | OUNDLE 33 11kV S STN | Primary | 11 | -0.4731 | 52.4954 | WPD Best View | Headroom (MW) | Thermal | 7.5 | 7.43 | 7.39 | 7.33 | 7.23 | 7.14 | 7.05 | 6.22 | 5.17 | 3.99 | 2.65 | 1.09 | -0.59 | -2.09 | -3.98 | -6.81 | -10.34 | -14.62
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Consumer Transformation | Headroom (MW) | Thermal | 16.27 | 16.24 | 16.26 | 16.18 | 15.96 | 15.78 | 15.2 | 14.05 | 12.96 | 11.87 | 10.75 | 9.59 | 8.36 | 7.08 | 5.6 | -0.25 | -7.36 | -15.12
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Leading the Way | Headroom (MW) | Thermal | 16.27 | 16.24 | 16.27 | 16.19 | 15.93 | 15.82 | 15.25 | 14.82 | 14.3 | 13.64 | 13.04 | 12.44 | 11.37 | 10.25 | 9.04 | 3.08 | -4.08 | -11.39
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | Steady Progression | Headroom (MW) | N/A | 16.27 | 16.26 | 16.3 | 16.27 | 16.22 | 16.26 | 16.27 | 16.3 | 16.24 | 15.87 | 15.8 | 15.72 | 15.43 | 15.09 | 14.66 | 14.19 | 13.25 | 11.84
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | System Transformation | Headroom (MW) | N/A | 16.27 | 16.26 | 16.3 | 16.25 | 16.17 | 16.21 | 16.24 | 16.17 | 15.42 | 14.82 | 14.17 | 13.47 | 12.74 | 12.09 | 11.31 | 9.24 | 6.06 | 2.58
Grendon 132kV | Irthlingborough | IRTHLINGBOROUGH 11kV S STN | Primary | 11 | -0.6141 | 52.3197 | WPD Best View | Headroom (MW) | N/A | 16.27 | 16.26 | 16.3 | 16.25 | 16.17 | 16.21 | 16.24 | 16.17 | 15.42 | 14.82 | 14.17 | 13.47 | 12.74 | 12.09 | 11.31 | 9.24 | 6.06 | 2.58
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Consumer Transformation | Headroom (MW) | Thermal | 15.3 | 15.14 | 14.87 | 14.7 | 14.37 | 14.02 | 12.98 | 10.97 | 9.29 | 7.6 | 5.75 | 3.86 | 1.93 | 0 | -2.22 | -11.07 | -21.71 | -33.34
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Leading the Way | Headroom (MW) | Thermal | 15.3 | 15.13 | 14.86 | 14.7 | 14.37 | 13.97 | 12.8 | 11.81 | 11 | 9.93 | 8.91 | 7.95 | 6.35 | 4.71 | 2.95 | -5.42 | -15.55 | -25.18
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | Steady Progression | Headroom (MW) | N/A | 15.3 | 15.19 | 15.12 | 15.06 | 15 | 14.92 | 14.85 | 14.7 | 14.44 | 13.58 | 13.27 | 12.9 | 12.22 | 11.64 | 10.91 | 9.84 | 8.55 | 6.97
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | System Transformation | Headroom (MW) | Thermal | 15.3 | 15.16 | 15.07 | 14.85 | 14.71 | 14.58 | 14.45 | 13.95 | 12.75 | 11.88 | 10.82 | 9.7 | 8.56 | 7.58 | 6.4 | 3.51 | -0.89 | -5.92
Grendon 132kV | Irthlingborough | PYTCHLEY ROAD 33 11kV S STN | Primary | 11 | -0.7207 | 52.3747 | WPD Best View | Headroom (MW) | Thermal | 15.3 | 15.13 | 14.86 | 14.7 | 14.38 | 13.97 | 13.14 | 12.42 | 11.56 | 10.69 | 9.83 | 9.01 | 7.59 | 6.19 | 4.7 | -2.18 | -10.77 | -18.83
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Consumer Transformation | Headroom (MW) | N/A | 25.36 | 25.1 | 24.88 | 24.61 | 23.97 | 23.47 | 22.98 | 22.51 | 22.08 | 21.7 | 21.3 | 20.9 | 20.49 | 20.04 | 19.57 | 16.03 | 11.4 | 6.27
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Leading the Way | Headroom (MW) | N/A | 25.36 | 25.08 | 24.84 | 24.55 | 23.85 | 23.32 | 22.81 | 22.32 | 21.87 | 21.48 | 21.02 | 20.55 | 20.05 | 19.5 | 18.88 | 14.67 | 9.34 | 2.32
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | Steady Progression | Headroom (MW) | N/A | 25.36 | 25.21 | 25.13 | 25.07 | 24.98 | 24.89 | 24.8 | 24.71 | 24.63 | 24.56 | 24.49 | 24.42 | 24.37 | 24.33 | 24.3 | 24.32 | 23.63 | 22.57
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | System Transformation | Headroom (MW) | N/A | 25.36 | 25.16 | 25.02 | 24.87 | 24.6 | 24.37 | 24.12 | 23.88 | 23.66 | 23.47 | 23.28 | 23.1 | 22.94 | 22.79 | 22.64 | 21.59 | 19.36 | 17.17
Grendon 132kV | Irthlingborough | RUSHDEN 33 11kV S STN | Primary | 11 | -0.597 | 52.2952 | WPD Best View | Headroom (MW) | N/A | 25.36 | 25.16 | 25.01 | 24.86 | 24.6 | 24.36 | 24.11 | 23.86 | 23.64 | 23.45 | 23.26 | 23.08 | 22.91 | 22.76 | 22.61 | 21.53 | 19.28 | 17.04
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Consumer Transformation | Headroom (MW) | Thermal | 8.8 | 8.77 | 8.78 | 8.76 | 8.54 | 8.34 | 8.03 | 7.43 | 6.87 | 6.3 | 5.79 | 5.24 | 4.65 | 4.09 | 3.4 | 1.2 | -1.22 | -4.01
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Leading the Way | Headroom (MW) | Thermal | 8.8 | 8.77 | 8.78 | 8.78 | 8.52 | 8.32 | 7.98 | 7.69 | 7.44 | 7.15 | 6.94 | 6.73 | 6.23 | 5.72 | 5.17 | 2.75 | -0.15 | -2.9
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | Steady Progression | Headroom (MW) | N/A | 8.8 | 8.78 | 8.8 | 8.81 | 8.78 | 8.75 | 8.73 | 8.7 | 8.63 | 8.4 | 8.29 | 8.15 | 7.89 | 7.64 | 7.32 | 6.87 | 6.32 | 5.53
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | System Transformation | Headroom (MW) | N/A | 8.8 | 8.77 | 8.8 | 8.8 | 8.75 | 8.7 | 8.59 | 8.32 | 7.89 | 7.5 | 7.1 | 6.66 | 6.19 | 5.77 | 5.27 | 4.21 | 2.64 | 0.9
Grendon 132kV | Irthlingborough | Raunds 11kv | Primary | 11 | -0.5483 | 52.345 | WPD Best View | Headroom (MW) | N/A | 8.8 | 8.77 | 8.8 | 8.8 | 8.75 | 8.7 | 8.59 | 8.32 | 7.89 | 7.5 | 7.1 | 6.66 | 6.19 | 5.77 | 5.27 | 4.21 | 2.64 | 0.9
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Consumer Transformation | Headroom (MW) | Thermal | 9.15 | 8.99 | 8.86 | 8.71 | 8.38 | 8.02 | 7.65 | 6.37 | 4.9 | 3.24 | 1.27 | -0.96 | -3.34 | -5.54 | -8.23 | -15.52 | -23.49 | -32.88
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Leading the Way | Headroom (MW) | Thermal | 9.15 | 8.98 | 8.84 | 8.68 | 8.33 | 7.9 | 7.44 | 7.02 | 6.62 | 6.23 | 5.73 | 5.24 | 3.33 | 1.48 | -0.47 | -9.58 | -18.81 | -25.34
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | Steady Progression | Headroom (MW) | Thermal | 9.15 | 9.06 | 9 | 8.95 | 8.89 | 8.82 | 8.76 | 8.47 | 8.18 | 7.79 | 7.37 | 6.86 | 5.71 | 4.59 | 3.07 | 1.13 | -0.86 | -3.19
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | System Transformation | Headroom (MW) | Thermal | 9.15 | 9.03 | 8.94 | 8.85 | 8.7 | 8.58 | 8.44 | 7.38 | 5.99 | 4.54 | 2.85 | 0.91 | -1.17 | -3.03 | -5.35 | -10.01 | -15.34 | -21.71
Grendon 132kV | Irthlingborough | THRAPSTON 33 11kV S STN | Primary | 11 | -0.5512 | 52.3921 | WPD Best View | Headroom (MW) | Thermal | 9.15 | 9.03 | 8.94 | 8.85 | 8.71 | 8.58 | 8.45 | 7.38 | 6 | 4.54 | 2.85 | 0.9 | -1.18 | -3.05 | -5.37 | -10.02 | -15.34 | -21.7
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Consumer Transformation | Headroom (MW) | N/A | 16.83 | 16.77 | 16.96 | 17.08 | 17.05 | 17 | 16.82 | 16.48 | 16.11 | 15.71 | 15.17 | 14.55 | 13.88 | 13.24 | 12.49 | 9.66 | 6.52 | 2.87
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Leading the Way | Headroom (MW) | N/A | 16.83 | 16.79 | 17.01 | 17.2 | 17.2 | 17.2 | 16.98 | 16.78 | 16.6 | 16.44 | 16.19 | 15.95 | 15.35 | 14.74 | 14.08 | 10.76 | 7.02 | 3.48
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | Steady Progression | Headroom (MW) | N/A | 16.83 | 16.81 | 17.03 | 17.23 | 17.42 | 17.53 | 17.56 | 17.53 | 17.5 | 17.45 | 17.35 | 17.23 | 16.95 | 16.66 | 16.27 | 15.64 | 14.7 | 13.5
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | System Transformation | Headroom (MW) | N/A | 16.83 | 16.81 | 17.04 | 17.23 | 17.38 | 17.46 | 17.39 | 17.16 | 16.88 | 16.58 | 16.13 | 15.6 | 15.05 | 14.55 | 13.95 | 12.41 | 10.27 | 7.94
Grendon 132kV | Kettering | BURTON LATIMER 33 11kV S STN | Primary | 11 | -0.6952 | 52.3639 | WPD Best View | Headroom (MW) | N/A | 16.83 | 16.8 | 17.04 | 17.25 | 17.31 | 17.35 | 17.16 | 16.82 | 16.45 | 16.06 | 15.5 | 14.87 | 14.18 | 13.51 | 12.7 | 9.75 | 6.55 | 2.44
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Consumer Transformation | Headroom (MW) | Thermal | 9.785 | 9.565 | 9.415 | 9.215 | 8.795 | 8.435 | 7.945 | 7.035 | 6.075 | 5.085 | 3.895 | 2.575 | 1.155 | -0.195 | -1.815 | -5.605 | -10.085 | -15.445
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Leading the Way | Headroom (MW) | Thermal | 9.785 | 9.545 | 9.385 | 9.175 | 8.705 | 8.335 | 7.915 | 7.455 | 7.045 | 6.725 | 6.385 | 6.045 | 4.905 | 3.785 | 2.605 | -1.625 | -4.115 | -10.545
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | Steady Progression | Headroom (MW) | Thermal | 9.785 | 9.645 | 9.595 | 9.555 | 3.815 | 3.785 | 3.015 | 2.135 | 1.295 | 0.455 | -0.365 | -1.145 | -2.035 | -2.855 | -3.815 | -4.935 | -6.365 | -8.115
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | System Transformation | Headroom (MW) | Thermal | 9.785 | 9.605 | 9.515 | 9.405 | 9.245 | 9.105 | 8.815 | 8.095 | 7.275 | 6.425 | 5.375 | 4.185 | 2.935 | 1.805 | 0.435 | -1.915 | -3.585 | -8.905
Grendon 132kV | Kettering | CHAPEL BRAMPTON 33 11kV S STN | Primary | 11 | -0.9273 | 52.2902 | WPD Best View | Headroom (MW) | Thermal | 9.785 | 9.605 | 9.505 | 9.395 | 9.205 | 9.035 | 8.695 | 7.925 | 7.055 | 6.165 | 5.095 | 3.895 | 2.625 | 1.505 | 0.145 | -2.145 | -3.815 | -9.135
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Consumer Transformation | Headroom (MW) | Thermal | 11.68 | 11.57 | 11.47 | 11.36 | 11.03 | 9.75 | 9.48 | 8.34 | 6.99 | 5.44 | 3.52 | 1.29 | -1.12 | -3.33 | -6.08 | -11.52 | -18.91 | -27.22
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Leading the Way | Headroom (MW) | Thermal | 11.68 | 11.56 | 11.47 | 11.36 | 10 | 9.73 | 9.45 | 9.19 | 8.94 | 8.72 | 8.42 | 8.13 | 6.24 | 4.41 | 2.46 | -3.97 | -13.61 | -18.88
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | Steady Progression | Headroom (MW) | Thermal | 11.68 | 11.64 | 11.64 | 11.66 | 11.69 | 11.69 | 11.68 | 11.43 | 11.18 | 10.85 | 10.44 | 9.93 | 8.71 | 7.5 | 5.87 | 3.77 | 1.48 | -1.21
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | System Transformation | Headroom (MW) | Thermal | 11.68 | 11.61 | 11.57 | 11.55 | 11.47 | 11.39 | 10.26 | 9.25 | 7.97 | 6.53 | 4.76 | 2.69 | 0.46 | -1.57 | -4.12 | -8.02 | -13.87 | -20.3
Grendon 132kV | Kettering | DESBOROUGH 33 11kV S STN | Primary | 11 | -0.815 | 52.4454 | WPD Best View | Headroom (MW) | Thermal | 11.68 | 11.56 | 11.47 | 11.37 | 11.02 | 9.74 | 9.47 | 9.06 | 8.62 | 8.16 | 7.55 | 6.89 | 4.89 | 2.99 | 0.87 | -5.42 | -14.75 | -20.78
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Consumer Transformation | Headroom (MW) | Thermal | 15.33 | 4.92 | 4.83 | 4.7 | 4.36 | 4.06 | 3.04 | 2.09 | 1.23 | 0.61 | 0.12 | -0.22 | -0.49 | -0.78 | -1.07 | -2.96 | -4.39 | -6.31
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Leading the Way | Headroom (MW) | Thermal | 15.33 | 4.91 | 4.82 | 4.69 | 4.32 | 4.02 | 3.5 | 3 | 2.5 | 2.25 | 1.94 | 1.65 | 1.34 | 1.01 | 0.65 | -1.58 | 1.48 | 2.64
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | Steady Progression | Headroom (MW) | Thermal | 15.33 | 4.99 | 4.98 | 4.97 | 4.96 | 4.92 | 3.85 | 2.79 | 1.77 | 0.82 | -0.04 | -0.75 | -1.11 | -1.38 | -1.53 | -1.57 | -1.9 | -2.56
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | System Transformation | Headroom (MW) | Thermal | 15.33 | 4.96 | 4.92 | 4.87 | 4.75 | 4.63 | 3.76 | 2.96 | 2.24 | 1.74 | 1.39 | 1.19 | 1.08 | 0.97 | 0.87 | 0.29 | 0.11 | -0.28
Grendon 132kV | Kettering | FARNDON ROAD 33 11kV S STN | Primary | 11 | -0.9335 | 52.471 | WPD Best View | Headroom (MW) | Thermal | 15.33 | 4.93 | 4.84 | 4.72 | 4.41 | 4.14 | 3.14 | 2.21 | 1.36 | 0.75 | 0.28 | -0.04 | -0.29 | -0.55 | -0.82 | -2.53 | -3.8 | -5.49
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Consumer Transformation | Headroom (MW) | Thermal | 32.09 | 31.86 | 31.7 | 31.52 | 31.18 | 30.54 | 29.8 | 28.73 | 27.6 | 26.43 | 25.15 | 23.75 | 22.26 | 20.81 | 19.11 | 12.27 | 3.08 | -7.35
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Leading the Way | Headroom (MW) | Thermal | 32.09 | 31.84 | 31.67 | 31.47 | 31.04 | 30.38 | 29.6 | 28.89 | 28.2 | 27.57 | 26.88 | 26.17 | 24.78 | 23.33 | 21.74 | 13.76 | 2.94 | -8.66
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | Steady Progression | Headroom (MW) | N/A | 32.09 | 31.91 | 31.82 | 31.72 | 31.6 | 31.51 | 31.42 | 31.32 | 31.22 | 31.12 | 31.01 | 30.88 | 30.62 | 30.07 | 29.35 | 28.46 | 26.9 | 24.27
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | System Transformation | Headroom (MW) | N/A | 32.09 | 31.89 | 31.77 | 31.63 | 31.43 | 31.32 | 31.21 | 30.83 | 30.02 | 29.16 | 28.18 | 27.12 | 26 | 25.01 | 23.83 | 21.05 | 15.68 | 9.85
Grendon 132kV | Kettering | FIELD STREET 33 11kV S STN | Primary | 11 | -0.7286 | 52.4029 | WPD Best View | Headroom (MW) | Thermal | 32.09 | 31.84 | 31.67 | 31.47 | 31.04 | 30.38 | 29.6 | 28.89 | 28.2 | 27.57 | 26.88 | 26.17 | 24.78 | 23.33 | 21.74 | 13.76 | 2.94 | -8.66
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Consumer Transformation | Headroom (MW) | N/A | 12.77 | 13 | 13.32 | 13.54 | 13.71 | 13.82 | 13.9 | 13.94 | 14 | 14.07 | 14.09 | 14.07 | 14.05 | 14.02 | 13.98 | 13.57 | 12.71 | 11.73
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Leading the Way | Headroom (MW) | N/A | 12.77 | 13.03 | 13.4 | 13.66 | 13.85 | 14 | 14.08 | 14.14 | 14.2 | 14.29 | 14.29 | 14.25 | 14.19 | 14.13 | 14.05 | 13.38 | 12.36 | 11.06
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | Steady Progression | Headroom (MW) | N/A | 12.77 | 12.98 | 13.29 | 13.51 | 13.73 | 13.89 | 14.02 | 14.12 | 14.23 | 14.32 | 14.39 | 14.45 | 14.49 | 14.52 | 14.56 | 14.73 | 14.58 | 14.28
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | System Transformation | Headroom (MW) | N/A | 12.77 | 13.01 | 13.35 | 13.58 | 13.81 | 13.96 | 14.08 | 14.16 | 14.25 | 14.36 | 14.4 | 14.41 | 14.43 | 14.45 | 14.46 | 14.46 | 13.98 | 13.48
Grendon 132kV | Kettering | KETTERING NORTH 33 11kV S STN | Primary | 11 | -0.7351 | 52.425 | WPD Best View | Headroom (MW) | N/A | 12.77 | 13.03 | 13.4 | 13.66 | 13.85 | 14 | 14.08 | 14.14 | 14.2 | 14.29 | 14.29 | 14.25 | 14.19 | 14.13 | 14.05 | 13.38 | 12.36 | 11.06
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Consumer Transformation | Headroom (MW) | Thermal | 2.77 | 2.71 | 2.66 | 2.6 | 2.45 | 2.33 | 2.22 | 1.82 | 1.37 | 0.86 | 0.19 | -0.58 | -1.42 | -2.18 | -3.13 | -6.15 | -8.49 | -11.31
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Leading the Way | Headroom (MW) | Thermal | 2.77 | 2.71 | 2.65 | 2.59 | 2.43 | 2.31 | 2.19 | 2.08 | 1.98 | 1.88 | 1.77 | 1.67 | 1.03 | 0.42 | -0.24 | -3.53 | -6.46 | -8.04
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | Steady Progression | Headroom (MW) | Thermal | 2.77 | 2.74 | 2.72 | 2.7 | 2.67 | 2.65 | 2.63 | 2.53 | 2.44 | 2.32 | 2.16 | 1.97 | 1.54 | 1.11 | 0.53 | -0.2 | -1.02 | -1.99
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | System Transformation | Headroom (MW) | Thermal | 2.77 | 2.73 | 2.69 | 2.66 | 2.59 | 2.54 | 2.48 | 2.14 | 1.71 | 1.24 | 0.62 | -0.11 | -0.9 | -1.61 | -2.49 | -4.38 | -6.27 | -8.53
Grendon 132kV | Kibworth | BRUNTINGTHORPE 33 11kV S STN | Primary | 11 | -1.1162 | 52.4887 | WPD Best View | Headroom (MW) | Thermal | 2.77 | 2.71 | 2.66 | 2.6 | 2.45 | 2.33 | 2.22 | 1.83 | 1.37 | 0.86 | 0.19 | -0.58 | -1.41 | -2.18 | -3.13 | -6.14 | -8.48 | -11.29
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Consumer Transformation | Headroom (MW) | Thermal | 12.97 | 12.83 | 12.71 | 12.54 | 12.15 | 11.71 | 11.29 | 9.84 | 8.16 | 6.25 | 3.57 | 0.48 | -2.89 | -5.97 | -9.77 | -17.42 | -27.24 | -39.18
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Leading the Way | Headroom (MW) | Thermal | 12.97 | 12.82 | 12.69 | 12.51 | 12.1 | 11.58 | 11.07 | 10.58 | 10.11 | 9.67 | 9.16 | 8.64 | 6.04 | 3.47 | 0.75 | -8.24 | -20.54 | -27.52
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | Steady Progression | Headroom (MW) | Thermal | 12.97 | 12.91 | 12.89 | 12.87 | 12.85 | 12.81 | 12.76 | 12.44 | 12.14 | 11.74 | 11.18 | 10.47 | 8.81 | 7.17 | 4.93 | 2.05 | -1.21 | -4.8
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | System Transformation | Headroom (MW) | Thermal | 12.97 | 12.87 | 12.81 | 12.74 | 12.6 | 12.47 | 12.31 | 11.07 | 9.49 | 7.8 | 5.37 | 2.52 | -0.54 | -3.29 | -6.73 | -12.02 | -19.81 | -29.29
Grendon 132kV | Kibworth | KIBWORTH 11kV S STN | Primary | 11 | -1.0234 | 52.5372 | WPD Best View | Headroom (MW) | Thermal | 12.97 | 12.84 | 12.71 | 12.54 | 12.16 | 11.72 | 11.3 | 9.85 | 8.17 | 6.25 | 3.58 | 0.49 | -2.88 | -5.96 | -9.76 | -17.38 | -27.17 | -39.07
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Consumer Transformation | Headroom (MW) | Thermal | 12.13 | 11.97 | 11.84 | 11.66 | 11.23 | 10.87 | 10.51 | 9.24 | 7.75 | 6.21 | 4.09 | 1.5 | -1.32 | -3.94 | -7.18 | -13.31 | -21.23 | -30.85
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Leading the Way | Headroom (MW) | Thermal | 12.13 | 11.96 | 11.82 | 11.63 | 11.16 | 10.78 | 10.41 | 10.06 | 9.73 | 9.62 | 9.48 | 9.14 | 7.02 | 4.99 | 2.74 | -4.37 | -14.4 | -19.74
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | Steady Progression | Headroom (MW) | Thermal | 12.13 | 12.05 | 12.01 | 11.97 | 11.93 | 11.87 | 11.81 | 11.52 | 11.24 | 10.95 | 10.54 | 9.95 | 8.52 | 7.11 | 5.21 | 2.91 | 0.05 | -3.21
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | System Transformation | Headroom (MW) | Thermal | 12.13 | 12.01 | 11.93 | 11.84 | 11.67 | 11.51 | 11.33 | 10.23 | 8.85 | 7.44 | 5.47 | 3.02 | 0.37 | -2.01 | -4.98 | -9.46 | -15.86 | -23.64
Grendon 132kV | Kibworth | MARKET HARBOROUGH 33 11kV S STN | Primary | 11 | -0.9025 | 52.4794 | WPD Best View | Headroom (MW) | Thermal | 12.13 | 11.97 | 11.84 | 11.66 | 11.24 | 10.88 | 10.53 | 9.56 | 8.44 | 7.34 | 5.76 | 3.8 | 1.21 | -1.25 | -4.2 | -10.46 | -18.8 | -27.06
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Consumer Transformation | Headroom (MW) | Thermal | 5.39 | 5.24 | 5.13 | 4.99 | 4.69 | 4.35 | 4.01 | 3.31 | 2.54 | 1.69 | 0.73 | -0.35 | -1.51 | -2.59 | -3.96 | -7.98 | -13.96 | -18.57
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Leading the Way | Headroom (MW) | Thermal | 5.39 | 5.24 | 5.12 | 4.98 | 4.66 | 4.27 | 3.86 | 3.46 | 3.06 | 2.65 | 2.41 | 2.17 | 1.22 | 0.25 | -0.8 | -5.15 | -14.05 | -17.31
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | Steady Progression | Headroom (MW) | Thermal | 5.39 | 5.29 | 5.25 | 5.21 | 5.16 | 5.09 | 5.02 | 4.86 | 4.71 | 4.52 | 4.3 | 4.02 | 3.44 | 2.87 | 2.1 | 1.07 | -0.22 | -1.69
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | System Transformation | Headroom (MW) | Thermal | 5.39 | 5.27 | 5.2 | 5.12 | 4.99 | 4.81 | 4.6 | 4.04 | 3.37 | 2.65 | 1.79 | 0.81 | -0.24 | -1.2 | -2.38 | -4.66 | -9.57 | -12.93
Grendon 132kV | Melton Mowbray | HOLWELL 33 11kV S STN | Primary | 11 | -0.9198 | 52.7753 | WPD Best View | Headroom (MW) | Thermal | 5.39 | 5.24 | 5.13 | 4.99 | 4.69 | 4.35 | 4.01 | 3.31 | 2.54 | 1.69 | 0.73 | -0.35 | -1.51 | -2.59 | -3.96 | -7.98 | -13.96 | -18.57
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Consumer Transformation | Headroom (MW) | Thermal | 13.36 | 13.12 | 12.39 | 12.06 | 11.38 | 10.55 | 7.68 | 1.66 | -3.55 | -8.89 | -15.07 | -21.62 | -28.37 | -35.06 | -42.93 | -68.69 | -100.3 | -135.06
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Leading the Way | Headroom (MW) | Thermal | 13.36 | 13.1 | 12.34 | 12.03 | 11.36 | 10.42 | 7.24 | 4.44 | 2.12 | -1.02 | -3.73 | -6.36 | -11.75 | -17.29 | -23.21 | -46.82 | -77.06 | -101.99
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | Steady Progression | Headroom (MW) | Thermal | 13.36 | 13.24 | 12.78 | 12.72 | 12.63 | 12.51 | 12.39 | 11.92 | 11.14 | 8.67 | 7.64 | 6.35 | 3.72 | 1.37 | -1.58 | -5.67 | -10.43 | -15.71
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | System Transformation | Headroom (MW) | Thermal | 13.36 | 13.18 | 12.59 | 12.45 | 12.18 | 11.85 | 11.46 | 9.7 | 5.81 | 2.71 | -1.19 | -5.53 | -10.06 | -14.02 | -18.85 | -28.5 | -42.32 | -58.52
Grendon 132kV | Melton Mowbray | MELTON MOWBRAY 11KV S STN | Primary | 11 | -0.8697 | 52.7644 | WPD Best View | Headroom (MW) | Thermal | 13.36 | 13.12 | 12.41 | 12.1 | 11.45 | 10.65 | 8.32 | 3.3 | -1.63 | -6.47 | -12.17 | -18.24 | -24.51 | -30.63 | -37.86 | -60.47 | -88.22 | -119.06
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Consumer Transformation | Headroom (MW) | Thermal | 7.05 | 6.97 | 6.92 | 6.85 | 6.73 | 6.58 | 6.41 | 5.75 | 4.93 | 3.98 | 2.81 | 1.45 | -0.02 | -1.37 | -3.05 | -6.05 | -9.44 | -13.62
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Leading the Way | Headroom (MW) | Thermal | 7.05 | 6.97 | 6.91 | 6.85 | 6.72 | 6.53 | 6.33 | 6.11 | 5.88 | 5.64 | 5.5 | 5.37 | 4.26 | 3.2 | 2.08 | -1.18 | -5.54 | -7.05
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | Steady Progression | Headroom (MW) | Thermal | 7.05 | 6.99 | 6.96 | 6.93 | 6.9 | 6.87 | 6.83 | 6.66 | 6.5 | 6.29 | 6.02 | 5.67 | 4.86 | 4.06 | 2.99 | 1.54 | 0.02 | -1.56
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | System Transformation | Headroom (MW) | Thermal | 7.05 | 6.98 | 6.94 | 6.9 | 6.84 | 6.75 | 6.64 | 6.03 | 5.25 | 4.37 | 3.24 | 1.92 | 0.49 | -0.81 | -2.44 | -4.84 | -7.88 | -11.64
Grendon 132kV | Melton Mowbray | OLD DALBY 33 11kV S STN | Primary | 11 | -0.9851 | 52.7981 | WPD Best View | Headroom (MW) | Thermal | 7.05 | 6.97 | 6.92 | 6.85 | 6.73 | 6.58 | 6.41 | 5.75 | 4.93 | 3.98 | 2.81 | 1.45 | -0.02 | -1.37 | -3.05 | -6.05 | -9.44 | -13.62
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Consumer Transformation | Headroom (MW) | N/A | 15.89 | 15.88 | 15.93 | 15.88 | 15.81 | 15.72 | 15.62 | 15.52 | 15.42 | 15.32 | 15.22 | 15.12 | 15.03 | 14.93 | 14.82 | 14.2 | 13.54 | 12.85
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Leading the Way | Headroom (MW) | N/A | 15.89 | 15.89 | 15.94 | 15.89 | 15.78 | 15.68 | 15.58 | 15.47 | 15.36 | 15.26 | 15.16 | 15.06 | 14.95 | 14.85 | 14.73 | 14.1 | 13.39 | 12.56
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | Steady Progression | Headroom (MW) | N/A | 15.89 | 15.88 | 15.92 | 15.88 | 15.84 | 15.8 | 15.77 | 15.73 | 15.69 | 15.64 | 15.59 | 15.54 | 15.49 | 15.45 | 15.4 | 15.17 | 14.95 | 14.72
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | System Transformation | Headroom (MW) | N/A | 15.89 | 15.89 | 15.94 | 15.89 | 15.83 | 15.79 | 15.75 | 15.68 | 15.61 | 15.53 | 15.46 | 15.39 | 15.32 | 15.26 | 15.19 | 14.86 | 14.44 | 14.03
Grendon 132kV | Northampton | BRACKMILLS 33 11kV S STN | Primary | 11 | -0.8666 | 52.2238 | WPD Best View | Headroom (MW) | N/A | 15.89 | 15.89 | 15.94 | 15.89 | 15.78 | 15.68 | 15.58 | 15.47 | 15.36 | 15.26 | 15.16 | 15.06 | 14.95 | 14.85 | 14.73 | 14.1 | 13.39 | 12.56
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Consumer Transformation | Headroom (MW) | N/A | 16.897 | 16.8666 | 16.8197 | 16.7684 | 16.5698 | 16.3683 | 16.172 | 15.9751 | 15.7787 | 15.5818 | 15.3634 | 15.1428 | 14.9227 | 14.7021 | 14.4803 | 13.3338 | 12.0614 | 10.7715
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Leading the Way | Headroom (MW) | N/A | 23.1249 | 23.0816 | 23.0137 | 22.9418 | 22.6708 | 22.3943 | 22.1179 | 21.8445 | 21.5696 | 21.2931 | 20.9889 | 20.6784 | 20.3634 | 20.0398 | 19.7085 | 17.9996 | 16.09 | 12.45
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | Steady Progression | Headroom (MW) | N/A | 9.3214 | 9.3177 | 9.3121 | 9.3084 | 9.3037 | 9.2912 | 9.2766 | 9.2598 | 9.2436 | 9.2234 | 9.2025 | 9.182 | 9.1614 | 9.1409 | 9.121 | 9.017 | 8.8975 | 8.7767
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | System Transformation | Headroom (MW) | N/A | 13.3203 | 13.3078 | 13.2878 | 13.2696 | 13.2184 | 13.1548 | 13.081 | 13.0071 | 12.9333 | 12.859 | 12.7767 | 12.6931 | 12.6095 | 12.5258 | 12.4413 | 12.0018 | 11.5174 | 11.029
Grendon 132kV | Northampton | CAMPBELL STREET 33 11kV S STN | Primary | 11 | -0.8967 | 52.243 | WPD Best View | Headroom (MW) | N/A | 13.8882 | 13.8622 | 13.8214 | 13.7783 | 13.6155 | 13.4495 | 13.2834 | 13.1192 | 12.9541 | 12.7881 | 12.6054 | 12.4189 | 12.2297 | 12.0354 | 11.8364 | 10.8101 | 9.6989 | 8.5714
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Consumer Transformation | Headroom (MW) | N/A | 15.7 | 15.53 | 15.57 | 15.43 | 15.08 | 14.8 | 14.52 | 14.26 | 14.02 | 13.8 | 13.58 | 13.36 | 13.13 | 12.9 | 12.64 | 10.88 | 8.9 | 6.64
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Leading the Way | Headroom (MW) | N/A | 15.7 | 15.52 | 15.57 | 15.42 | 15.03 | 14.72 | 14.43 | 14.16 | 13.91 | 13.68 | 13.44 | 13.18 | 12.92 | 12.64 | 12.31 | 12.28 | 6.49 | 2.84
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | Steady Progression | Headroom (MW) | N/A | 15.7 | 15.59 | 15.72 | 15.68 | 15.64 | 15.58 | 15.51 | 15.45 | 15.4 | 15.34 | 15.28 | 15.23 | 15.19 | 15.15 | 15.12 | 15.07 | 14.82 | 14.21
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | System Transformation | Headroom (MW) | N/A | 15.7 | 15.56 | 15.68 | 15.6 | 15.45 | 15.32 | 15.16 | 15.02 | 14.88 | 14.76 | 14.64 | 14.52 | 14.42 | 14.33 | 14.24 | 14.91 | 11.67 | 10.45
Grendon 132kV | Northampton | NORTHAMPTON 11kV S STN | Primary | 11 | -0.9135 | 52.2457 | WPD Best View | Headroom (MW) | N/A | 15.7 | 15.52 | 15.57 | 15.42 | 15.03 | 14.72 | 14.43 | 14.16 | 13.91 | 13.68 | 13.44 | 13.18 | 12.92 | 12.64 | 12.31 | 12.28 | 6.49 | 2.84
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Consumer Transformation | Headroom (MW) | N/A | 9.64 | 9.59 | 9.56 | 9.54 | 9.5 | 9.46 | 9.42 | 9.37 | 9.33 | 9.28 | 9.23 | 9.17 | 9.11 | 9.05 | 8.99 | 8.54 | 8.96 | 9.48
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Leading the Way | Headroom (MW) | N/A | 9.64 | 9.59 | 9.56 | 9.53 | 9.5 | 9.46 | 9.42 | 9.38 | 9.33 | 9.27 | 9.22 | 9.16 | 9.1 | 9.03 | 8.97 | 9.67 | 9.15 | 6.57
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | Steady Progression | Headroom (MW) | N/A | 9.64 | 9.59 | 9.57 | 9.54 | 9.52 | 9.49 | 9.44 | 9.42 | 9.39 | 9.37 | 9.34 | 9.32 | 9.29 | 9.26 | 9.23 | 9.09 | 9.02 | 8.92
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | System Transformation | Headroom (MW) | N/A | 9.64 | 9.59 | 9.57 | 9.54 | 9.51 | 9.48 | 9.44 | 9.41 | 9.37 | 9.33 | 9.29 | 9.25 | 9.2 | 9.16 | 9.11 | 9.44 | 9.39 | 7.64
Grendon 132kV | Northampton | PINEHAM 33 11kV S STN | Primary | 11 | -0.9577 | 52.2176 | WPD Best View | Headroom (MW) | N/A | 9.64 | 9.59 | 9.56 | 9.53 | 9.5 | 9.46 | 9.42 | 9.38 | 9.33 | 9.27 | 9.22 | 9.16 | 9.1 | 9.03 | 8.97 | 9.67 | 9.15 | 6.57
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Consumer Transformation | Headroom (MW) | Thermal | 5.56 | 5.46 | 5.39 | 5.3 | 5.1 | 4.94 | 4.79 | 4.17 | 3.43 | 2.57 | 1.54 | 0.35 | -0.93 | -2.12 | -3.6 | -6.42 | -10.46 | -14.61
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Leading the Way | Headroom (MW) | Thermal | 5.56 | 5.46 | 5.38 | 5.28 | 5.05 | 4.89 | 4.73 | 4.6 | 4.47 | 4.33 | 4.19 | 4.05 | 3.06 | 2.09 | 1.05 | -2.2 | -7.72 | -10.15
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | Steady Progression | Headroom (MW) | Thermal | 5.56 | 5.51 | 5.48 | 5.46 | 5.43 | 5.4 | 5.37 | 5.21 | 5.07 | 4.88 | 4.65 | 4.36 | 3.69 | 3.03 | 2.13 | 1.07 | -0.14 | -1.54
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | System Transformation | Headroom (MW) | Thermal | 5.56 | 5.49 | 5.44 | 5.39 | 5.3 | 5.23 | 5.15 | 4.59 | 3.89 | 3.09 | 2.12 | 0.98 | -0.24 | -1.32 | -2.68 | -4.72 | -8.08 | -11.4
Grendon 132kV | Northampton | ROADE 33 11kV S STN | Primary | 11 | -0.8911 | 52.1522 | WPD Best View | Headroom (MW) | Thermal | 5.56 | 5.46 | 5.38 | 5.28 | 5.05 | 4.89 | 4.73 | 4.6 | 4.47 | 4.33 | 4.19 | 4.05 | 3.06 | 2.09 | 1.05 | -2.2 | -7.72 | -10.15
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Consumer Transformation | Headroom (MW) | Thermal | 16.73 | 16.59 | 16.5 | 16.18 | 15.65 | 15.21 | 14.8 | 14.2 | 13.59 | 12.95 | 12.21 | 11.39 | 10.54 | 9.71 | 8.72 | 5.27 | 0.82 | -4.29
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Leading the Way | Headroom (MW) | Thermal | 16.73 | 16.58 | 16.48 | 16.13 | 15.56 | 15.1 | 14.66 | 14.29 | 13.95 | 13.63 | 13.25 | 12.86 | 12.08 | 11.3 | 10.45 | 6.4 | 1.1 | -4.45
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | Steady Progression | Headroom (MW) | N/A | 16.73 | 16.62 | 16.57 | 16.51 | 16.45 | 16.41 | 16.35 | 16.3 | 16.24 | 16.18 | 16.01 | 15.83 | 15.48 | 15.16 | 14.74 | 14.26 | 13.33 | 11.92
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | System Transformation | Headroom (MW) | N/A | 16.73 | 16.61 | 16.53 | 16.46 | 16.36 | 16.22 | 16 | 15.58 | 15.11 | 14.61 | 14.03 | 13.39 | 12.72 | 12.12 | 11.4 | 9.81 | 7.08 | 4.14
Grendon 132kV | Northampton | WOOTTON 33 11kV S STN | Primary | 11 | -0.8743 | 52.2054 | WPD Best View | Headroom (MW) | Thermal | 16.73 | 16.58 | 16.48 | 16.13 | 15.56 | 15.1 | 14.66 | 14.29 | 13.95 | 13.63 | 13.25 | 12.86 | 12.08 | 11.3 | 10.45 | 6.4 | 1.1 | -4.45
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Consumer Transformation | Headroom (MW) | Thermal | 22.36 | 22.14 | 21.93 | 21.46 | 20.87 | 20.38 | 19.48 | 18.2 | 17.2 | 16.28 | 15.24 | 14.17 | 13.1 | 11.95 | 10.74 | 4.2 | -4.56 | -13.89
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Leading the Way | Headroom (MW) | Thermal | 22.36 | 22.12 | 21.91 | 21.43 | 20.78 | 20.27 | 19.31 | 18.44 | 17.71 | 16.85 | 15.93 | 14.99 | 13.98 | 12.91 | 11.75 | 5.6 | -2.62 | -12.48
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | Steady Progression | Headroom (MW) | N/A | 18.8348 | 18.8202 | 18.8038 | 18.7874 | 18.7692 | 18.7363 | 18.7009 | 18.6606 | 18.5629 | 18.1684 | 18.0555 | 17.9245 | 17.7579 | 17.6412 | 17.5442 | 17.2108 | 16.856 | 16.4971
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | System Transformation | Headroom (MW) | N/A | 22.36 | 22.2 | 22.08 | 22.01 | 21.77 | 21.56 | 21.32 | 21.08 | 20.52 | 20.15 | 19.72 | 19.33 | 18.98 | 18.69 | 18.36 | 16.78 | 13.79 | 10.72
Grendon 132kV | Northampton East | BOOTHVILLE 33 11kV S STN | Primary | 11 | -0.8579 | 52.2715 | WPD Best View | Headroom (MW) | N/A | 22.36 | 22.14 | 21.96 | 21.8 | 21.26 | 20.85 | 20.45 | 20.05 | 19.33 | 18.84 | 18.25 | 17.67 | 17.06 | 16.45 | 15.79 | 11.98 | 6.78 | 0.27
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Consumer Transformation | Headroom (MW) | Thermal | 3.83 | 3.77 | 3.72 | 3.66 | 3.53 | 3.42 | 3.32 | 2.86 | 2.32 | 1.7 | 0.96 | 0.09 | -0.86 | -1.73 | -2.83 | -4.85 | -7.32 | -10.33
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Leading the Way | Headroom (MW) | Thermal | 3.83 | 3.77 | 3.71 | 3.65 | 3.5 | 3.39 | 3.29 | 3.19 | 3.1 | 3.02 | 2.92 | 2.83 | 2.13 | 1.44 | 0.69 | -1.66 | -4.79 | -6.47
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | Steady Progression | Headroom (MW) | Thermal | 3.83 | 3.8 | 3.78 | 3.77 | 3.75 | 3.73 | 3.71 | 3.61 | 3.5 | 3.36 | 3.19 | 2.98 | 2.49 | 2 | 1.34 | 0.52 | -0.37 | -1.39
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | System Transformation | Headroom (MW) | Thermal | 3.83 | 3.79 | 3.76 | 3.72 | 3.67 | 3.62 | 3.57 | 3.16 | 2.64 | 2.05 | 1.34 | 0.5 | -0.4 | -1.2 | -2.21 | -3.72 | -5.72 | -8.14
Grendon 132kV | Northampton East | DENTON 33 11kV S STN | Primary | 11 | -0.7764 | 52.2176 | WPD Best View | Headroom (MW) | Thermal | 3.83 | 3.77 | 3.71 | 3.65 | 3.5 | 3.39 | 3.29 | 3.19 | 3.1 | 3.02 | 2.93 | 2.84 | 2.14 | 1.46 | 0.7 | -1.65 | -4.77 | -6.45
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Consumer Transformation | Headroom (MW) | Thermal | 5.885 | 5.825 | 5.765 | 5.695 | 5.515 | 5.375 | 5.255 | 4.945 | 4.595 | 4.225 | 3.725 | 3.165 | 2.555 | 1.985 | 1.295 | -0.365 | -2.535 | -5.095
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Leading the Way | Headroom (MW) | Thermal | 5.885 | 5.815 | 5.755 | 5.685 | 5.475 | 5.335 | 5.205 | 5.085 | 4.975 | 4.865 | 4.755 | 4.635 | 4.135 | 3.655 | 3.125 | 1.185 | -1.475 | -3.485
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | Steady Progression | Headroom (MW) | N/A | 5.885 | 5.855 | 5.845 | 5.825 | 5.805 | 5.785 | 5.765 | 5.695 | 5.635 | 5.555 | 5.455 | 5.325 | 5.025 | 4.745 | 4.365 | 3.885 | 3.295 | 2.545
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | System Transformation | Headroom (MW) | Thermal | 5.885 | 5.845 | 5.805 | 5.775 | 5.695 | 5.645 | 5.575 | 5.335 | 5.025 | 4.695 | 4.255 | 3.755 | 3.225 | 2.735 | 2.125 | 1.135 | -0.395 | -2.195
Grendon 132kV | Northampton East | EARLS BARTON 33 11kV S STN | Primary | 11 | -0.7605 | 52.2627 | WPD Best View | Headroom (MW) | Thermal | 5.885 | 5.845 | 5.805 | 5.775 | 5.695 | 5.635 | 5.575 | 5.335 | 5.025 | 4.695 | 4.265 | 3.775 | 3.245 | 2.755 | 2.135 | 1.125 | -0.425 | -2.255
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Consumer Transformation | Headroom (MW) | N/A | 14.3 | 14.14 | 14.01 | 13.86 | 13.54 | 13.29 | 13.04 | 12.82 | 12.61 | 12.41 | 12.23 | 12.05 | 11.86 | 11.64 | 11.42 | 9.69 | 7.21 | 4.45
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Leading the Way | Headroom (MW) | N/A | 14.3 | 14.13 | 14 | 13.83 | 13.49 | 13.22 | 12.96 | 12.73 | 12.51 | 12.31 | 12.09 | 11.87 | 11.62 | 11.35 | 11.03 | 8.9 | 6.04 | 2.22
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | Steady Progression | Headroom (MW) | N/A | 14.3 | 14.2 | 14.15 | 14.11 | 14.05 | 14 | 13.94 | 13.88 | 13.83 | 13.78 | 13.73 | 13.7 | 13.66 | 13.64 | 13.63 | 13.63 | 13.27 | 12.67
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | System Transformation | Headroom (MW) | N/A | 14.3 | 14.18 | 14.09 | 14 | 13.86 | 13.74 | 13.61 | 13.48 | 13.37 | 13.27 | 13.17 | 13.09 | 13.01 | 12.95 | 12.88 | 12.42 | 11.19 | 9.96
Grendon 132kV | Northampton East | Northampton East 11kv S Stn | Primary | 11 | -0.8372 | 52.243 | WPD Best View | Headroom (MW) | N/A | 14.3 | 14.13 | 14 | 13.84 | 13.5 | 13.24 | 12.99 | 12.76 | 12.55 | 12.35 | 12.14 | 11.92 | 11.68 | 11.41 | 11.11 | 9.03 | 6.21 | 2.48
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Consumer Transformation | Headroom (MW) | Thermal | 7.3 | 7.19 | 7.09 | 6.93 | 6.54 | 6.14 | 5.43 | 2.97 | 0.34 | -2.64 | -5.87 | -9.52 | -13.46 | -17.12 | -21.63 | -32.25 | -43.48 | -56.61
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Leading the Way | Headroom (MW) | Thermal | 7.3 | 7.18 | 7.09 | 6.92 | 6.49 | 6.02 | 5.2 | 4.44 | 3.76 | 2.95 | 2.33 | 1.73 | -1.22 | -4.18 | -7.33 | -18.27 | -31.07 | -38.25
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | Steady Progression | Headroom (MW) | Thermal | 7.3 | 7.26 | 7.27 | 7.24 | 7.2 | 7.15 | 7.1 | 6.68 | 6.22 | 5.38 | 4.7 | 3.85 | 1.9 | -0.02 | -2.57 | -5.84 | -9.22 | -12.84
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | System Transformation | Headroom (MW) | Thermal | 7.3 | 7.23 | 7.19 | 7.11 | 6.96 | 6.77 | 6.54 | 4.86 | 2.47 | -0.07 | -2.89 | -6.15 | -9.64 | -12.75 | -16.65 | -23.09 | -30.63 | -39.76
Grendon 132kV | Northampton East | OLNEY 33 11kV S STN | Primary | 11 | -0.7113 | 52.154 | WPD Best View | Headroom (MW) | Thermal | 7.3 | 7.19 | 7.1 | 6.94 | 6.55 | 6.15 | 5.74 | 5.21 | 4.37 | 3.66 | 2.97 | 2.24 | -0.61 | -3.34 | -6.32 | -15.47 | -26.16 | -32.2
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Consumer Transformation | Headroom (MW) | N/A | 16.46 | 16.37 | 16.3 | 16.22 | 15.95 | 15.64 | 15.35 | 15.09 | 14.84 | 14.62 | 14.41 | 14.2 | 13.98 | 13.74 | 13.44 | 11.26 | 8.04 | 4.43
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Leading the Way | Headroom (MW) | N/A | 16.46 | 16.36 | 16.29 | 16.2 | 15.89 | 15.56 | 15.26 | 14.98 | 14.73 | 14.5 | 14.24 | 13.98 | 13.69 | 13.36 | 12.95 | 10.18 | 6.42 | 1.42
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | Steady Progression | Headroom (MW) | N/A | 16.46 | 16.39 | 16.36 | 16.32 | 16.27 | 16.24 | 16.2 | 16.16 | 16.13 | 16.09 | 16.05 | 16.01 | 15.97 | 15.92 | 15.88 | 15.7 | 15.43 | 14.79
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | System Transformation | Headroom (MW) | N/A | 16.46 | 16.38 | 16.33 | 16.27 | 16.2 | 16.15 | 16.05 | 15.91 | 15.78 | 15.67 | 15.57 | 15.48 | 15.4 | 15.34 | 15.27 | 14.47 | 13 | 11.52
Grendon 132kV | Northampton East | WELLINGBOROUGH ROAD 33 11kV S STN | Primary | 11 | -0.8514 | 52.2519 | WPD Best View | Headroom (MW) | N/A | 16.46 | 16.36 | 16.29 | 16.2 | 15.89 | 15.56 | 15.26 | 14.98 | 14.73 | 14.5 | 14.24 | 13.98 | 13.69 | 13.36 | 12.95 | 10.18 | 6.42 | 1.42
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Consumer Transformation | Headroom (MW) | N/A | 18.18 | 18.01 | 17.9 | 17.79 | 17.58 | 17.48 | 17.37 | 17.26 | 17.16 | 17.04 | 16.92 | 16.8 | 16.68 | 16.56 | 16.44 | 14.36 | 11.55 | 8.43
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Leading the Way | Headroom (MW) | N/A | 18.18 | 17.99 | 17.88 | 17.75 | 17.49 | 17.38 | 17.26 | 17.14 | 17.02 | 16.89 | 16.74 | 16.58 | 16.43 | 16.27 | 16.05 | 13.59 | 10.37 | 6.11
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | Steady Progression | Headroom (MW) | N/A | 18.18 | 18.03 | 17.96 | 17.88 | 17.78 | 17.7 | 17.63 | 17.56 | 17.48 | 17.41 | 17.34 | 17.26 | 17.19 | 17.12 | 17.05 | 16.71 | 16.31 | 15.85
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | System Transformation | Headroom (MW) | N/A | 18.18 | 18.02 | 17.93 | 17.83 | 17.69 | 17.61 | 17.52 | 17.44 | 17.36 | 17.27 | 17.19 | 17.11 | 17.02 | 16.94 | 16.86 | 16.43 | 15.75 | 14.65
Grendon 132kV | Northampton West | ABINGTON 33 11kV S STN | Primary | 11 | -0.8765 | 52.2478 | WPD Best View | Headroom (MW) | N/A | 18.18 | 17.99 | 17.88 | 17.75 | 17.49 | 17.38 | 17.26 | 17.14 | 17.02 | 16.89 | 16.74 | 16.58 | 16.43 | 16.27 | 16.05 | 13.59 | 10.37 | 6.11
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Consumer Transformation | Headroom (MW) | N/A | 12.17 | 12.19 | 11.95 | 11.88 | 11.67 | 11.47 | 11.23 | 11.01 | 10.79 | 10.58 | 10.36 | 10.14 | 9.88 | 9.63 | 9.38 | 7.75 | 4.86 | 2.54
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Leading the Way | Headroom (MW) | Thermal | 12.17 | 12.2 | 11.97 | 11.9 | 11.67 | 11.46 | 11.21 | 10.96 | 10.72 | 10.49 | 10.24 | 9.96 | 9.64 | 9.36 | 9.05 | 7.16 | 3.16 | -0.04
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | Steady Progression | Headroom (MW) | N/A | 12.17 | 12.23 | 12.26 | 12.29 | 12.31 | 12.3 | 12.28 | 12.24 | 12.2 | 12.16 | 12.11 | 12.07 | 12.03 | 11.99 | 11.96 | 11.92 | 11.61 | 11.03
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | System Transformation | Headroom (MW) | N/A | 12.17 | 12.22 | 12.23 | 12.02 | 11.97 | 11.9 | 11.78 | 11.65 | 11.53 | 11.41 | 11.28 | 11.15 | 11.03 | 10.94 | 10.85 | 10.28 | 8.4 | 7.35
Grendon 132kV | Northampton West | BANBURY LANE 33 11kV S STN | Primary | 11 | -0.9457 | 52.2152 | WPD Best View | Headroom (MW) | Thermal | 12.17 | 12.2 | 11.97 | 11.9 | 11.67 | 11.46 | 11.21 | 10.96 | 10.72 | 10.49 | 10.24 | 9.96 | 9.64 | 9.36 | 9.05 | 7.16 | 3.16 | -0.04
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Consumer Transformation | Headroom (MW) | Thermal | 5.8 | 5.77 | 5.77 | 5.7 | 5.56 | 5.45 | 5.34 | 5.01 | 4.64 | 4.21 | 3.71 | 3.14 | 2.53 | 1.96 | 1.26 | -0.31 | -2.28 | -4.62
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Leading the Way | Headroom (MW) | Thermal | 5.8 | 5.78 | 5.78 | 5.7 | 5.54 | 5.42 | 5.31 | 5.2 | 5.1 | 5 | 4.89 | 4.79 | 4.3 | 3.83 | 3.32 | 1.53 | -0.91 | -2.61
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | Steady Progression | Headroom (MW) | N/A | 5.8 | 5.8 | 5.82 | 5.81 | 5.79 | 5.76 | 5.74 | 5.67 | 5.59 | 5.49 | 5.37 | 5.23 | 4.91 | 4.6 | 4.19 | 3.66 | 3.08 | 2.32
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | System Transformation | Headroom (MW) | Thermal | 5.8 | 5.79 | 5.81 | 5.77 | 5.71 | 5.66 | 5.6 | 5.33 | 4.98 | 4.59 | 4.13 | 3.61 | 3.04 | 2.54 | 1.9 | 0.9 | -0.57 | -2.29
Grendon 132kV | Northampton West | BUGBROOKE 33 11kV S STN | Primary | 11 | -0.9988 | 52.2147 | WPD Best View | Headroom (MW) | Thermal | 5.8 | 5.78 | 5.78 | 5.7 | 5.54 | 5.42 | 5.31 | 5.2 | 5.1 | 5 | 4.89 | 4.79 | 4.3 | 3.83 | 3.32 | 1.53 | -0.91 | -2.61
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Consumer Transformation | Headroom (MW) | N/A | 15.89 | 16 | 16.15 | 16.19 | 16.04 | 15.62 | 15.26 | 14.92 | 14.61 | 14.31 | 14 | 13.69 | 13.37 | 13.03 | 12.66 | 9.97 | 6.03 | 1.63
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Leading the Way | Headroom (MW) | Thermal | 15.89 | 16.02 | 16.19 | 16.22 | 15.99 | 15.53 | 15.15 | 14.82 | 14.52 | 14.21 | 13.85 | 13.49 | 13.11 | 12.68 | 12.19 | 8.84 | 4.29 | -1.79
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | Steady Progression | Headroom (MW) | N/A | 15.89 | 16.01 | 16.18 | 16.25 | 16.24 | 16.23 | 16.25 | 16.26 | 16.26 | 16.23 | 16.19 | 16.16 | 16.11 | 16.06 | 16.02 | 15.8 | 15.41 | 14.8
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | System Transformation | Headroom (MW) | N/A | 15.89 | 16.02 | 16.19 | 16.26 | 16.21 | 16.18 | 16.16 | 16.11 | 15.97 | 15.83 | 15.68 | 15.54 | 15.42 | 15.31 | 15.22 | 14.37 | 12.54 | 10.71
Grendon 132kV | Northampton West | ELLESMERE AVENUE 33 11kV S STN | Primary | 11 | -0.9315 | 52.2418 | WPD Best View | Headroom (MW) | Thermal | 15.89 | 16.02 | 16.19 | 16.22 | 15.99 | 15.53 | 15.15 | 14.82 | 14.52 | 14.21 | 13.85 | 13.49 | 13.11 | 12.68 | 12.19 | 8.84 | 4.29 | -1.79
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Consumer Transformation | Headroom (MW) | N/A | 14.095 | 14.035 | 13.885 | 13.695 | 13.255 | 12.895 | 12.565 | 12.245 | 11.945 | 11.675 | 11.405 | 11.145 | 10.865 | 10.555 | 10.235 | 7.925 | 4.715 | 1.135
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Leading the Way | Headroom (MW) | Thermal | 14.095 | 14.025 | 13.875 | 13.665 | 13.155 | 12.785 | 12.425 | 12.105 | 11.805 | 11.515 | 11.205 | 10.905 | 10.585 | 10.215 | 9.795 | 7.005 | 3.305 | -1.625
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | Steady Progression | Headroom (MW) | N/A | 9.1217 | 9.1108 | 9.1005 | 9.0899 | 9.0781 | 9.0576 | 9.0358 | 9.0124 | 8.9903 | 8.9626 | 8.9349 | 8.9078 | 8.8811 | 8.854 | 8.8281 | 8.6955 | 8.5427 | 8.3849
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | System Transformation | Headroom (MW) | N/A | 13.0348 | 13.0015 | 12.9619 | 12.9156 | 12.8373 | 12.7484 | 12.651 | 12.5576 | 12.4628 | 12.3681 | 12.2649 | 12.1581 | 12.0509 | 11.9415 | 11.8325 | 11.2876 | 10.175 | 8.715
Grendon 132kV | Northampton West | KINGSTHORPE 33 11kV S STN | Primary | 11 | -0.9006 | 52.2645 | WPD Best View | Headroom (MW) | Thermal | 13.5906 | 13.5298 | 13.4542 | 13.3564 | 13.1472 | 12.845 | 12.495 | 12.185 | 11.885 | 11.615 | 11.315 | 11.015 | 10.705 | 10.335 | 9.935 | 7.205 | 3.575 | -1.235
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Consumer Transformation | Headroom (MW) | N/A | 63.03 | 62.96 | 62.92 | 62.87 | 62.68 | 62.51 | 62.17 | 61.82 | 61.45 | 61.07 | 60.68 | 60.27 | 59.83 | 59.48 | 59.11 | 56.85 | 54.38 | 51.64
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Leading the Way | Headroom (MW) | N/A | 63.03 | 62.95 | 62.91 | 62.85 | 62.58 | 62.36 | 62.01 | 61.63 | 61.22 | 60.79 | 60.35 | 59.87 | 59.36 | 58.98 | 58.59 | 56.38 | 53.63 | 50.11
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | Steady Progression | Headroom (MW) | N/A | 51.4379 | 51.4279 | 51.4201 | 51.4114 | 51.4002 | 51.3797 | 51.3566 | 51.3296 | 51.3009 | 51.2685 | 51.2306 | 51.1882 | 51.1397 | 51.0948 | 51.0522 | 50.9062 | 50.7945 | 50.6796
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | System Transformation | Headroom (MW) | N/A | 63.03 | 62.97 | 62.94 | 62.9 | 62.77 | 62.73 | 62.69 | 62.61 | 62.41 | 62.19 | 61.97 | 61.73 | 61.48 | 61.3 | 61.13 | 60.29 | 59.01 | 57.73
Grendon 132kV | Northampton West | NORTHAMPTON WEST 11kV S STN | Primary | 11 | -0.9134 | 52.245 | WPD Best View | Headroom (MW) | N/A | 63.03 | 62.95 | 62.91 | 62.85 | 62.58 | 62.36 | 62.01 | 61.63 | 61.22 | 60.79 | 60.35 | 59.87 | 59.36 | 58.98 | 58.59 | 56.38 | 53.63 | 50.11
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Consumer Transformation | Headroom (MW) | N/A | 11.86 | 11.76 | 11.7 | 11.63 | 11.49 | 11.38 | 11.35 | 11.3 | 11.19 | 11.08 | 10.95 | 10.82 | 10.68 | 10.52 | 10.35 | 9.56 | 8.72 | 7.85
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Leading the Way | Headroom (MW) | N/A | 11.86 | 11.76 | 11.69 | 11.62 | 11.47 | 11.35 | 11.36 | 11.34 | 11.21 | 11.08 | 10.94 | 10.78 | 10.61 | 10.42 | 10.23 | 9.36 | 8.46 | 7.28
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | Steady Progression | Headroom (MW) | N/A | 11.86 | 11.79 | 11.75 | 11.71 | 11.67 | 11.63 | 11.64 | 11.66 | 11.64 | 11.63 | 11.61 | 11.59 | 11.58 | 11.55 | 11.53 | 11.5 | 11.32 | 11.03
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | System Transformation | Headroom (MW) | N/A | 11.86 | 11.78 | 11.73 | 11.67 | 11.6 | 11.54 | 11.56 | 11.56 | 11.51 | 11.45 | 11.38 | 11.31 | 11.24 | 11.15 | 11.06 | 10.75 | 10.28 | 9.83
Grendon 132kV | Oakham | EMPINGHAM 33 11kV S STN | Primary | 11 | -0.5957 | 52.6622 | WPD Best View | Headroom (MW) | N/A | 11.86 | 11.78 | 11.73 | 11.67 | 11.6 | 11.54 | 11.56 | 11.56 | 11.51 | 11.45 | 11.38 | 11.31 | 11.24 | 11.15 | 11.06 | 10.75 | 10.28 | 9.83
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Consumer Transformation | Headroom (MW) | N/A | 3.62 | 3.59 | 3.55 | 3.51 | 3.42 | 3.35 | 3.28 | 3.22 | 3.17 | 3.12 | 3.07 | 3.02 | 2.96 | 2.91 | 2.85 | 2.43 | 1.87 | 1.23
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Leading the Way | Headroom (MW) | N/A | 3.62 | 3.58 | 3.55 | 3.51 | 3.41 | 3.34 | 3.26 | 3.2 | 3.15 | 3.1 | 3.04 | 2.98 | 2.91 | 2.84 | 2.77 | 2.27 | 1.63 | 0.76
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | Steady Progression | Headroom (MW) | N/A | 3.62 | 3.6 | 3.59 | 3.57 | 3.56 | 3.54 | 3.53 | 3.51 | 3.5 | 3.48 | 3.47 | 3.46 | 3.45 | 3.45 | 3.44 | 3.45 | 3.39 | 3.25
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | System Transformation | Headroom (MW) | N/A | 3.62 | 3.59 | 3.57 | 3.55 | 3.51 | 3.48 | 3.44 | 3.41 | 3.37 | 3.35 | 3.32 | 3.3 | 3.28 | 3.26 | 3.25 | 3.14 | 2.86 | 2.6
Grendon 132kV | Oakham | EXTON 33 11kV S STN | Primary | 11 | -0.6525 | 52.686 | WPD Best View | Headroom (MW) | N/A | 3.62 | 3.59 | 3.57 | 3.55 | 3.51 | 3.48 | 3.44 | 3.41 | 3.37 | 3.35 | 3.32 | 3.3 | 3.28 | 3.26 | 3.25 | 3.14 | 2.86 | 2.6
Bicker Fen 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Consumer Transformation | Headroom (MW) | Thermal | 4.93 | 4.87 | 4.82 | 4.76 | 4.63 | 4.48 | 4.11 | 3.17 | 2.22 | 1.19 | 0 | -1.31 | -2.71 | -4.03 | -5.64 | -9.65 | -14.26 | -19.55
Bicker Fen 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Leading the Way | Headroom (MW) | Thermal | 4.93 | 4.87 | 4.82 | 4.76 | 4.62 | 4.43 | 3.99 | 3.59 | 3.23 | 2.77 | 2.47 | 2.19 | 1.13 | 0.07 | -1.06 | -4.93 | -9.87 | -12.71
Bicker Fen 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | Steady Progression | Headroom (MW) | Thermal | 4.93 | 4.89 | 4.87 | 4.85 | 4.83 | 4.8 | 4.77 | 4.64 | 4.48 | 4.13 | 3.89 | 3.57 | 2.88 | 2.23 | 1.37 | 0.25 | -1 | -2.32
Bicker Fen 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | System Transformation | Headroom (MW) | Thermal | 4.93 | 4.88 | 4.85 | 4.82 | 4.75 | 4.66 | 4.56 | 4.06 | 3.26 | 2.47 | 1.5 | 0.39 | -0.8 | -1.85 | -3.15 | -5.27 | -8.08 | -11.49
Bicker Fen 132kV | Oakham | MARKET OVERTON 33 11kV S STN | Primary | 11 | -0.6665 | 52.7588 | WPD Best View | Headroom (MW) | Thermal | 4.93 | 4.88 | 4.83 | 4.78 | 4.67 | 4.53 | 4.18 | 3.25 | 2.3 | 1.29 | 0.11 | -1.2 | -2.59 | -3.89 | -5.47 | -9.32 | -13.83 | -19.01
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Consumer Transformation | Headroom (MW) | Thermal | 15.05 | 14.86 | 14.72 | 14.54 | 14.09 | 13.68 | 13.38 | 12.38 | 11.24 | 9.96 | 8.32 | 6.46 | 4.47 | 2.63 | 0.38 | -5.2 | -12.37 | -20.91
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Leading the Way | Headroom (MW) | Thermal | 15.05 | 14.85 | 14.69 | 14.51 | 13.99 | 13.52 | 13.2 | 12.73 | 12.27 | 11.83 | 11.33 | 10.84 | 9.19 | 7.58 | 5.88 | -0.55 | -9.31 | -15.69
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | Steady Progression | Headroom (MW) | N/A | 15.05 | 14.94 | 14.88 | 14.83 | 14.75 | 14.7 | 14.7 | 14.49 | 14.29 | 14.04 | 13.71 | 13.3 | 12.36 | 11.43 | 10.18 | 8.64 | 6.77 | 4.42
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | System Transformation | Headroom (MW) | Thermal | 15.05 | 14.9 | 14.81 | 14.7 | 14.5 | 14.37 | 14.32 | 13.53 | 12.5 | 11.44 | 10.03 | 8.4 | 6.65 | 5.08 | 3.12 | -0.05 | -5.24 | -11.41
Grendon 132kV | Oakham | OAKHAM 11kV S STN | Primary | 11 | -0.7096 | 52.6682 | WPD Best View | Headroom (MW) | Thermal | 15.05 | 14.9 | 14.8 | 14.69 | 14.48 | 14.34 | 14.27 | 13.47 | 12.44 | 11.37 | 9.95 | 8.31 | 6.55 | 4.97 | 3 | -0.26 | -5.52 | -11.79
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Consumer Transformation | Headroom (MW) | Thermal | 4.23 | 4.15 | 4.08 | 4 | 3.8 | 3.66 | 3.55 | 2.94 | 2.19 | 1.31 | 0.03 | -1.47 | -3.09 | -4.58 | -6.42 | -9.69 | -14.63 | -19.88
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Leading the Way | Headroom (MW) | Thermal | 4.23 | 4.14 | 4.07 | 3.99 | 3.76 | 3.61 | 3.5 | 3.42 | 3.3 | 3.18 | 3.04 | 2.9 | 1.67 | 0.46 | -0.8 | -4.58 | -11.35 | -13.77
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | Steady Progression | Headroom (MW) | Thermal | 4.23 | 4.18 | 4.16 | 4.14 | 4.11 | 4.07 | 4.06 | 3.92 | 3.78 | 3.59 | 3.3 | 2.95 | 2.08 | 1.24 | 0.09 | -1.31 | -2.99 | -4.84
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | System Transformation | Headroom (MW) | Thermal | 4.23 | 4.17 | 4.12 | 4.08 | 3.99 | 3.92 | 3.88 | 3.32 | 2.6 | 1.78 | 0.55 | -0.89 | -2.45 | -3.84 | -5.59 | -8.11 | -12.41 | -16.9
Grendon 132kV | Oakham | UPPINGHAM 33 11kV S STN | Primary | 11 | -0.719 | 52.5955 | WPD Best View | Headroom (MW) | Thermal | 4.23 | 4.17 | 4.12 | 4.08 | 3.99 | 3.91 | 3.86 | 3.31 | 2.58 | 1.76 | 0.52 | -0.92 | -2.48 | -3.87 | -5.63 | -8.17 | -12.49 | -17
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Consumer Transformation | Headroom (MW) | N/A | 19.51 | 19.36 | 19.26 | 19.06 | 18.49 | 18.06 | 17.64 | 17.3 | 16.99 | 16.66 | 16.34 | 16.04 | 15.71 | 15.37 | 15 | 12.25 | 8.21 | 3.71
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Leading the Way | Headroom (MW) | N/A | 19.51 | 19.34 | 19.24 | 19.01 | 18.37 | 17.91 | 17.48 | 17.15 | 16.86 | 16.51 | 16.14 | 15.78 | 15.39 | 14.95 | 14.46 | 11.12 | 6.49 | 4.02
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | Steady Progression | Headroom (MW) | N/A | 15.3912 | 15.3843 | 15.3781 | 15.3716 | 15.3628 | 15.3423 | 15.3196 | 15.2937 | 15.2676 | 15.2352 | 15.2032 | 15.1717 | 15.14 | 15.1082 | 15.0777 | 14.9155 | 14.7275 | 14.5342
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | System Transformation | Headroom (MW) | N/A | 19.51 | 19.38 | 19.3 | 19.22 | 19.01 | 18.8 | 18.57 | 18.41 | 18.27 | 18.11 | 17.96 | 17.83 | 17.7 | 17.6 | 17.5 | 16.84 | 14.87 | 12.89
Grendon 132kV | Wellingborough | CANNON STREET 33 11kV S STN | Primary | 11 | -0.6892 | 52.3051 | WPD Best View | Headroom (MW) | N/A | 19.51 | 19.38 | 19.3 | 19.22 | 19.01 | 18.8 | 18.57 | 18.4 | 18.27 | 18.1 | 17.95 | 17.82 | 17.69 | 17.58 | 17.49 | 16.83 | 14.85 | 12.88
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Consumer Transformation | Headroom (MW) | Thermal | 4.98 | 4.94 | 4.91 | 4.87 | 4.76 | 4.69 | 4.28 | 3.28 | 2.41 | 1.51 | 0.5 | -0.57 | -1.68 | -2.76 | -4.04 | -7.81 | -12.49 | -17.62
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Leading the Way | Headroom (MW) | Thermal | 4.98 | 4.94 | 4.91 | 4.87 | 4.76 | 4.69 | 4.25 | 3.88 | 3.6 | 3.18 | 2.82 | 2.48 | 1.65 | 0.81 | -0.09 | -3.47 | -7.87 | -11.17
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | Steady Progression | Headroom (MW) | N/A | 4.98 | 4.96 | 4.95 | 4.93 | 4.92 | 4.9 | 4.88 | 4.8 | 4.66 | 4.22 | 4.04 | 3.82 | 3.35 | 2.93 | 2.4 | 1.66 | 0.89 | 0.04
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | System Transformation | Headroom (MW) | Thermal | 4.98 | 4.95 | 4.93 | 4.91 | 4.86 | 4.83 | 4.8 | 4.5 | 3.82 | 3.27 | 2.6 | 1.85 | 1.07 | 0.39 | -0.46 | -1.97 | -4.03 | -6.47
Grendon 132kV | Wellingborough | HARROLD 33 11kV S STN | Primary | 11 | -0.6048 | 52.2063 | WPD Best View | Headroom (MW) | Thermal | 4.98 | 4.94 | 4.91 | 4.87 | 4.76 | 4.69 | 4.48 | 4.29 | 3.97 | 3.7 | 3.43 | 3.2 | 2.49 | 1.82 | 1.1 | -1.43 | -4.79 | -7.04
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Consumer Transformation | Headroom (MW) | N/A | 15.57 | 15.37 | 15.35 | 15.21 | 14.81 | 14.54 | 14.28 | 13.99 | 13.71 | 13.44 | 13.06 | 12.64 | 12.21 | 11.79 | 11.3 | 9.19 | 6.41 | 3.18
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Leading the Way | Headroom (MW) | N/A | 15.57 | 15.35 | 15.34 | 15.2 | 14.73 | 14.44 | 14.16 | 13.89 | 13.63 | 13.38 | 13.12 | 12.87 | 12.45 | 12.02 | 11.55 | 9.17 | 5.94 | 2.47
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | Steady Progression | Headroom (MW) | N/A | 15.57 | 15.43 | 15.46 | 15.41 | 15.32 | 15.24 | 15.17 | 15.08 | 15.01 | 14.92 | 14.8 | 14.69 | 14.51 | 14.34 | 14.14 | 13.77 | 13.15 | 12.27
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | System Transformation | Headroom (MW) | N/A | 15.57 | 15.4 | 15.42 | 15.33 | 15.14 | 15 | 14.85 | 14.67 | 14.49 | 14.32 | 14.03 | 13.73 | 13.41 | 13.12 | 12.8 | 11.9 | 10.23 | 8.41
Grendon 132kV | Wellingborough | LITTLE IRCHESTER 33 11kV S STN | Primary | 11 | -0.6796 | 52.2875 | WPD Best View | Headroom (MW) | N/A | 15.57 | 15.4 | 15.42 | 15.33 | 15.14 | 15 | 14.85 | 14.67 | 14.49 | 14.32 | 14.03 | 13.73 | 13.41 | 13.12 | 12.8 | 11.9 | 10.23 | 8.41
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Consumer Transformation | Headroom (MW) | N/A | 15.49 | 15.39 | 15.33 | 15.27 | 15.12 | 14.99 | 14.74 | 14.53 | 14.31 | 14.11 | 13.91 | 13.71 | 13.51 | 13.3 | 13.09 | 11.58 | 9.61 | 7.4
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Leading the Way | Headroom (MW) | N/A | 15.49 | 15.38 | 15.32 | 15.25 | 15.05 | 14.91 | 14.64 | 14.43 | 14.21 | 13.99 | 13.77 | 13.55 | 13.32 | 13.08 | 12.8 | 11.05 | 8.8 | 5.83
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | Steady Progression | Headroom (MW) | N/A | 15.49 | 15.41 | 15.37 | 15.33 | 15.27 | 15.24 | 15.2 | 15.17 | 15.13 | 15.09 | 15.05 | 15.01 | 14.97 | 14.93 | 14.89 | 14.69 | 14.43 | 14.12
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | System Transformation | Headroom (MW) | N/A | 15.49 | 15.4 | 15.35 | 15.3 | 15.21 | 15.18 | 15.13 | 15.09 | 15.03 | 14.91 | 14.8 | 14.7 | 14.61 | 14.52 | 14.44 | 13.97 | 12.96 | 11.95
Grendon 132kV | Wellingborough | PARK FARM 33 11kV S STN | Primary | 11 | -0.7389 | 52.2994 | WPD Best View | Headroom (MW) | N/A | 15.49 | 15.4 | 15.35 | 15.3 | 15.21 | 15.18 | 15.13 | 15.09 | 15.03 | 14.91 | 14.8 | 14.7 | 14.61 | 14.52 | 14.44 | 13.97 | 12.96 | 11.95
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Consumer Transformation | Headroom (MW) | Thermal | 1.84 | 1.99 | 1.92 | 1.82 | 1.59 | 1.39 | 1.17 | 0.94 | 0.72 | 0.5 | 0.3 | 0.08 | -0.13 | -0.37 | -0.61 | -2.82 | -4.29 | -5.91
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Leading the Way | Headroom (MW) | Thermal | 1.84 | 2.01 | 1.94 | 1.83 | 1.55 | 1.32 | 1.09 | 0.85 | 0.59 | 0.36 | 0.13 | -0.1 | -0.35 | -0.6 | -0.86 | -3.17 | -4.82 | -7.01
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | Steady Progression | Headroom (MW) | N/A | 1.84 | 2 | 1.99 | 1.98 | 1.96 | 1.94 | 1.92 | 1.9 | 1.87 | 1.83 | 1.8 | 1.76 | 1.73 | 1.7 | 1.67 | 1.6 | 1.41 | 1.05
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | System Transformation | Headroom (MW) | Thermal | 1.84 | 2.01 | 1.98 | 1.93 | 1.84 | 1.76 | 1.64 | 1.52 | 1.4 | 1.29 | 1.18 | 1.06 | 0.95 | 0.83 | 0.72 | -0.21 | -0.92 | -1.61
Grendon 132kV | Wellingborough | SHARNBROOK 33 11kV S STN | Primary | 11 | -0.5653 | 52.2283 | WPD Best View | Headroom (MW) | Thermal | 1.84 | 2.02 | 1.96 | 1.88 | 1.66 | 1.48 | 1.29 | 1.11 | 0.91 | 0.74 | 0.57 | 0.39 | 0.2 | 0.01 | -0.19 | -2.13 | -3.43 | -5.11
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Consumer Transformation | Headroom (MW) | N/A | 20.03 | 19.91 | 19.83 | 19.73 | 19.55 | 19.34 | 19.14 | 18.94 | 18.74 | 18.55 | 18.42 | 18.29 | 18.15 | 18 | 17.85 | 16.56 | 14.24 | 12.77
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Leading the Way | Headroom (MW) | Thermal | 20.03 | 19.91 | 19.82 | 19.72 | 19.52 | 19.28 | 19.04 | 18.79 | 18.54 | 1.97 | 1.81 | 1.66 | 1.49 | 1.32 | 1.13 | -0.28 | -3.87 | -5.73
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | Steady Progression | Headroom (MW) | N/A | 20.03 | 19.93 | 19.88 | 19.83 | 19.77 | 19.71 | 19.64 | 19.58 | 19.52 | 19.46 | 19.41 | 19.35 | 19.31 | 19.26 | 19.22 | 19.08 | 18.79 | 18.42
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | System Transformation | Headroom (MW) | N/A | 20.03 | 19.92 | 19.85 | 19.79 | 19.69 | 19.56 | 19.43 | 19.3 | 19.16 | 19.04 | 18.95 | 18.87 | 18.79 | 18.72 | 18.65 | 18.22 | 16.54 | 15.82
Grendon 132kV | Wellingborough 132 11 | Wellingborough 132/11kv (Reserve) | Primary | 11 | -0.6846 | 52.2923 | WPD Best View | Headroom (MW) | N/A | 20.03 | 19.92 | 19.85 | 19.79 | 19.69 | 19.56 | 19.43 | 19.3 | 19.16 | 19.04 | 18.95 | 18.87 | 18.79 | 18.72 | 18.65 | 18.22 | 16.54 | 15.82
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Consumer Transformation | Headroom (MW) | Thermal | 11.96 | 11.82 | 11.69 | 11.67 | 11.42 | 11.11 | 10.54 | 9.74 | 9.09 | 8.46 | 7.82 | 7.21 | 6.62 | 5.99 | 5.31 | 1.18 | -3.58 | -8.71
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Leading the Way | Headroom (MW) | Thermal | 11.96 | 11.81 | 11.68 | 11.69 | 11.44 | 11.12 | 10.51 | 9.93 | 9.4 | 8.78 | 8.19 | 7.64 | 7.08 | 6.49 | 5.86 | 1.56 | -2.99 | -8.56
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | Steady Progression | Headroom (MW) | N/A | 11.96 | 11.88 | 11.85 | 11.94 | 12.02 | 11.99 | 11.96 | 11.92 | 11.84 | 11.56 | 11.48 | 11.39 | 11.27 | 11.18 | 11.11 | 10.89 | 10.45 | 9.72
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | System Transformation | Headroom (MW) | N/A | 11.96 | 11.85 | 11.78 | 11.84 | 11.83 | 11.71 | 11.56 | 11.39 | 11.02 | 10.76 | 10.47 | 10.21 | 9.99 | 9.8 | 9.62 | 8.25 | 6.52 | 4.73
Lea Marston 132kV | Tamworth | ATHERSTONE 33 11kV S STN | Primary | 11 | -1.5492 | 52.585 | WPD Best View | Headroom (MW) | Thermal | 11.96 | 11.82 | 11.69 | 11.67 | 11.42 | 11.11 | 10.54 | 9.74 | 9.09 | 8.46 | 7.82 | 7.21 | 6.62 | 5.99 | 5.31 | 1.18 | -3.58 | -8.71
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Consumer Transformation | Headroom (MW) | N/A | 19.72 | 19.88 | 17.39 | 17.39 | 17.46 | 17.47 | 17.45 | 17.46 | 17.43 | 17.41 | 17.38 | 17.35 | 17.33 | 17.3 | 17.27 | 16.79 | 16.57 | 16.34
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Leading the Way | Headroom (MW) | N/A | 19.72 | 19.9 | 17.43 | 17.42 | 17.49 | 17.48 | 17.45 | 17.48 | 17.45 | 17.42 | 13.42 | 13.39 | 13.36 | 13.33 | 13.29 | 12.47 | 12.22 | 11.95
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | Steady Progression | Headroom (MW) | N/A | 19.72 | 19.86 | 17.35 | 17.36 | 17.44 | 17.46 | 17.48 | 17.5 | 17.5 | 17.48 | 17.47 | 17.45 | 17.44 | 17.42 | 17.4 | 17.31 | 17.19 | 17.06
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | System Transformation | Headroom (MW) | N/A | 19.72 | 19.88 | 17.39 | 17.4 | 17.48 | 17.49 | 17.48 | 17.49 | 17.48 | 17.46 | 17.44 | 17.42 | 17.4 | 17.37 | 17.35 | 16.95 | 16.79 | 16.63
Lea Marston 132kV | Tamworth | BIRCH COPPICE 33 11kV S STN | Primary | 11 | -1.6266 | 52.5925 | WPD Best View | Headroom (MW) | N/A | 19.72 | 19.88 | 17.39 | 17.39 | 17.46 | 17.47 | 17.45 | 17.46 | 17.43 | 17.41 | 17.38 | 17.35 | 17.33 | 17.3 | 17.27 | 16.79 | 16.57 | 16.34
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Consumer Transformation | Headroom (MW) | Thermal | 5.47 | 5.41 | 5.33 | 5.22 | 4.91 | 4.63 | 4.13 | 3.22 | 2.41 | 1.59 | 0.67 | -0.29 | -1.28 | -2.26 | -3.42 | -8.18 | -13.79 | -19.99
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Leading the Way | Headroom (MW) | Thermal | 5.47 | 5.4 | 5.33 | 5.22 | 4.89 | 4.58 | 4.03 | 3.53 | 3.08 | 2.54 | 2.06 | 1.59 | 0.72 | -0.15 | -1.11 | -5.69 | -11.45 | -16.85
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | Steady Progression | Headroom (MW) | N/A | 5.47 | 5.46 | 5.47 | 5.47 | 5.46 | 5.44 | 5.42 | 5.35 | 5.24 | 4.91 | 4.75 | 4.56 | 4.19 | 3.86 | 3.44 | 2.9 | 1.97 | 0.86
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | System Transformation | Headroom (MW) | Thermal | 5.47 | 5.44 | 5.42 | 5.38 | 5.28 | 5.17 | 5.04 | 4.73 | 4.15 | 3.66 | 3.07 | 2.43 | 1.76 | 1.19 | 0.5 | -1.11 | -3.7 | -6.58
Lea Marston 132kV | Tamworth | POLESWORTH 33 11kV S STN | Primary | 11 | -1.6131 | 52.6164 | WPD Best View | Headroom (MW) | Thermal | 5.47 | 5.41 | 5.34 | 5.25 | 4.98 | 4.75 | 4.3 | 3.45 | 2.69 | 1.93 | 1.05 | 0.13 | -0.82 | -1.77 | -2.88 | -7.05 | -12.52 | -18.46
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Consumer Transformation | Headroom (MW) | N/A | 23.32 | 23.26 | 23.23 | 23.16 | 22.63 | 22.05 | 21.49 | 20.98 | 20.5 | 20.06 | 19.61 | 19.17 | 18.71 | 18.2 | 17.66 | 13 | 8.69 | 2.29
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Leading the Way | Headroom (MW) | Thermal | 23.32 | 23.26 | 23.22 | 23.14 | 22.51 | 21.89 | 21.31 | 20.79 | 20.27 | 19.8 | 19.27 | 18.74 | 18.17 | 17.53 | 16.78 | 12.39 | 5.86 | -2.9
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | Steady Progression | Headroom (MW) | N/A | 23.32 | 23.3 | 23.31 | 23.31 | 23.31 | 23.26 | 23.21 | 23.15 | 23.08 | 23 | 22.92 | 22.83 | 22.74 | 22.64 | 22.54 | 22.09 | 21.46 | 21.82
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | System Transformation | Headroom (MW) | N/A | 23.32 | 23.29 | 23.28 | 23.26 | 23.2 | 23.11 | 22.82 | 22.55 | 22.3 | 22.07 | 21.84 | 21.63 | 21.44 | 21.28 | 21.12 | 19.59 | 18.19 | 15.38
Lea Marston 132kV | Tamworth | TAMWORTH GRID 11kV S STN | Primary | 11 | -1.6878 | 52.6322 | WPD Best View | Headroom (MW) | N/A | 23.32 | 23.31 | 23.33 | 23.33 | 23.33 | 23.27 | 23.19 | 23.11 | 23.03 | 22.94 | 22.83 | 22.7 | 22.59 | 22.5 | 22.41 | 21.46 | 20.45 | 20.09
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Consumer Transformation | Headroom (MW) | Thermal | 11.38 | 11.25 | 11.15 | 11.04 | 10.79 | 10.6 | 10.09 | 9.05 | 8.14 | 7.21 | 6.11 | 4.94 | 3.74 | 2.55 | 1.15 | -3.31 | -9.19 | -15.69
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Leading the Way | Headroom (MW) | Thermal | 11.38 | 11.24 | 11.14 | 11.03 | 10.76 | 10.57 | 10.04 | 9.58 | 9.21 | 8.72 | 8.26 | 7.83 | 6.88 | 5.9 | 4.85 | 0.61 | -5.14 | -10.11
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | Steady Progression | Headroom (MW) | N/A | 11.38 | 11.29 | 11.24 | 11.19 | 11.14 | 11.09 | 11.03 | 10.92 | 10.75 | 10.31 | 10.09 | 9.83 | 9.33 | 8.88 | 8.29 | 7.45 | 6.47 | 5.3
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | System Transformation | Headroom (MW) | Thermal | 11.38 | 11.27 | 11.2 | 11.13 | 11.02 | 10.92 | 10.82 | 10.47 | 9.78 | 9.21 | 8.47 | 7.65 | 6.79 | 6.05 | 5.15 | 3.39 | 0.68 | -2.5
Lea Marston 132kV | Tamworth | WOOD END 33 11kV S STN | Primary | 11 | -1.6299 | 52.5822 | WPD Best View | Headroom (MW) | Thermal | 11.38 | 11.25 | 11.16 | 11.05 | 10.82 | 10.64 | 10.46 | 10.04 | 9.52 | 8.69 | 7.98 | 7.16 | 6.26 | 5.45 | 4.48 | 2.22 | -0.76 | -4.31
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Consumer Transformation | Headroom (MW) | Thermal | 28.79 | 28.55 | 28.39 | 28.21 | 27.94 | 27.47 | 26.81 | 26.04 | 25.26 | 24.49 | 23.66 | 22.78 | 21.86 | 20.93 | 19.87 | 14.69 | 7.45 | -0.71
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Leading the Way | Headroom (MW) | Thermal | 28.79 | 28.54 | 28.36 | 28.16 | 27.83 | 27.31 | 26.6 | 25.96 | 25.35 | 24.77 | 24.17 | 23.56 | 22.61 | 21.61 | 20.49 | 14.26 | 5.84 | -3.98
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | Steady Progression | Headroom (MW) | N/A | 28.79 | 28.6 | 28.5 | 28.39 | 28.27 | 28.17 | 28.07 | 27.97 | 27.87 | 27.77 | 27.66 | 27.54 | 27.42 | 27.29 | 27.09 | 26.59 | 25.39 | 23.51
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | System Transformation | Headroom (MW) | N/A | 28.79 | 28.58 | 28.45 | 28.31 | 28.14 | 28.01 | 27.87 | 27.72 | 27.23 | 26.7 | 26.12 | 25.52 | 24.9 | 24.35 | 23.72 | 21.88 | 17.99 | 13.75
Lea Marston 132kV | Tamworth Town 132 11 | TAMWORTH TOWN 11kV S STN | Primary | 11 | -1.6873 | 52.6324 | WPD Best View | Headroom (MW) | N/A | 28.79 | 28.6 | 28.5 | 28.39 | 28.27 | 28.16 | 28.05 | 27.94 | 27.83 | 27.71 | 27.6 | 27.48 | 27.35 | 27.22 | 27.02 | 26.48 | 25.31 | 23.41
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Consumer Transformation | Headroom (MW) | N/A | 15.8 | 15.69 | 15.58 | 15.45 | 15.23 | 15.16 | 14.79 | 14.19 | 13.73 | 13.29 | 12.84 | 12.4 | 11.97 | 11.51 | 11.01 | 8.18 | 4.55 | 0.69
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Leading the Way | Headroom (MW) | N/A | 15.8 | 15.68 | 15.57 | 15.43 | 15.19 | 15.2 | 14.83 | 14.43 | 14.1 | 13.69 | 13.31 | 12.94 | 12.52 | 12.09 | 11.62 | 8.99 | 5.64 | 1.69
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | Steady Progression | Headroom (MW) | N/A | 15.8 | 15.71 | 15.67 | 15.63 | 15.63 | 15.71 | 15.71 | 15.68 | 15.61 | 15.37 | 15.31 | 15.24 | 15.16 | 15.11 | 15.06 | 14.93 | 14.56 | 14.01
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | System Transformation | Headroom (MW) | N/A | 15.8 | 15.7 | 15.64 | 15.56 | 15.5 | 15.54 | 15.49 | 15.39 | 15.13 | 14.97 | 14.79 | 14.63 | 14.48 | 14.36 | 14.24 | 13.57 | 12.29 | 10.96
Lea Marston 132kV | Tamworth Town 33 | APOLLO 33 11kV S STN | Primary | 11 | -1.7101 | 52.6382 | WPD Best View | Headroom (MW) | N/A | 15.8 | 15.71 | 15.67 | 15.63 | 15.63 | 15.71 | 15.71 | 15.68 | 15.61 | 15.37 | 15.31 | 15.24 | 15.16 | 15.11 | 15.06 | 14.93 | 14.56 | 14.01
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Consumer Transformation | Headroom (MW) | N/A | 33.46 | 33.01 | 32.91 | 32.94 | 32.71 | 32.51 | 32.38 | 32.2 | 32.06 | 31.71 | 31.59 | 31.47 | 31.36 | 31.24 | 31.11 | 28.78 | 24.52 | 19.71
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Leading the Way | Headroom (MW) | N/A | 33.46 | 32.99 | 32.91 | 33.02 | 32.83 | 32.74 | 32.68 | 32.55 | 32.43 | 31.85 | 31.74 | 31.65 | 31.52 | 31.36 | 31.16 | 27.95 | 23 | 16.58
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | Steady Progression | Headroom (MW) | N/A | 33.46 | 33.11 | 33.1 | 33.23 | 33.41 | 33.44 | 33.46 | 33.47 | 33.5 | 33.52 | 33.56 | 33.6 | 33.69 | 33.78 | 33.87 | 33.83 | 33.34 | 32.29
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | System Transformation | Headroom (MW) | N/A | 33.46 | 33.06 | 33.03 | 33.15 | 33.23 | 33.24 | 33.29 | 33.29 | 33.31 | 33.12 | 33.17 | 33.22 | 33.31 | 33.44 | 33.59 | 33.32 | 30.99 | 28.49
Ratcliffe 132kV | Loughborough 132 11 (GT1B1) | LOUGHBOROUGH 11kV S STN | Primary | 11 | -1.2096 | 52.7869 | WPD Best View | Headroom (MW) | N/A | 33.46 | 33.01 | 32.91 | 32.94 | 32.71 | 32.51 | 32.38 | 32.2 | 32.06 | 31.71 | 31.59 | 31.47 | 31.36 | 31.24 | 31.11 | 28.78 | 24.52 | 19.71
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Consumer Transformation | Headroom (MW) | N/A | 24.82 | 24.68 | 24.59 | 15.27 | 15.03 | 14.67 | 13.67 | 12.74 | 11.88 | 11.24 | 10.81 | 10.49 | 10.23 | 9.95 | 9.66 | 7 | 5.15 | 2.86
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Leading the Way | Headroom (MW) | N/A | 24.82 | 24.66 | 24.57 | 15.24 | 14.94 | 14.53 | 13.94 | 13.36 | 12.77 | 12.39 | 12.09 | 11.79 | 11.45 | 11.07 | 10.68 | 7.88 | 10 | 10.55
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | Steady Progression | Headroom (MW) | N/A | 24.82 | 24.7 | 24.63 | 15.34 | 15.25 | 15.18 | 14.19 | 13.22 | 12.27 | 11.39 | 10.59 | 9.93 | 9.57 | 9.29 | 9.11 | 8.8 | 8.29 | 7.86
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | System Transformation | Headroom (MW) | N/A | 24.82 | 24.69 | 24.61 | 15.31 | 15.17 | 15.06 | 14.3 | 13.51 | 12.79 | 12.28 | 11.97 | 11.79 | 11.67 | 11.57 | 11.48 | 10.81 | 10.42 | 9.77
Ratcliffe 132kV | Loughborough 33 | BRUSH 33 11kV S STN | Primary | 11 | -1.1937 | 52.7815 | WPD Best View | Headroom (MW) | N/A | 24.82 | 24.68 | 24.59 | 15.27 | 15.03 | 14.67 | 13.67 | 12.74 | 11.88 | 11.24 | 10.81 | 10.49 | 10.23 | 9.95 | 9.66 | 7 | 5.15 | 2.86
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Consumer Transformation | Headroom (MW) | Thermal | 16.42 | 16.19 | 15.99 | 15.76 | 15.25 | 14.83 | 14.44 | 13.78 | 13.07 | 12.34 | 11.41 | 10.37 | 9.2 | 8.1 | 6.77 | 2.51 | -3.32 | -10.09
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Leading the Way | Headroom (MW) | Thermal | 16.42 | 16.17 | 15.96 | 15.68 | 15.12 | 14.68 | 14.27 | 13.91 | 13.57 | 13.28 | 12.91 | 12.55 | 11.57 | 10.58 | 9.45 | 4.19 | -2.85 | -9.81
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | Steady Progression | Headroom (MW) | N/A | 16.42 | 16.31 | 16.27 | 16.25 | 16.24 | 16.21 | 16.19 | 16.06 | 15.95 | 15.81 | 15.64 | 15.46 | 15.02 | 14.61 | 14.05 | 13.48 | 12.2 | 10.41
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | System Transformation | Headroom (MW) | Thermal | 16.42 | 16.26 | 16.14 | 16.04 | 15.87 | 15.7 | 15.52 | 15.05 | 14.51 | 13.94 | 13.2 | 12.35 | 11.45 | 10.66 | 9.62 | 7.6 | 3.97 | -0.08
Ratcliffe 132kV | Loughborough 33 | QUORN 33 11kV S STN | Primary | 11 | -1.1742 | 52.7489 | WPD Best View | Headroom (MW) | Thermal | 16.42 | 16.19 | 15.99 | 15.76 | 15.25 | 14.83 | 14.44 | 13.78 | 13.07 | 12.34 | 11.41 | 10.37 | 9.2 | 8.1 | 6.77 | 2.51 | -3.32 | -10.09
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Consumer Transformation | Headroom (MW) | Thermal | 15.35 | 15.44 | 15.69 | 15.9 | 15.6 | 15.4 | 15.15 | 13.89 | 13.37 | 12.82 | 12.04 | 11.18 | 10.26 | 9.3 | 8.18 | 4.19 | -1.2 | -7.22
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Leading the Way | Headroom (MW) | Thermal | 15.35 | 15.46 | 15.76 | 16.05 | 15.71 | 14.71 | 14.42 | 14.13 | 13.81 | 13.48 | 13.02 | 12.54 | 11.67 | 10.78 | 9.81 | 5.6 | -0.29 | -6.38
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | Steady Progression | Headroom (MW) | N/A | 15.35 | 15.49 | 15.81 | 16.04 | 16.09 | 16.18 | 16.26 | 16.33 | 16.39 | 15.62 | 15.56 | 15.49 | 15.26 | 15.05 | 14.75 | 14.65 | 13.75 | 12.36
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | System Transformation | Headroom (MW) | N/A | 15.35 | 15.49 | 15.81 | 16.1 | 16.08 | 16.08 | 16.05 | 15.04 | 14.72 | 14.38 | 13.87 | 13.3 | 12.69 | 12.13 | 11.46 | 9.99 | 7.16 | 4.04
Ratcliffe 132kV | Loughborough 33 | SHEPSHED 33 11kV S STN | Primary | 11 | -1.2851 | 52.7697 | WPD Best View | Headroom (MW) | Thermal | 15.35 | 15.44 | 15.69 | 15.9 | 15.6 | 15.4 | 15.15 | 13.89 | 13.37 | 12.82 | 12.04 | 11.18 | 10.26 | 9.3 | 8.18 | 4.19 | -1.2 | -7.22
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Consumer Transformation | Headroom (MW) | N/A | 17.93 | 17.83 | 17.76 | 17.68 | 17.53 | 17.2 | 16.83 | 16.48 | 16.16 | 15.87 | 15.57 | 15.26 | 14.96 | 14.63 | 14.29 | 11.83 | 8.4 | 4.6
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Leading the Way | Headroom (MW) | N/A | 17.93 | 17.83 | 17.75 | 17.65 | 17.47 | 17.12 | 16.73 | 16.38 | 16.05 | 15.75 | 15.41 | 15.06 | 14.69 | 14.29 | 13.84 | 10.86 | 6.92 | 1.7
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | Steady Progression | Headroom (MW) | N/A | 17.93 | 17.86 | 17.82 | 17.78 | 17.73 | 17.69 | 17.65 | 17.61 | 17.57 | 17.53 | 17.48 | 17.44 | 17.39 | 17.34 | 17.29 | 17.07 | 16.75 | 16.28
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | System Transformation | Headroom (MW) | N/A | 17.93 | 17.85 | 17.8 | 17.73 | 17.65 | 17.6 | 17.55 | 17.48 | 17.36 | 17.21 | 17.06 | 16.92 | 16.79 | 16.68 | 16.58 | 15.82 | 14.21 | 12.63
Ratcliffe 132kV | Nottingham | BEESTON 33 11kV S STN | Primary | 11 | -1.2151 | 52.9303 | WPD Best View | Headroom (MW) | N/A | 17.93 | 17.83 | 17.76 | 17.67 | 17.52 | 17.19 | 16.81 | 16.46 | 16.13 | 15.84 | 15.53 | 15.22 | 14.89 | 14.55 | 14.19 | 11.6 | 8.06 | 3.94
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Consumer Transformation | Headroom (MW) | N/A | 19.29 | 19.16 | 19.1 | 19.04 | 18.8 | 18.65 | 18.49 | 18.33 | 18.2 | 18.08 | 17.95 | 17.82 | 17.7 | 17.56 | 17.44 | 16.48 | 15.19 | 13.79
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Leading the Way | Headroom (MW) | N/A | 19.29 | 19.15 | 19.1 | 19.03 | 18.75 | 18.64 | 18.49 | 18.33 | 18.22 | 18.1 | 17.97 | 17.84 | 17.7 | 17.56 | 17.4 | 16.23 | 14.7 | 12.78
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | Steady Progression | Headroom (MW) | N/A | 19.29 | 19.17 | 19.12 | 19.07 | 19.01 | 19.01 | 18.98 | 18.93 | 18.89 | 18.84 | 18.79 | 18.74 | 18.7 | 18.65 | 18.6 | 18.36 | 18.04 | 17.7
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | System Transformation | Headroom (MW) | N/A | 19.29 | 19.16 | 19.11 | 19.06 | 18.98 | 18.94 | 18.86 | 18.76 | 18.68 | 18.61 | 18.55 | 18.49 | 18.46 | 18.44 | 18.44 | 18.25 | 17.74 | 16.96
Ratcliffe 132kV | Nottingham | CASTLE ROAD 33 11kV S STN | Primary | 11 | -1.1518 | 52.9491 | WPD Best View | Headroom (MW) | N/A | 19.29 | 19.15 | 19.1 | 19.03 | 18.75 | 18.64 | 18.49 | 18.33 | 18.22 | 18.1 | 17.97 | 17.84 | 17.7 | 17.56 | 17.4 | 16.23 | 14.7 | 12.78
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Consumer Transformation | Headroom (MW) | N/A | 25.32 | 25.02 | 24.76 | 24.21 | 23.59 | 23.11 | 22.69 | 22.31 | 21.94 | 21.58 | 21.23 | 20.88 | 20.52 | 20.14 | 19.71 | 16.38 | 11.31 | 5.64
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Leading the Way | Headroom (MW) | N/A | 25.32 | 25 | 24.73 | 24.16 | 23.49 | 23.01 | 22.59 | 22.25 | 21.88 | 21.52 | 21.1 | 20.68 | 20.23 | 19.7 | 19.1 | 14.84 | 8.96 | 1.15
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | Steady Progression | Headroom (MW) | N/A | 25.32 | 25.15 | 25.06 | 24.97 | 24.87 | 24.79 | 24.73 | 24.67 | 24.61 | 24.53 | 24.47 | 24.42 | 24.38 | 24.36 | 24.36 | 24.48 | 23.7 | 22.47
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | System Transformation | Headroom (MW) | N/A | 25.32 | 25.09 | 24.92 | 24.75 | 24.49 | 24.28 | 24.09 | 23.92 | 23.74 | 23.57 | 23.4 | 23.25 | 23.14 | 23.04 | 22.95 | 22.14 | 19.63 | 17.15
Ratcliffe 132kV | Nottingham | CLIFTON 33 11kV S STN | Primary | 11 | -1.1785 | 52.9039 | WPD Best View | Headroom (MW) | N/A | 25.32 | 25.01 | 24.74 | 24.18 | 23.53 | 23.03 | 22.59 | 22.21 | 21.83 | 21.47 | 21.07 | 20.67 | 20.25 | 19.77 | 19.22 | 15.27 | 9.64 | 2.49
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Consumer Transformation | Headroom (MW) | Thermal | 0.32 | 0.24 | 0.11 | -0.04 | -0.38 | -0.57 | -0.82 | -1.55 | -2.39 | -3.3 | -4.51 | -5.9 | -7.39 | -8.81 | -10.54 | -16.23 | -21.01 | -26.74
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Leading the Way | Headroom (MW) | Thermal | 0.32 | 0.23 | 0.1 | -0.06 | -0.43 | -0.6 | -0.86 | -1.09 | -1.31 | -1.46 | -1.66 | -1.84 | -3.05 | -4.23 | -5.5 | -13.86 | -19.81 | -23.73
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | Steady Progression | Headroom (MW) | Thermal | 0.32 | 0.3 | 0.26 | 0.23 | 0.19 | 0.2 | 0.16 | 0 | -0.17 | -0.36 | -0.63 | -0.96 | -1.72 | -2.47 | -3.48 | -4.68 | -6.23 | -8.07
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | System Transformation | Headroom (MW) | Thermal | 0.32 | 0.27 | 0.2 | 0.12 | -0.02 | -0.06 | -0.19 | -0.82 | -1.58 | -2.41 | -3.53 | -4.82 | -6.21 | -7.45 | -9 | -13.46 | -17.09 | -21.39
Ratcliffe 132kV | Nottingham | COTGRAVE 33 11kV S STN | Primary | 11 | -1.0308 | 52.9236 | WPD Best View | Headroom (MW) | Thermal | 0.32 | 0.24 | 0.11 | -0.04 | -0.38 | -0.57 | -0.82 | -1.55 | -2.39 | -3.3 | -4.51 | -5.9 | -7.39 | -8.81 | -10.54 | -16.23 | -21.01 | -26.74
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Consumer Transformation | Headroom (MW) | N/A | 9.5 | 9.41 | 9.35 | 9.3 | 9.24 | 9.19 | 9.14 | 9.09 | 9.04 | 8.99 | 8.94 | 8.9 | 8.85 | 8.8 | 8.76 | 12.33 | 5.46 | 4.83
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Leading the Way | Headroom (MW) | N/A | 9.5 | 9.4 | 9.35 | 9.29 | 9.22 | 9.17 | 9.14 | 9.09 | 9.04 | 8.99 | 8.94 | 8.89 | 10.41 | 0.94 | 0.89 | 0.37 | 0.45 | 1.11
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | Steady Progression | Headroom (MW) | N/A | 9.5 | 9.41 | 9.36 | 9.31 | 9.26 | 9.22 | 9.13 | 9.09 | 9.04 | 9 | 8.96 | 8.92 | 8.88 | 8.84 | 8.8 | 8.61 | 8.47 | 8.28
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | System Transformation | Headroom (MW) | N/A | 9.5 | 9.41 | 9.36 | 9.31 | 9.25 | 9.2 | 9.16 | 9.11 | 9.07 | 9.02 | 8.98 | 8.94 | 9.35 | 3.03 | 2.99 | 2.78 | 2.68 | 2.48
Ratcliffe 132kV | Nottingham | LENTON 33 11kV S STN | Primary | 11 | -1.1888 | 52.944 | WPD Best View | Headroom (MW) | N/A | 9.5 | 9.4 | 9.35 | 9.29 | 9.22 | 9.17 | 9.14 | 9.09 | 9.04 | 8.99 | 8.94 | 8.89 | 10.41 | 0.94 | 0.89 | 0.37 | 0.45 | 1.11
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Consumer Transformation | Headroom (MW) | N/A | 23.73 | 23.58 | 23.5 | 23.41 | 23.25 | 23.11 | 22.94 | 22.77 | 22.69 | 22.57 | 22.41 | 22.26 | 22.11 | 21.92 | 21.73 | 19.69 | 16.87 | 13.64
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Leading the Way | Headroom (MW) | N/A | 23.73 | 23.57 | 23.48 | 23.39 | 23.18 | 22.99 | 22.77 | 22.52 | 22.42 | 22.26 | 22.05 | 21.84 | 21.64 | 21.37 | 21.09 | 18.63 | 15.42 | 11.46
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | Steady Progression | Headroom (MW) | N/A | 23.73 | 23.6 | 23.53 | 23.46 | 23.36 | 23.32 | 23.26 | 23.19 | 23.18 | 23.16 | 23.13 | 23.12 | 23.12 | 23.09 | 23.06 | 22.9 | 22.55 | 22.13
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | System Transformation | Headroom (MW) | N/A | 23.73 | 23.59 | 23.51 | 23.43 | 23.31 | 23.28 | 23.22 | 23.1 | 23.05 | 23.03 | 23 | 22.97 | 22.94 | 22.87 | 22.81 | 22.45 | 21.33 | 19.71
Ratcliffe 132kV | Nottingham | NORTH WILFORD 33 11kV S STN | Primary | 11 | -1.1639 | 52.9347 | WPD Best View | Headroom (MW) | N/A | 23.73 | 23.57 | 23.48 | 23.39 | 23.18 | 23 | 22.77 | 22.53 | 22.42 | 22.27 | 22.06 | 21.86 | 21.66 | 21.39 | 21.12 | 18.68 | 15.5 | 11.61
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Consumer Transformation | Headroom (MW) | N/A | 12.38 | 12.26 | 12.16 | 12.02 | 11.6 | 11.31 | 10.95 | 10.62 | 10.36 | 10.06 | 9.76 | 9.47 | 9.19 | 8.88 | 8.6 | 6.91 | 4.86 | 2.61
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Leading the Way | Headroom (MW) | N/A | 12.38 | 12.24 | 12.14 | 11.04 | 10.55 | 10.25 | 9.87 | 9.53 | 9.26 | 8.93 | 8.61 | 8.31 | 8.01 | 7.73 | 7.45 | 5.75 | 3.44 | 0.45
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | Steady Progression | Headroom (MW) | N/A | 12.38 | 12.32 | 12.3 | 12.28 | 12.24 | 12.23 | 12.19 | 12.16 | 12.14 | 12.1 | 12.06 | 12.02 | 11.98 | 11.95 | 11.92 | 11.88 | 11.68 | 11.19
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | System Transformation | Headroom (MW) | N/A | 12.38 | 12.29 | 12.24 | 12.17 | 11.98 | 11.87 | 11.69 | 11.53 | 11.4 | 11.25 | 11.08 | 10.93 | 10.79 | 10.65 | 10.53 | 10.07 | 9.11 | 8.08
Ratcliffe 132kV | Nottingham | SNEINTON 33 11kV S STN | Primary | 11 | -1.1326 | 52.9487 | WPD Best View | Headroom (MW) | N/A | 12.38 | 12.24 | 12.13 | 11.97 | 11.48 | 11.18 | 10.81 | 10.47 | 10.2 | 9.88 | 9.56 | 9.26 | 8.97 | 8.69 | 8.42 | 6.73 | 4.44 | 1.49
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Consumer Transformation | Headroom (MW) | N/A | 15.6 | 15.51 | 15.47 | 15.42 | 15.35 | 15.3 | 15.25 | 15.23 | 15.19 | 15.14 | 15.09 | 15.04 | 15 | 14.95 | 14.91 | 14.6 | 14.29 | 13.97
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Leading the Way | Headroom (MW) | N/A | 15.6 | 15.51 | 15.46 | 15.41 | 15.33 | 15.28 | 15.23 | 15.22 | 15.16 | 15.11 | 15.05 | 15 | 14.95 | 14.9 | 14.84 | 14.54 | 14.22 | 13.81
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | Steady Progression | Headroom (MW) | N/A | 15.1907 | 15.1891 | 15.1882 | 15.187 | 15.1845 | 15.1801 | 15.1754 | 15.1711 | 15.1677 | 15.1633 | 15.1586 | 15.12 | 15.08 | 15.04 | 15 | 14.82 | 14.61 | 14.41
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | System Transformation | Headroom (MW) | N/A | 15.6 | 15.52 | 15.47 | 15.42 | 15.37 | 15.32 | 15.27 | 15.26 | 15.22 | 15.17 | 15.13 | 15.09 | 15.05 | 15 | 14.96 | 14.76 | 14.53 | 14.32
Ratcliffe 132kV | Nottingham | TALBOT ST 33 11kV S STN | Primary | 11 | -1.1544 | 52.9557 | WPD Best View | Headroom (MW) | N/A | 15.6 | 15.51 | 15.46 | 15.41 | 15.33 | 15.28 | 15.23 | 15.22 | 15.16 | 15.11 | 15.05 | 15 | 14.95 | 14.9 | 14.84 | 14.54 | 14.22 | 13.81
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Consumer Transformation | Headroom (MW) | Thermal | 22.55 | 22.34 | 22.19 | 22.02 | 21.48 | 20.74 | 20.19 | 19.66 | 19.11 | 18.68 | 18.08 | 17.46 | 16.82 | 16.12 | 15.38 | 10.5 | 3.19 | -4.89
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Leading the Way | Headroom (MW) | Thermal | 22.55 | 22.33 | 22.16 | 21.96 | 21.35 | 20.58 | 20.07 | 19.64 | 19.13 | 18.74 | 18.14 | 17.49 | 16.76 | 15.95 | 15.06 | 9.24 | 1.24 | -9.2
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | Steady Progression | Headroom (MW) | N/A | 18.0833 | 18.0665 | 18.0515 | 18.0381 | 18.0204 | 17.9784 | 17.9317 | 17.8847 | 17.8346 | 17.7505 | 17.6828 | 17.6129 | 17.5365 | 17.4708 | 17.41 | 17.1575 | 16.8107 | 16.4599
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | System Transformation | Headroom (MW) | N/A | 22.55 | 22.37 | 22.26 | 22.14 | 21.99 | 21.91 | 21.93 | 21.76 | 21.52 | 21.36 | 21.15 | 20.93 | 20.71 | 20.53 | 20.35 | 19.26 | 16.02 | 12.78
Ratcliffe 132kV | Nottingham | WEST BRIDGFORD 33 11kV S STN | Primary | 11 | -1.1398 | 52.925 | WPD Best View | Headroom (MW) | Thermal | 22.55 | 22.34 | 22.19 | 22.02 | 21.48 | 20.74 | 20.18 | 19.65 | 19.1 | 18.67 | 18.07 | 17.45 | 16.8 | 16.11 | 15.37 | 10.49 | 3.16 | -4.93
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Consumer Transformation | Headroom (MW) | N/A | 19.92 | 19.68 | 19.48 | 19.23 | 18.57 | 18.05 | 17.56 | 17.11 | 16.68 | 16.26 | 15.84 | 15.44 | 15.03 | 14.57 | 14.08 | 10.62 | 5.95 | 0.77
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Leading the Way | Headroom (MW) | Thermal | 19.92 | 19.66 | 19.44 | 19.18 | 18.42 | 17.88 | 17.37 | 16.9 | 16.44 | 16.01 | 15.53 | 15.07 | 14.57 | 14.04 | 13.42 | 9.39 | 4.06 | -2.96
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | Steady Progression | Headroom (MW) | N/A | 19.92 | 19.79 | 19.73 | 19.67 | 19.58 | 19.49 | 19.4 | 19.32 | 19.24 | 19.16 | 19.09 | 19.02 | 18.97 | 18.94 | 18.91 | 18.89 | 18.22 | 17.24
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | System Transformation | Headroom (MW) | N/A | 19.92 | 19.74 | 19.62 | 19.48 | 19.2 | 18.97 | 18.72 | 18.48 | 18.27 | 18.06 | 17.86 | 17.68 | 17.52 | 17.38 | 17.24 | 16.21 | 14.01 | 11.88
Ratcliffe 132kV | Nottingham | WOLLATON ROAD 33 11kV S STN | Primary | 11 | -1.1839 | 52.9552 | WPD Best View | Headroom (MW) | Thermal | 19.92 | 19.66 | 19.44 | 19.18 | 18.42 | 17.88 | 17.37 | 16.9 | 16.44 | 16.01 | 15.53 | 15.07 | 14.57 | 14.04 | 13.42 | 9.39 | 4.06 | -2.96
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Consumer Transformation | Headroom (MW) | Thermal | 3.49 | 3.39 | 3.32 | 3.24 | 3.11 | 2.79 | 1.94 | 1.15 | 0.43 | -0.11 | -0.55 | -0.89 | -1.17 | -1.47 | -1.79 | -4.15 | 0.4 | -10.19
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Leading the Way | Headroom (MW) | Thermal | 3.49 | 3.38 | 3.31 | 3.21 | 3.06 | 2.71 | 2.21 | 1.73 | 1.26 | 0.96 | 0.64 | 0.31 | -0.03 | -0.41 | 6.78 | -6.74 | -10.24 | -14.84
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | Steady Progression | Headroom (MW) | Thermal | 3.49 | 3.42 | 3.38 | 3.34 | 3.29 | 3.25 | 2.49 | 1.74 | 1.01 | 0.33 | -0.28 | -0.79 | -1.07 | -1.28 | -1.41 | -1.63 | -1.97 | -2.4
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | System Transformation | Headroom (MW) | Thermal | 3.49 | 3.4 | 3.35 | 3.29 | 3.22 | 3.16 | 2.59 | 2.06 | 1.53 | 1.12 | 0.83 | 0.65 | 0.53 | 0.43 | 1.69 | -6.19 | -7.64 | -9.06
Ratcliffe 132kV | Toton | CHILWELL 33 11kV S STN | Primary | 11 | -1.2292 | 52.9158 | WPD Best View | Headroom (MW) | Thermal | 3.49 | 3.39 | 3.32 | 3.24 | 3.11 | 2.79 | 1.94 | 1.15 | 0.43 | -0.11 | -0.55 | -0.89 | -1.17 | -1.47 | -1.79 | -4.15 | 0.4 | -10.19
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Consumer Transformation | Headroom (MW) | Fault level | 11.9157 | 11.808 | 11.672 | 11.4869 | 11.0208 | 10.5406 | 10.0559 | 9.5588 | 9.0487 | 8.5268 | 7.9637 | 7.4152 | 6.8577 | 6.2991 | 5.7512 | 2.9192 | -0.13003 | -3.2391
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Leading the Way | Headroom (MW) | Fault level | 16.3076 | 16.1577 | 15.9685 | 15.7122 | 15.0843 | 14.4241 | 13.7615 | 13.0851 | 12.3816 | 11.651 | 10.8579 | 10.0772 | 9.2811 | 8.4764 | 7.6771 | 3.5596 | -0.8467 | -6.14
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | Steady Progression | Headroom (MW) | N/A | 6.5734 | 6.5657 | 6.5585 | 6.5507 | 6.5426 | 6.5137 | 6.4794 | 6.4399 | 6.3991 | 6.3478 | 6.2952 | 6.2438 | 6.1924 | 6.1414 | 6.0919 | 5.836 | 5.5381 | 5.234
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | System Transformation | Headroom (MW) | N/A | 9.3934 | 9.3551 | 9.3076 | 9.2488 | 9.1359 | 8.9882 | 8.8138 | 8.6305 | 8.4415 | 8.2458 | 8.0345 | 7.8277 | 7.6155 | 7.4033 | 7.1934 | 6.0929 | 4.911 | 3.7176
Ratcliffe 132kV | Toton | LONG EATON 33 11kV S STN | Primary | 11 | -1.2748 | 52.8983 | WPD Best View | Headroom (MW) | Fault level | 9.7939 | 9.7053 | 9.5935 | 9.4414 | 9.0583 | 8.6637 | 8.2653 | 7.8567 | 7.4374 | 7.0084 | 6.5456 | 6.0948 | 5.6366 | 5.1774 | 4.7271 | 2.3994 | -0.10687 | -2.6623
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Consumer Transformation | Headroom (MW) | Fault level | -35.1648 | -35.2906 | -35.4588 | -35.6659 | -36.0766 | -36.4694 | -36.8649 | -37.248 | -37.6334 | -38.0194 | -38.4347 | -38.8556 | -39.2748 | -39.6986 | -40.1122 | -42.2361 | -44.5715 | -46.9578
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Leading the Way | Headroom (MW) | Fault level | -48.1256 | -48.304 | -48.545 | -48.8384 | -49.3952 | -49.9504 | -50.5141 | -51.0454 | -51.5852 | -52.1381 | -52.7204 | -53.322 | -53.9305 | -54.549 | -55.173 | -58.4271 | -61.9076 | -65.466
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | Steady Progression | Headroom (MW) | Fault level | -19.399 | -19.4152 | -19.4326 | -19.4482 | -19.4635 | -19.493 | -19.5273 | -19.5628 | -19.597 | -19.6393 | -19.682 | -19.7231 | -19.7642 | -19.8052 | -19.8438 | -20.0505 | -20.293 | -20.5436
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | System Transformation | Headroom (MW) | Fault level | -27.7211 | -27.7745 | -27.843 | -27.9177 | -28.0316 | -28.1628 | -28.3149 | -28.4622 | -28.6112 | -28.7606 | -28.9212 | -29.0871 | -29.2531 | -29.4212 | -29.5862 | -30.4331 | -31.3624 | -32.3005
Ratcliffe 132kV | Toton | TOTON 11kV S STN | Primary | 11 | -1.2645 | 52.9168 | WPD Best View | Headroom (MW) | Fault level | -28.903 | -29.0064 | -29.1446 | -29.3148 | -29.6525 | -29.9762 | -30.3022 | -30.6181 | -30.9367 | -31.2553 | -31.599 | -31.9472 | -32.2946 | -32.6471 | -32.9921 | -34.7629 | -36.7015 | -38.6827
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Consumer Transformation | Headroom (MW) | Thermal | 14.34 | 14.17 | 14.02 | 13.83 | 13.4 | 13.06 | 12.36 | 11.17 | 10.06 | 8.96 | 7.67 | 6.28 | 4.84 | 3.42 | 1.78 | -3.91 | -11.43 | -19.75
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Leading the Way | Headroom (MW) | Thermal | 14.34 | 14.16 | 14.01 | 13.81 | 13.36 | 13.02 | 12.29 | 11.82 | 11.33 | 10.75 | 10.19 | 9.58 | 8.41 | 7.22 | 5.94 | 0.43 | -7.17 | -14.17
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | Steady Progression | Headroom (MW) | N/A | 14.34 | 14.25 | 14.22 | 14.18 | 14.14 | 14.11 | 14.07 | 14 | 13.84 | 13.38 | 13.18 | 12.93 | 12.4 | 11.93 | 11.34 | 10.62 | 9.46 | 7.96
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | System Transformation | Headroom (MW) | Thermal | 14.34 | 14.22 | 14.14 | 14.05 | 13.88 | 13.75 | 13.59 | 13.26 | 12.47 | 11.85 | 11.02 | 10.09 | 9.12 | 8.28 | 7.26 | 5.27 | 1.77 | -2.21
Ratcliffe 132kV | Willoughby | BINGHAM 33 11kV S STN | Primary | 11 | -0.9455 | 52.9491 | WPD Best View | Headroom (MW) | Thermal | 14.34 | 14.17 | 14.02 | 13.83 | 13.4 | 13.06 | 12.36 | 11.17 | 10.06 | 8.96 | 7.67 | 6.28 | 4.84 | 3.42 | 1.78 | -3.91 | -11.43 | -19.75
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Consumer Transformation | Headroom (MW) | Thermal | 14.59 | 14.46 | 14.35 | 14.22 | 13.96 | 13.74 | 13.33 | 12.52 | 11.78 | 11.02 | 10.12 | 9.15 | 8.16 | 7.19 | 6.05 | 2.5 | -2.18 | -7.41
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Leading the Way | Headroom (MW) | Thermal | 14.59 | 14.45 | 14.34 | 14.21 | 13.94 | 13.72 | 13.28 | 12.91 | 12.59 | 12.2 | 11.82 | 11.45 | 10.64 | 9.84 | 8.97 | 5.43 | 0.67 | -3.52
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | Steady Progression | Headroom (MW) | N/A | 14.59 | 14.51 | 14.46 | 14.42 | 14.38 | 14.33 | 14.27 | 14.17 | 14.03 | 13.72 | 13.53 | 13.32 | 12.9 | 12.52 | 12.02 | 11.34 | 10.48 | 9.43
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | System Transformation | Headroom (MW) | N/A | 14.59 | 14.49 | 14.42 | 14.34 | 14.23 | 14.13 | 14.01 | 13.69 | 13.14 | 12.65 | 12.01 | 11.31 | 10.59 | 9.95 | 9.19 | 7.69 | 5.38 | 2.71
Ratcliffe 132kV | Willoughby | EAST LEAKE 33 11kV S STN | Primary | 11 | -1.1815 | 52.8435 | WPD Best View | Headroom (MW) | Thermal | 14.59 | 14.46 | 14.35 | 14.22 | 13.96 | 13.74 | 13.33 | 12.52 | 11.78 | 11.02 | 10.12 | 9.15 | 8.16 | 7.19 | 6.05 | 2.5 | -2.18 | -7.41
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Consumer Transformation | Headroom (MW) | Thermal | 7.37 | 6.56 | 6.44 | 6.29 | 5.97 | 5.69 | 5.39 | 4.78 | 4.08 | 3.32 | 2.36 | 1.27 | 0.06 | -1.11 | -2.39 | -5.6 | -9.34 | -13.71
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Leading the Way | Headroom (MW) | Thermal | 7.37 | 6.55 | 6.43 | 6.26 | 5.92 | 5.62 | 5.31 | 4.99 | 4.66 | 4.33 | 3.98 | 3.6 | 2.58 | 1.53 | 0.58 | -2.91 | -7.46 | -10.93
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | Steady Progression | Headroom (MW) | N/A | 7.37 | 7.32 | 7.3 | 6.58 | 6.55 | 6.52 | 6.48 | 6.36 | 6.25 | 6.11 | 5.91 | 5.68 | 5.17 | 4.66 | 4 | 3.15 | 2.07 | 0.75
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | System Transformation | Headroom (MW) | Thermal | 7.37 | 7.3 | 6.53 | 6.46 | 6.34 | 6.22 | 6.07 | 5.6 | 5.03 | 4.4 | 3.59 | 2.65 | 1.64 | 0.71 | -0.37 | -2.35 | -4.99 | -8.03
Ratcliffe 132kV | Willoughby | KEYWORTH 33 11kV S STN | Primary | 11 | -1.0799 | 52.869 | WPD Best View | Headroom (MW) | Thermal | 7.37 | 6.56 | 6.44 | 6.29 | 5.97 | 5.69 | 5.39 | 4.78 | 4.08 | 3.32 | 2.36 | 1.27 | 0.06 | -1.11 | -2.39 | -5.6 | -9.34 | -13.71
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Consumer Transformation | Headroom (MW) | Thermal | 12.33 | 12.44 | 12.35 | 12.55 | 12 | 11.77 | 11.63 | 11.18 | 10.64 | 10.11 | 9.47 | 8.77 | 8.01 | 7.24 | 6.36 | 0.41 | -4.39 | -9.86
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Leading the Way | Headroom (MW) | Thermal | 12.33 | 12.45 | 12.35 | 12.65 | 12.03 | 11.86 | 11.8 | 11.48 | 11.05 | 10.66 | 10.25 | 9.82 | 9.07 | 8.34 | 7.56 | 0.96 | -4.73 | -10.92
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | Steady Progression | Headroom (MW) | N/A | 12.33 | 12.45 | 12.44 | 12.72 | 12.71 | 12.86 | 13.04 | 13.18 | 13.23 | 13.27 | 13.3 | 13.32 | 13.18 | 13 | 12.75 | 12.74 | 11.83 | 10.48
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | System Transformation | Headroom (MW) | N/A | 12.33 | 12.46 | 12.44 | 12.74 | 12.62 | 12.68 | 12.8 | 12.63 | 12.32 | 11.99 | 11.56 | 11.08 | 10.58 | 10.12 | 9.58 | 7.26 | 4.52 | 1.52
Ratcliffe 132kV | Willoughby | MOUNTSORREL 33 11kV S STN | Primary | 11 | -1.1325 | 52.7236 | WPD Best View | Headroom (MW) | Thermal | 12.33 | 12.44 | 12.35 | 12.55 | 12 | 11.77 | 11.63 | 11.18 | 10.64 | 10.11 | 9.47 | 8.77 | 8.01 | 7.24 | 6.36 | 0.41 | -4.39 | -9.86
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Consumer Transformation | Headroom (MW) | Thermal | 3.35 | 3.32 | 3.29 | 3.26 | 3.17 | 3.05 | 2.88 | 1.84 | 0.59 | -0.88 | -2.87 | -5.18 | -7.68 | -9.96 | -12.8 | -18.31 | -24.63 | -32.27
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Leading the Way | Headroom (MW) | Thermal | 3.35 | 3.32 | 3.29 | 3.25 | 3.16 | 3 | 2.79 | 2.58 | 2.37 | 2.13 | 1.92 | 1.7 | -0.18 | -1.99 | -3.9 | -9.62 | -17.26 | -19.86
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | Steady Progression | Headroom (MW) | Thermal | 3.35 | 3.34 | 3.33 | 3.32 | 3.31 | 3.3 | 3.28 | 3.05 | 2.82 | 2.5 | 2.07 | 1.51 | 0.17 | -1.14 | -2.92 | -5.22 | -7.77 | -10.21
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | System Transformation | Headroom (MW) | Thermal | 3.35 | 3.33 | 3.31 | 3.29 | 3.26 | 3.19 | 3.11 | 2.18 | 0.95 | -0.44 | -2.31 | -4.5 | -6.88 | -9.01 | -11.7 | -15.66 | -20.65 | -26.87
Ratcliffe 132kV | Willoughby | SOUTH CROXTON 33 11kV S STN | Primary | 11 | -0.9989 | 52.6964 | WPD Best View | Headroom (MW) | Thermal | 3.35 | 3.32 | 3.29 | 3.26 | 3.17 | 3.06 | 2.91 | 1.88 | 0.64 | -0.82 | -2.8 | -5.1 | -7.59 | -9.86 | -12.7 | -17.86 | -24.07 | -31.6
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Consumer Transformation | Headroom (MW) | Thermal | 13.07 | 12.92 | 13.21 | 13.48 | 13.24 | 13.13 | 13.01 | 12.82 | 12.57 | 12.3 | 11.94 | 11.45 | 10.93 | 10.43 | 9.81 | 7.03 | 2.61 | -2.51
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Leading the Way | Headroom (MW) | Thermal | 13.07 | 12.89 | 13.24 | 13.61 | 13.35 | 13.29 | 13.15 | 13.14 | 13.08 | 13.03 | 12.98 | 12.79 | 12.29 | 11.76 | 11.15 | 7.49 | 2.16 | -3.78
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | Steady Progression | Headroom (MW) | N/A | 13.07 | 13.02 | 13.39 | 13.76 | 13.94 | 14.12 | 14.25 | 14.39 | 14.53 | 14.64 | 14.74 | 14.81 | 14.76 | 14.71 | 14.59 | 14.77 | 13.99 | 12.85
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | System Transformation | Headroom (MW) | N/A | 13.07 | 12.97 | 13.34 | 13.7 | 13.77 | 13.88 | 13.95 | 13.93 | 13.84 | 13.75 | 13.58 | 13.29 | 12.96 | 12.68 | 12.32 | 11.63 | 9.22 | 6.46
Ratcliffe 132kV | Willoughby | SYSTON 33 11kV S STN | Primary | 11 | -1.0613 | 52.7008 | WPD Best View | Headroom (MW) | Thermal | 13.07 | 12.92 | 13.21 | 13.48 | 13.24 | 13.13 | 13.01 | 12.82 | 12.57 | 12.3 | 11.94 | 11.45 | 10.93 | 10.43 | 9.81 | 7.03 | 2.61 | -2.51
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Consumer Transformation | Headroom (MW) | Thermal | 5.03 | 4.93 | 4.85 | 4.75 | 4.51 | 4.34 | 4.16 | 3.29 | 2.24 | 1.03 | -0.7 | -2.7 | -4.87 | -6.83 | -9.32 | -13.63 | -19.77 | -26.32
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Leading the Way | Headroom (MW) | Thermal | 5.03 | 4.92 | 4.83 | 4.74 | 4.47 | 4.28 | 4.09 | 3.92 | 3.75 | 3.59 | 3.43 | 3.28 | 1.64 | 0.09 | -1.6 | -6.46 | -14.38 | -16.99
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | Steady Progression | Headroom (MW) | Thermal | 5.03 | 4.97 | 4.94 | 4.92 | 4.88 | 4.84 | 4.81 | 4.6 | 4.39 | 4.12 | 3.73 | 3.25 | 2.08 | 0.92 | -0.64 | -2.43 | -4.69 | -7.09
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | System Transformation | Headroom (MW) | Thermal | 5.03 | 4.95 | 4.9 | 4.85 | 4.74 | 4.66 | 4.57 | 3.77 | 2.76 | 1.6 | -0.05 | -1.99 | -4.09 | -5.97 | -8.33 | -11.66 | -16.9 | -22.72
Ratcliffe 132kV | Willoughby | WILLOUGHBY 11kV S STN | Primary | 11 | -1.0713 | 52.8256 | WPD Best View | Headroom (MW) | Thermal | 5.03 | 4.93 | 4.85 | 4.75 | 4.51 | 4.34 | 4.16 | 3.29 | 2.24 | 1.03 | -0.7 | -2.7 | -4.87 | -6.83 | -9.32 | -13.63 | -19.77 | -26.32
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Consumer Transformation | Headroom (MW) | N/A | 5.63 | 5.61 | 5.6 | 5.58 | 5.52 | 5.46 | 5.26 | 5.01 | 4.77 | 4.54 | 4.32 | 4.13 | 3.94 | 3.74 | 3.48 | 2.84 | 2.37 | 1.83
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Leading the Way | Headroom (MW) | N/A | 5.63 | 5.61 | 5.6 | 5.58 | 5.53 | 5.44 | 5.28 | 5.08 | 4.87 | 4.65 | 4.43 | 4.21 | 3.99 | 3.81 | 3.59 | 2.82 | 2.48 | 1.95
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | Steady Progression | Headroom (MW) | N/A | 5.63 | 5.61 | 5.6 | 5.6 | 5.58 | 5.56 | 5.45 | 5.33 | 5.22 | 5.11 | 5.01 | 4.94 | 4.9 | 4.87 | 4.85 | 4.78 | 4.7 | 4.62
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | System Transformation | Headroom (MW) | N/A | 5.63 | 5.61 | 5.6 | 5.59 | 5.55 | 5.51 | 5.42 | 5.27 | 5.12 | 4.97 | 4.85 | 4.77 | 4.71 | 4.64 | 4.51 | 4.32 | 4.16 | 3.99
Stalybridge 132kV | Buxton (Part) | FLAGG 33 11kV S STN | Primary | 11 | -1.7819 | 53.2151 | WPD Best View | Headroom (MW) | N/A | 5.63 | 5.61 | 5.6 | 5.58 | 5.55 | 5.5 | 5.38 | 5.25 | 5.14 | 5.05 | 4.98 | 4.93 | 4.89 | 4.84 | 4.79 | 4.48 | 4.18 | 3.83
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Consumer Transformation | Headroom (MW) | N/A | 14.49 | 14.37 | 14.31 | 14.25 | 14.11 | 13.89 | 13.65 | 13.41 | 13.17 | 12.94 | 12.74 | 12.53 | 12.33 | 12.12 | 11.91 | 10.45 | 9.37 | 8.23
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Leading the Way | Headroom (MW) | N/A | 14.49 | 14.37 | 14.31 | 14.24 | 14.04 | 13.8 | 13.54 | 13.28 | 13.01 | 12.75 | 12.52 | 12.3 | 12.07 | 11.85 | 11.61 | 10.31 | 9.27 | 7.96
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | Steady Progression | Headroom (MW) | N/A | 14.49 | 14.39 | 14.33 | 14.28 | 14.2 | 14.14 | 14.07 | 14.02 | 13.95 | 13.89 | 13.83 | 13.77 | 13.71 | 13.65 | 13.57 | 13.24 | 12.8 | 12.37
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | System Transformation | Headroom (MW) | N/A | 14.49 | 14.38 | 14.33 | 14.27 | 14.16 | 14.08 | 13.99 | 13.84 | 13.69 | 13.54 | 13.4 | 13.27 | 13.15 | 13.03 | 12.91 | 12.33 | 11.72 | 11.05
Stalybridge 132kV | Buxton (Part) | HINDLOW 33 11kV S STN | Primary | 11 | -1.8546 | 53.2115 | WPD Best View | Headroom (MW) | N/A | 14.49 | 14.38 | 14.32 | 14.27 | 14.15 | 14.05 | 13.87 | 13.68 | 13.48 | 13.3 | 13.13 | 12.96 | 12.8 | 12.63 | 12.47 | 11.38 | 10.63 | 9.84
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Consumer Transformation | Headroom (MW) | Thermal | 6.16 | 6.11 | 6.08 | 6.04 | 5.93 | 5.85 | 5.39 | 4.78 | 4.16 | 3.62 | 3.06 | 2.52 | 1.97 | 1.46 | 0.83 | -0.48 | -1.59 | -3.14
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Leading the Way | Headroom (MW) | Thermal | 6.16 | 6.11 | 6.07 | 6.03 | 5.9 | 5.81 | 5.62 | 5.44 | 5.25 | 5.18 | 5.11 | 5.04 | 4.61 | 4.2 | 3.76 | 8.09 | -2.24 | -3.51
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | Steady Progression | Headroom (MW) | Thermal | 6.16 | 6.13 | 6.12 | 6.11 | 6.09 | 6.08 | 5.52 | 4.91 | 4.32 | 3.76 | 3.23 | 2.74 | 2.28 | 1.87 | 1.43 | 0.96 | 0.42 | -0.23
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | System Transformation | Headroom (MW) | Thermal | 6.16 | 6.12 | 6.1 | 6.08 | 6.03 | 5.99 | 5.57 | 4.99 | 4.4 | 3.88 | 3.36 | 2.85 | 2.33 | 1.87 | 1.29 | 4.15 | -2.64 | -4.21
Staythorpe 132kV | Checkerhouse | BEVERCOTES 33 11kV S STN | Primary | 11 | -0.9599 | 53.2618 | WPD Best View | Headroom (MW) | Thermal | 6.16 | 6.11 | 6.08 | 6.04 | 5.93 | 5.85 | 5.39 | 4.78 | 4.16 | 3.62 | 3.06 | 2.52 | 1.97 | 1.46 | 0.83 | -0.48 | -1.59 | -3.14
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Consumer Transformation | Headroom (MW) | Thermal | 4.26 | 4.23 | 4.21 | 4.19 | 4.15 | 4.03 | 3.89 | 3.31 | 2.63 | 1.97 | 1.06 | 0.01 | -1.12 | -2.24 | -3.38 | -6.96 | -11.48 | -16.85
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Leading the Way | Headroom (MW) | Thermal | 4.26 | 4.74 | 4.73 | 4.7 | 4.81 | 4.78 | 4.72 | 4.58 | 4.36 | 4.12 | 3.94 | 3.76 | 2.83 | 1.76 | 0.62 | -3.27 | -8.41 | -11.57
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | Steady Progression | Headroom (MW) | Thermal | 4.26 | 4.24 | 4.23 | 4.22 | 4.21 | 4.19 | 4.17 | 4.06 | 3.94 | 3.77 | 3.6 | 3.39 | 2.87 | 2.28 | 1.5 | 0.52 | -0.1 | -0.9
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | System Transformation | Headroom (MW) | Thermal | 4.26 | 4.24 | 4.22 | 4.21 | 4.19 | 4.17 | 4.15 | 3.69 | 3.03 | 2.4 | 1.6 | 0.65 | -0.37 | -1.37 | -2.51 | -3.96 | -6.88 | -10.65
Staythorpe 132kV | Checkerhouse | CHECKERHOUSE 11kV S STN | Primary | 11 | -0.9961 | 53.307 | WPD Best View | Headroom (MW) | Thermal | 4.26 | 4.23 | 4.21 | 4.19 | 4.15 | 4.03 | 3.89 | 3.31 | 2.63 | 1.97 | 1.06 | 0.01 | -1.12 | -2.24 | -3.38 | -6.96 | -11.48 | -16.85
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Consumer Transformation | Headroom (MW) | Thermal | 6.43 | 6.3 | 6.18 | 6.25 | 5.87 | 5.59 | 5.34 | 4.69 | 3.96 | 3.14 | 2.11 | 0.94 | -0.38 | -1.59 | -3.08 | -6.68 | -11.34 | -16.83
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Leading the Way | Headroom (MW) | Thermal | 6.43 | 6.28 | 6.16 | 6.27 | 5.83 | 5.54 | 5.25 | 4.98 | 4.71 | 4.46 | 4.2 | 3.93 | 2.91 | 1.9 | 0.78 | -3.39 | -9.09 | -13.44
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | Steady Progression | Headroom (MW) | Thermal | 6.43 | 6.37 | 6.34 | 6.49 | 6.46 | 6.43 | 6.4 | 6.26 | 6.13 | 5.97 | 5.76 | 5.51 | 4.89 | 4.28 | 3.47 | 2.44 | 1.16 | -0.45
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | System Transformation | Headroom (MW) | Thermal | 6.43 | 6.34 | 6.27 | 6.41 | 6.25 | 6.14 | 6.01 | 5.51 | 4.89 | 4.19 | 3.27 | 2.2 | 1.05 | 0.03 | -1.24 | -3.41 | -6.7 | -10.52
Staythorpe 132kV | Checkerhouse | HALLCROFT RD 33 11kV S STN | Primary | 11 | -0.9562 | 53.3353 | WPD Best View | Headroom (MW) | Thermal | 6.43 | 6.3 | 6.18 | 6.25 | 5.87 | 5.59 | 5.34 | 4.69 | 3.96 | 3.14 | 2.11 | 0.94 | -0.38 | -1.59 | -3.08 | -6.68 | -11.34 | -16.83
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Consumer Transformation | Headroom (MW) | Thermal | 8.45 | 8.44 | 8.39 | 8.32 | 8.1 | 7.92 | 7.51 | 6.6 | 5.77 | 4.91 | 3.88 | 2.78 | 1.61 | 0.49 | -0.85 | -4.98 | -10.93 | -16.43
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Leading the Way | Headroom (MW) | Thermal | 8.45 | 8.44 | 8.38 | 8.32 | 8.06 | 7.88 | 7.42 | 7.03 | 6.7 | 6.28 | 5.9 | 5.54 | 4.6 | 3.68 | 2.68 | -1.22 | -8.29 | -12.1
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | Steady Progression | Headroom (MW) | N/A | 8.45 | 8.46 | 8.45 | 8.45 | 8.42 | 8.4 | 8.38 | 8.28 | 8.14 | 7.79 | 7.59 | 7.35 | 6.85 | 6.39 | 5.8 | 5.01 | 4.02 | 2.93
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | System Transformation | Headroom (MW) | Thermal | 8.45 | 8.46 | 8.43 | 8.4 | 8.31 | 8.24 | 8.15 | 7.79 | 7.14 | 6.56 | 5.83 | 5.01 | 4.14 | 3.39 | 2.46 | 0.69 | -2.8 | -5.7
Staythorpe 132kV | Checkerhouse | MISSON 33 11kV S STN | Primary | 11 | -0.9691 | 53.4481 | WPD Best View | Headroom (MW) | Thermal | 8.45 | 8.45 | 8.41 | 8.36 | 8.19 | 8.05 | 7.67 | 6.8 | 6 | 5.16 | 4.17 | 3.09 | 1.97 | 0.89 | -0.41 | -4.25 | -9.88 | -15.07
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Consumer Transformation | Headroom (MW) | Thermal | 4.41 | 4.36 | 4.33 | 4.28 | 4.17 | 4.09 | 4.02 | 3.91 | 3.8 | 3.69 | 3.45 | 3.17 | 2.88 | 2.6 | 2.27 | 1.44 | 0.21 | -1.25
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Leading the Way | Headroom (MW) | Thermal | 4.41 | 4.36 | 4.32 | 4.27 | 4.15 | 4.06 | 3.98 | 3.91 | 3.83 | 3.76 | 3.68 | 3.6 | 3.35 | 3.12 | 2.87 | 1.93 | 0.42 | -0.63
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | Steady Progression | Headroom (MW) | N/A | 4.41 | 4.38 | 4.36 | 4.35 | 4.33 | 4.32 | 4.3 | 4.27 | 4.25 | 4.22 | 4.17 | 4.1 | 3.96 | 3.82 | 3.63 | 3.39 | 3.03 | 2.59
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | System Transformation | Headroom (MW) | N/A | 4.41 | 4.37 | 4.35 | 4.32 | 4.27 | 4.24 | 4.2 | 4.13 | 4.05 | 3.97 | 3.76 | 3.52 | 3.26 | 3.02 | 2.74 | 2.27 | 1.37 | 0.3
Staythorpe 132kV | Checkerhouse | MISTERTON 33 11kV S STN | Primary | 11 | -0.8439 | 53.4342 | WPD Best View | Headroom (MW) | Thermal | 4.41 | 4.36 | 4.33 | 4.28 | 4.18 | 4.09 | 4.02 | 3.92 | 3.81 | 3.7 | 3.46 | 3.19 | 2.89 | 2.62 | 2.29 | 1.45 | 0.22 | -1.23
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Consumer Transformation | Headroom (MW) | Thermal | 3.73 | 3.66 | 3.62 | 3.56 | 3.32 | 3.17 | 3.02 | 2.16 | 1.14 | -0.06 | -1.65 | -3.51 | -5.51 | -7.34 | -9.62 | -14.12 | -18.87 | -24.7
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Leading the Way | Headroom (MW) | Thermal | 3.73 | 3.65 | 3.6 | 3.54 | 3.25 | 3.09 | 2.94 | 2.8 | 2.65 | 2.51 | 2.38 | 2.24 | 0.75 | -0.67 | -2.18 | -7.14 | -13.19 | -15.39
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | Steady Progression | Headroom (MW) | Thermal | 3.73 | 3.69 | 3.67 | 3.65 | 3.61 | 3.59 | 3.56 | 3.35 | 3.15 | 2.9 | 2.54 | 2.1 | 1.02 | -0.05 | -1.5 | -3.35 | -5.27 | -7.36
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | System Transformation | Headroom (MW) | Thermal | 3.73 | 3.67 | 3.65 | 3.62 | 3.5 | 3.44 | 3.36 | 2.58 | 1.6 | 0.46 | -1.07 | -2.86 | -4.79 | -6.53 | -8.73 | -12.17 | -16.31 | -21.47
Staythorpe 132kV | Checkerhouse | NORTH WHEATLEY 33 11kV S STN | Primary | 11 | -0.8825 | 53.3719 | WPD Best View | Headroom (MW) | Thermal | 3.73 | 3.66 | 3.62 | 3.56 | 3.32 | 3.17 | 3.02 | 2.17 | 1.15 | -0.05 | -1.64 | -3.5 | -5.5 | -7.32 | -9.61 | -14.1 | -18.85 | -24.68
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Consumer Transformation | Headroom (MW) | N/A | 11.21 | 11.11 | 11.02 | 10.93 | 10.67 | 10.47 | 10.27 | 10.09 | 9.92 | 9.77 | 9.62 | 9.48 | 9.32 | 9.15 | 8.98 | 7.07 | 5.3 | 3.33
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Leading the Way | Headroom (MW) | N/A | 11.21 | 11.1 | 11.01 | 10.91 | 10.62 | 10.41 | 10.2 | 10.02 | 9.85 | 9.69 | 9.54 | 9.37 | 9.18 | 8.98 | 8.75 | 5.98 | 3.94 | 1.3
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | Steady Progression | Headroom (MW) | N/A | 11.21 | 11.15 | 11.12 | 11.09 | 11.05 | 11.01 | 10.97 | 10.93 | 10.89 | 10.85 | 10.82 | 10.79 | 10.77 | 10.76 | 10.75 | 10.77 | 10.61 | 10.2
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | System Transformation | Headroom (MW) | N/A | 11.21 | 11.13 | 11.08 | 11.02 | 10.91 | 10.81 | 10.71 | 10.61 | 10.51 | 10.43 | 10.36 | 10.29 | 10.24 | 10.19 | 10.15 | 9.19 | 8.33 | 7.44
Staythorpe 132kV | Checkerhouse | ORDSALL RD 33 11kV S STN | Primary | 11 | -0.9498 | 53.3129 | WPD Best View | Headroom (MW) | N/A | 11.21 | 11.11 | 11.02 | 10.93 | 10.67 | 10.47 | 10.27 | 10.09 | 9.92 | 9.77 | 9.62 | 9.48 | 9.32 | 9.15 | 8.98 | 7.07 | 5.3 | 3.33
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Consumer Transformation | Headroom (MW) | Thermal | 0.88 | 0.78 | 0.88 | 0.94 | 0.97 | 0.99 | 0.99 | 0.41 | -0.29 | -1.12 | -2.26 | -3.65 | -5.22 | -6.64 | -8.43 | -14.01 | -18.14 | -23.22
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Leading the Way | Headroom (MW) | Thermal | 0.88 | 0.78 | 0.88 | 0.98 | 1.05 | 1.13 | 1.15 | 1.17 | 1.21 | 1.27 | 1.35 | 1.37 | 0.2 | -0.94 | -2.15 | -9.21 | -14.51 | -16.76
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | Steady Progression | Headroom (MW) | Thermal | 0.88 | 0.81 | 0.92 | 1.01 | 1.17 | 1.27 | 1.34 | 1.27 | 1.21 | 1.11 | 0.95 | 0.7 | -0.11 | -0.91 | -2.03 | -3.26 | -4.94 | -6.85
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | System Transformation | Headroom (MW) | Thermal | 0.88 | 0.8 | 0.91 | 1 | 1.15 | 1.24 | 1.3 | 0.79 | 0.11 | -0.67 | -1.75 | -3.09 | -4.6 | -5.96 | -7.68 | -11.71 | -15.28 | -19.68
Staythorpe 132kV | Checkerhouse | TUXFORD 33 11kV S STN | Primary | 11 | -0.9022 | 53.2344 | WPD Best View | Headroom (MW) | Thermal | 0.88 | 0.78 | 0.88 | 0.94 | 0.97 | 1 | 1 | 0.43 | -0.27 | -1.09 | -2.22 | -3.6 | -5.16 | -6.58 | -8.38 | -13.88 | -17.99 | -23.04
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Consumer Transformation | Headroom (MW) | Thermal | 1.71 | 1.66 | 1.62 | 1.57 | 1.47 | 1.38 | 1.28 | 0.77 | 0.17 | -0.55 | -1.5 | -2.55 | -3.74 | -4.83 | -6.2 | -8.91 | -11.78 | -15.29
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Leading the Way | Headroom (MW) | Thermal | 1.71 | 1.65 | 1.61 | 1.57 | 1.46 | 1.35 | 1.23 | 1.12 | 1 | 0.86 | 0.73 | 0.68 | -0.23 | -1.12 | -2.06 | -4.99 | -8.65 | -10.03
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | Steady Progression | Headroom (MW) | Thermal | 1.71 | 1.67 | 1.65 | 1.64 | 1.62 | 1.59 | 1.57 | 1.45 | 1.32 | 1.17 | 0.95 | 0.71 | 0.09 | -0.53 | -1.39 | -2.49 | -3.72 | -4.97
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | System Transformation | Headroom (MW) | Thermal | 1.71 | 1.67 | 1.64 | 1.61 | 1.57 | 1.51 | 1.46 | 0.99 | 0.4 | -0.28 | -1.18 | -2.18 | -3.32 | -4.36 | -5.66 | -7.65 | -10.12 | -13.18
Staythorpe 132kV | Checkerhouse | WOODBECK 33 11kV S STN | Primary | 11 | -0.8341 | 53.2976 | WPD Best View | Headroom (MW) | Thermal | 1.71 | 1.66 | 1.62 | 1.57 | 1.47 | 1.38 | 1.28 | 0.78 | 0.17 | -0.54 | -1.49 | -2.53 | -3.73 | -4.82 | -6.18 | -8.89 | -11.76 | -15.28
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Consumer Transformation | Headroom (MW) | Thermal | 14.23 | 14.11 | 13.99 | 13.85 | 13.56 | 13.32 | 12.68 | 11.2 | 9.84 | 8.41 | 6.69 | 4.82 | 2.87 | 1.02 | -1.23 | -9.62 | -17.54 | -26.42
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Leading the Way | Headroom (MW) | Thermal | 14.23 | 14.1 | 13.99 | 13.84 | 13.54 | 13.29 | 12.61 | 12.01 | 11.52 | 10.88 | 10.28 | 9.71 | 8.16 | 6.64 | 5.02 | -4.94 | -13.04 | -19.2
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | Steady Progression | Headroom (MW) | N/A | 14.23 | 14.16 | 14.13 | 14.09 | 14.05 | 14.01 | 13.97 | 13.8 | 13.57 | 12.98 | 12.65 | 12.24 | 11.39 | 10.6 | 9.57 | 8.23 | 6.63 | 4.8
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | System Transformation | Headroom (MW) | Thermal | 14.23 | 14.14 | 14.07 | 14 | 13.88 | 13.77 | 13.65 | 13.05 | 11.97 | 11 | 9.74 | 8.33 | 6.83 | 5.54 | 3.94 | -0.9 | -5 | -9.81
Staythorpe 132kV | Grantham North 132 11 (T1) | GRANTHAM NORTH 11kV S STN | Primary | 11 | -0.6471 | 52.9375 | WPD Best View | Headroom (MW) | Thermal | 14.23 | 14.11 | 13.99 | 13.85 | 13.56 | 13.32 | 12.68 | 11.2 | 9.84 | 8.41 | 6.69 | 4.82 | 2.87 | 1.02 | -1.23 | -9.62 | -17.54 | -26.42
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Consumer Transformation | Headroom (MW) | Thermal | 24.13 | 23.91 | 23.75 | 23.56 | 23.14 | 22.81 | 22.6 | 21.91 | 20.98 | 19.86 | 18.31 | 16.53 | 14.62 | 12.83 | 10.67 | 4.31 | -4.7 | -15.22
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Leading the Way | Headroom (MW) | Thermal | 24.13 | 23.88 | 23.71 | 23.51 | 23.02 | 22.68 | 22.48 | 22.43 | 22.13 | 21.72 | 21.2 | 20.63 | 18.96 | 17.32 | 15.59 | 8.29 | -1.98 | -10.56
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | Steady Progression | Headroom (MW) | N/A | 24.13 | 23.98 | 23.91 | 23.84 | 23.84 | 23.9 | 24 | 24.03 | 24 | 23.88 | 23.69 | 23.42 | 22.66 | 21.92 | 20.93 | 19.92 | 18.78 | 16.43
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | System Transformation | Headroom (MW) | N/A | 24.13 | 23.95 | 23.83 | 23.72 | 23.58 | 23.58 | 23.7 | 23.3 | 22.53 | 21.72 | 20.55 | 19.15 | 17.63 | 16.25 | 14.52 | 12.68 | 6.98 | 0.22
Staythorpe 132kV | Grantham South 132 11 | GRANTHAM SOUTH 11kV S STN | Primary | 11 | -0.6384 | 52.904 | WPD Best View | Headroom (MW) | Thermal | 24.13 | 23.91 | 23.75 | 23.56 | 23.14 | 22.81 | 22.6 | 21.91 | 20.98 | 19.86 | 18.31 | 16.53 | 14.62 | 12.83 | 10.67 | 4.31 | -4.7 | -15.22
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Consumer Transformation | Headroom (MW) | Thermal | 4.54 | 4.5 | 4.44 | 4.38 | 4.21 | 3.93 | 3.62 | 2.66 | 1.54 | 0.25 | -1.36 | -3.21 | -5.22 | -7.07 | -9.34 | -14.16 | -19.71 | -26.49
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Leading the Way | Headroom (MW) | Thermal | 4.54 | 4.5 | 4.44 | 4.37 | 4.19 | 3.8 | 3.39 | 2.96 | 2.52 | 2.06 | 1.73 | 1.39 | -0.2 | -1.76 | -3.4 | -8.81 | -15.76 | -19.43
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | Steady Progression | Headroom (MW) | Thermal | 4.54 | 4.53 | 4.52 | 4.51 | 4.49 | 4.46 | 4.43 | 4.24 | 4.05 | 3.8 | 3.46 | 3.04 | 2.03 | 1.02 | -0.34 | -2.07 | -4 | -6
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | System Transformation | Headroom (MW) | Thermal | 4.54 | 4.52 | 4.49 | 4.45 | 4.39 | 4.28 | 4.15 | 3.33 | 2.27 | 1.14 | -0.32 | -2.02 | -3.86 | -5.52 | -7.61 | -10.77 | -15.23 | -20.72
Staythorpe 132kV | Hawton | BOTTESFORD 33 11kV S STN | Primary | 11 | -0.8147 | 52.9306 | WPD Best View | Headroom (MW) | Thermal | 4.54 | 4.5 | 4.44 | 4.38 | 4.21 | 3.93 | 3.62 | 2.66 | 1.54 | 0.25 | -1.36 | -3.21 | -5.22 | -7.07 | -9.34 | -14.16 | -19.71 | -26.49
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Consumer Transformation | Headroom (MW) | Thermal | 5.09 | 5.02 | 4.96 | 4.89 | 4.74 | 4.61 | 4.12 | 2.79 | 1.55 | 0.23 | -1.39 | -3.16 | -5.02 | -6.8 | -8.94 | -16.11 | -22.9 | -30.58
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Leading the Way | Headroom (MW) | Thermal | 5.09 | 5.02 | 4.96 | 4.89 | 4.73 | 4.61 | 4.09 | 3.66 | 3.33 | 2.86 | 2.44 | 2.04 | 0.64 | -0.75 | -2.23 | -9.18 | -16.06 | -20.42
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | Steady Progression | Headroom (MW) | Thermal | 5.09 | 5.05 | 5.02 | 5 | 4.97 | 4.94 | 4.89 | 4.72 | 4.49 | 3.92 | 3.59 | 3.18 | 2.29 | 1.47 | 0.39 | -1.04 | -2.58 | -4.24
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | System Transformation | Headroom (MW) | Thermal | 5.09 | 5.03 | 5 | 4.96 | 4.89 | 4.83 | 4.76 | 4.18 | 3.15 | 2.2 | 0.96 | -0.45 | -1.94 | -3.26 | -4.9 | -8.49 | -12.18 | -16.64
Staythorpe 132kV | Hawton | CARLTON ON TRENT 33 11kV S STN | Primary | 11 | -0.8137 | 53.1687 | WPD Best View | Headroom (MW) | Thermal | 5.09 | 5.02 | 4.96 | 4.89 | 4.74 | 4.61 | 4.12 | 2.79 | 1.55 | 0.23 | -1.39 | -3.16 | -5.02 | -6.8 | -8.94 | -16.11 | -22.9 | -30.58
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Consumer Transformation | Headroom (MW) | Thermal | 13.44 | 13.31 | 13.2 | 13.06 | 12.79 | 12.54 | 12.3 | 11.68 | 10.99 | 10.23 | 9.26 | 8.16 | 6.98 | 5.89 | 4.54 | 0.85 | -3.1 | -7.79
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Leading the Way | Headroom (MW) | Thermal | 13.44 | 13.3 | 13.19 | 13.04 | 12.75 | 12.49 | 12.23 | 11.99 | 11.77 | 11.54 | 11.32 | 11.09 | 10.15 | 9.22 | 8.25 | 4.2 | -0.66 | -3.95
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | Steady Progression | Headroom (MW) | N/A | 13.44 | 13.37 | 13.33 | 13.29 | 13.26 | 13.21 | 13.16 | 13.02 | 12.89 | 12.72 | 12.5 | 12.23 | 11.63 | 11.05 | 10.27 | 9.33 | 8.11 | 6.63
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | System Transformation | Headroom (MW) | Thermal | 13.44 | 13.34 | 13.27 | 13.2 | 13.08 | 12.96 | 12.83 | 12.34 | 11.72 | 11.05 | 10.17 | 9.16 | 8.08 | 7.12 | 5.91 | 3.72 | 0.81 | -2.6
Staythorpe 132kV | Hawton | CAYTHORPE 33 11kV S STN | Primary | 11 | -0.9917 | 53.0069 | WPD Best View | Headroom (MW) | Thermal | 13.44 | 13.31 | 13.2 | 13.06 | 12.79 | 12.54 | 12.3 | 11.68 | 10.99 | 10.23 | 9.26 | 8.16 | 6.98 | 5.89 | 4.54 | 0.85 | -3.1 | -7.79
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Consumer Transformation | Headroom (MW) | N/A | 12.45 | 12.5 | 12.55 | 12.59 | 12.54 | 12.46 | 12.35 | 12.22 | 12.08 | 11.91 | 11.73 | 11.57 | 11.4 | 11.22 | 11.04 | 9.93 | 9.31 | 8.67
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Leading the Way | Headroom (MW) | N/A | 12.45 | 12.51 | 12.57 | 12.61 | 12.54 | 12.44 | 12.31 | 12.15 | 11.96 | 11.75 | 11.53 | 11.34 | 11.13 | 10.95 | 10.77 | 9.75 | 9.07 | 8.3
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | Steady Progression | Headroom (MW) | N/A | 12.45 | 12.5 | 12.55 | 12.59 | 12.61 | 12.63 | 12.65 | 12.67 | 12.68 | 12.69 | 12.7 | 12.68 | 12.67 | 12.65 | 12.61 | 12.53 | 12.38 | 12.22
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | System Transformation | Headroom (MW) | N/A | 12.45 | 12.5 | 12.56 | 12.6 | 12.63 | 12.61 | 12.56 | 12.5 | 12.42 | 12.33 | 12.23 | 12.14 | 12.03 | 11.94 | 11.83 | 11.32 | 11 | 10.71
Staythorpe 132kV | Hawton | FERNWOOD 33 11kV S STN | Primary | 11 | -0.7772 | 53.0423 | WPD Best View | Headroom (MW) | N/A | 12.45 | 12.5 | 12.55 | 12.59 | 12.54 | 12.46 | 12.35 | 12.22 | 12.08 | 11.91 | 11.73 | 11.57 | 11.4 | 11.22 | 11.04 | 9.93 | 9.31 | 8.67
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Consumer Transformation | Headroom (MW) | Thermal | 13.7 | 13.47 | 13.34 | 5.95 | 5.45 | 4.92 | 3.89 | 2.69 | 1.49 | 0.4 | -0.75 | -1.89 | -2.9 | -3.93 | -4.24 | -8.58 | -13.44 | -20.97
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Leading the Way | Headroom (MW) | Thermal | 13.7 | 13.45 | 13.33 | 5.93 | 5.39 | 4.76 | 3.99 | 3.22 | 2.45 | 1.88 | 1.36 | 0.88 | -0.05 | -1 | -0.92 | -6.06 | -9.67 | -17.8
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | Steady Progression | Headroom (MW) | Thermal | 13.7 | 13.56 | 13.55 | 6.34 | 6.28 | 6.21 | 5.41 | 4.57 | 3.75 | 2.97 | 2.23 | 1.57 | 0.97 | 0.44 | -0.13 | -0.74 | -1.71 | -3.29
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | System Transformation | Headroom (MW) | Thermal | 13.7 | 13.52 | 13.46 | 6.18 | 5.98 | 5.8 | 5.08 | 4.14 | 3.15 | 2.35 | 1.53 | 0.71 | -0.06 | -0.76 | -1.46 | -3.18 | -5.49 | -9.39
Staythorpe 132kV | Hawton | HAWTON 11kV S STN | Primary | 11 | -0.8053 | 53.0499 | WPD Best View | Headroom (MW) | Thermal | 13.7 | 13.47 | 13.34 | 5.95 | 5.45 | 4.92 | 3.89 | 2.69 | 1.49 | 0.4 | -0.75 | -1.89 | -2.9 | -3.93 | -4.24 | -8.58 | -13.44 | -20.97
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Consumer Transformation | Headroom (MW) | Thermal | 13.14 | 12.96 | 12.88 | 12.75 | 12.28 | 11.8 | 11.3 | 10.33 | 9.22 | 8 | 6.42 | 4.66 | 2.76 | 0.95 | -1.18 | -7.24 | -14.83 | -23.75
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Leading the Way | Headroom (MW) | Thermal | 13.14 | 13.06 | 12.87 | 12.73 | 12.18 | 11.6 | 11.02 | 10.45 | 9.82 | 9.21 | 8.5 | 7.78 | 6.14 | 4.54 | 2.85 | -4.12 | -13.23 | -20.95
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | Steady Progression | Headroom (MW) | N/A | 13.14 | 13.13 | 13.14 | 13.15 | 13.14 | 13.11 | 13.06 | 12.89 | 12.71 | 12.48 | 12.18 | 11.82 | 11.05 | 10.28 | 9.25 | 7.89 | 6.13 | 3.91
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | System Transformation | Headroom (MW) | Thermal | 13.14 | 13.11 | 12.98 | 12.94 | 12.78 | 12.64 | 12.46 | 11.75 | 10.83 | 9.91 | 8.65 | 7.2 | 5.67 | 4.29 | 2.6 | -0.51 | -5.6 | -11.57
Staythorpe 132kV | Hawton | NEWARK JUNCTION 33 11kV S STN | Primary | 11 | -0.7986 | 53.0784 | WPD Best View | Headroom (MW) | Thermal | 13.14 | 12.96 | 12.88 | 12.75 | 12.29 | 11.8 | 11.3 | 10.33 | 9.23 | 8.01 | 6.43 | 4.67 | 2.78 | 0.97 | -1.16 | -7.22 | -14.81 | -23.73
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Consumer Transformation | Headroom (MW) | Thermal | 3.08 | 3.04 | 3 | 2.95 | 2.83 | 2.6 | 1.85 | 0.32 | -1.01 | -2.37 | -3.97 | -5.65 | -7.38 | -9.08 | -11.06 | -17.9 | -26.38 | -35.8
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Leading the Way | Headroom (MW) | Thermal | 3.08 | 3.04 | 3 | 2.95 | 2.84 | 2.52 | 1.64 | 0.87 | 0.22 | -0.64 | -1.42 | -2.17 | -3.6 | -5.04 | -6.58 | -12.97 | -21.15 | -28.02
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | Steady Progression | Headroom (MW) | Thermal | 3.08 | 3.06 | 3.05 | 3.04 | 3.03 | 3 | 2.98 | 2.88 | 2.69 | 2.07 | 1.81 | 1.49 | 0.84 | 0.25 | -0.5 | -1.52 | -2.74 | -3.96
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | System Transformation | Headroom (MW) | Thermal | 3.08 | 3.05 | 3.03 | 3.01 | 2.97 | 2.91 | 2.84 | 2.39 | 1.38 | 0.63 | -0.34 | -1.41 | -2.52 | -3.49 | -4.67 | -7.01 | -10.76 | -15.2
Staythorpe 132kV | Hawton | SIBTHORPE 33 11kV S STN | Primary | 11 | -0.8755 | 52.9994 | WPD Best View | Headroom (MW) | Thermal | 3.08 | 3.04 | 3 | 2.95 | 2.83 | 2.6 | 1.85 | 0.32 | -1.01 | -2.37 | -3.97 | -5.65 | -7.38 | -9.08 | -11.06 | -17.9 | -26.38 | -35.8
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Consumer Transformation | Headroom (MW) | Thermal | 5.73 | 5.64 | 5.58 | 5.5 | 5.29 | 4.98 | 4.75 | 4.16 | 3.52 | 2.82 | 1.92 | 0.91 | -0.17 | -1.15 | -2.66 | -6.15 | -10.77 | -16.39
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Leading the Way | Headroom (MW) | Thermal | 5.73 | 5.63 | 5.57 | 5.49 | 5.27 | 4.86 | 4.54 | 4.16 | 3.8 | 3.48 | 3.09 | 2.7 | 1.77 | 0.88 | -0.41 | -4.5 | -10.17 | -15.08
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | Steady Progression | Headroom (MW) | N/A | 5.73 | 5.68 | 5.68 | 5.68 | 5.67 | 5.64 | 5.61 | 5.51 | 5.41 | 5.29 | 5.13 | 4.93 | 4.48 | 4.03 | 3.47 | 2.77 | 1.79 | 0.59
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | System Transformation | Headroom (MW) | Thermal | 5.73 | 5.66 | 5.64 | 5.61 | 5.54 | 5.46 | 5.44 | 5.01 | 4.45 | 3.93 | 3.23 | 2.42 | 1.55 | 0.78 | -0.39 | -1.85 | -4.8 | -8.52
Staythorpe 132kV | Hawton | SOUTHWELL 33 11kV S STN | Primary | 11 | -0.9412 | 53.0774 | WPD Best View | Headroom (MW) | Thermal | 5.73 | 5.64 | 5.58 | 5.5 | 5.29 | 4.98 | 4.75 | 4.16 | 3.52 | 2.82 | 1.92 | 0.91 | -0.17 | -1.15 | -2.66 | -6.15 | -10.77 | -16.39
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Consumer Transformation | Headroom (MW) | Thermal | 4.15 | 4.09 | 4.03 | 3.96 | 3.8 | 3.68 | 3.56 | 2.75 | 1.77 | 0.63 | -0.89 | -2.67 | -4.62 | -6.38 | -8.58 | -13.11 | -17.65 | -23.26
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Leading the Way | Headroom (MW) | Thermal | 4.15 | 4.08 | 4.02 | 3.95 | 3.78 | 3.64 | 3.52 | 3.41 | 3.3 | 3.2 | 3.09 | 2.97 | 1.5 | 0.11 | -1.37 | -6.46 | -12.31 | -14.52
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | Steady Progression | Headroom (MW) | Thermal | 4.15 | 4.12 | 4.1 | 4.08 | 4.06 | 4.04 | 4.01 | 3.81 | 3.62 | 3.37 | 3.02 | 2.57 | 1.52 | 0.48 | -0.93 | -2.73 | -4.62 | -6.65
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | System Transformation | Headroom (MW) | Thermal | 4.15 | 4.1 | 4.07 | 4.03 | 3.97 | 3.91 | 3.85 | 3.09 | 2.13 | 1.04 | -0.43 | -2.16 | -4.03 | -5.72 | -7.84 | -11.32 | -15.32 | -20.28
Staythorpe 132kV | Hawton | SWINDERBY 33 11kV S STN | Primary | 11 | -0.7129 | 53.1675 | WPD Best View | Headroom (MW) | Thermal | 4.15 | 4.1 | 4.06 | 4.01 | 3.9 | 3.82 | 3.73 | 3.17 | 2.52 | 1.74 | 0.7 | -0.53 | -2.09 | -3.56 | -5.45 | -8.8 | -12.28 | -16.45
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Consumer Transformation | Headroom (MW) | Thermal | 4.65 | 4.59 | 4.54 | 4.48 | 4.32 | 4.07 | 3.8 | 2.86 | 1.75 | 0.45 | -1.05 | -2.8 | -4.7 | -6.43 | -8.6 | -13.39 | -17.83 | -23.33
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Leading the Way | Headroom (MW) | Thermal | 4.65 | 4.58 | 4.53 | 4.46 | 4.28 | 3.94 | 3.57 | 3.16 | 2.73 | 2.26 | 2.09 | 1.91 | 0.44 | -0.97 | -2.46 | -7.53 | -13.24 | -15.35
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | Steady Progression | Headroom (MW) | Thermal | 4.65 | 4.62 | 4.61 | 4.59 | 4.57 | 4.54 | 4.51 | 4.31 | 4.12 | 3.87 | 3.53 | 3.11 | 2.08 | 1.07 | -0.3 | -2.04 | -3.94 | -5.89
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | System Transformation | Headroom (MW) | Thermal | 4.65 | 4.61 | 4.57 | 4.54 | 4.47 | 4.32 | 4.15 | 3.31 | 2.26 | 1.08 | -0.37 | -2.06 | -3.89 | -5.54 | -7.62 | -10.92 | -14.79 | -19.6
Staythorpe 132kV | Hawton | WESTBOROUGH 33 11kV S STN | Primary | 11 | -0.7385 | 52.9954 | WPD Best View | Headroom (MW) | Thermal | 4.65 | 4.59 | 4.54 | 4.48 | 4.32 | 4.07 | 3.8 | 2.87 | 1.75 | 0.46 | -1.04 | -2.79 | -4.68 | -6.41 | -8.58 | -13.37 | -17.82 | -23.32
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Consumer Transformation | Headroom (MW) | Thermal | 11.28 | 11.11 | 10.95 | 10.75 | 10.24 | 9.81 | 9.11 | 8.46 | 7.85 | 7.35 | 6.94 | 6.59 | 6.26 | 5.9 | 5.51 | 2.63 | -0.96 | -5.05
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Leading the Way | Headroom (MW) | Thermal | 11.28 | 11.1 | 10.93 | 10.69 | 10.1 | 9.65 | 9.13 | 8.65 | 8.17 | 7.81 | 7.43 | 7.05 | 6.65 | 6.19 | 5.68 | 2.24 | 1.97 | -10.22
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | Steady Progression | Headroom (MW) | N/A | 11.28 | 11.2 | 11.16 | 11.11 | 11.04 | 10.97 | 10.49 | 10 | 9.52 | 9.07 | 8.66 | 8.33 | 8.14 | 8 | 7.91 | 7.81 | 7.41 | 6.47
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | System Transformation | Headroom (MW) | N/A | 11.28 | 11.16 | 11.07 | 10.96 | 10.75 | 10.55 | 10.04 | 9.57 | 9.15 | 8.81 | 8.56 | 8.38 | 8.25 | 8.13 | 8.02 | 7.23 | 9.62 | 3.55
Staythorpe 132kV | Worksop | KILTON RD 33 11kV S STN | Primary | 11 | -1.1111 | 53.3085 | WPD Best View | Headroom (MW) | Thermal | 11.28 | 11.11 | 10.95 | 10.75 | 10.24 | 9.81 | 9.11 | 8.46 | 7.85 | 7.35 | 6.94 | 6.59 | 6.26 | 5.9 | 5.51 | 2.63 | -0.96 | -5.05
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Consumer Transformation | Headroom (MW) | N/A | 11.285 | 11.395 | 11.345 | 11.285 | 12.195 | 12.805 | 13.305 | 13.595 | 13.885 | 14.175 | 14.375 | 14.445 | 14.515 | 12.855 | 12.905 | 13.1878 | 11.1895 | 8.848
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Leading the Way | Headroom (MW) | N/A | 11.285 | 11.415 | 11.365 | 11.275 | 12.455 | 13.425 | 14.135 | 14.805 | 15.425 | 16.085 | 16.785 | 17.515 | 18.225 | 17.165 | 17.905 | 19.1238 | 16.0606 | 14.535
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | Steady Progression | Headroom (MW) | N/A | 11.285 | 11.395 | 11.375 | 11.365 | 12.275 | 12.855 | 13.265 | 13.665 | 14.065 | 14.2602 | 14.1752 | 14.0695 | 13.8299 | 13.593 | 13.2759 | 12.8055 | 12.3299 | 11.8512
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | System Transformation | Headroom (MW) | N/A | 11.285 | 11.415 | 11.385 | 11.345 | 12.365 | 13.045 | 13.615 | 13.975 | 14.315 | 14.665 | 14.925 | 15.075 | 15.215 | 14.555 | 14.2171 | 13.1025 | 11.7603 | 10.1405
Staythorpe 132kV | Worksop | MANTON 33 11kV S STN | Primary | 11 | -1.0958 | 53.2945 | WPD Best View | Headroom (MW) | N/A | 11.285 | 11.395 | 11.345 | 11.285 | 12.195 | 12.805 | 13.305 | 13.595 | 13.885 | 14.175 | 14.375 | 14.445 | 14.515 | 12.855 | 12.8765 | 11.4209 | 9.6903 | 7.6625
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Consumer Transformation | Headroom (MW) | Thermal | 8.68 | 8.58 | 5.35 | 5.29 | 5.08 | 4.89 | 4.18 | 3.52 | 2.92 | 2.46 | 2.14 | 1.91 | 1.73 | 1.54 | 1.34 | 0.01 | -0.75 | -1.79
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Leading the Way | Headroom (MW) | Thermal | 8.68 | 8.57 | 5.35 | 5.28 | 5.02 | 4.81 | 4.46 | 4.1 | 3.74 | 3.54 | 3.34 | 3.13 | 2.92 | 2.68 | 2.44 | 0.99 | 7.08 | -6.16
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | Steady Progression | Headroom (MW) | Thermal | 8.68 | 8.6 | 5.36 | 5.33 | 5.28 | 5.25 | 4.47 | 3.7 | 2.95 | 2.24 | 1.61 | 1.08 | 0.8 | 0.58 | 0.44 | 0.2 | -0.11 | -0.54
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | System Transformation | Headroom (MW) | N/A | 8.68 | 8.59 | 5.36 | 5.32 | 5.25 | 5.17 | 4.54 | 3.95 | 3.41 | 3.03 | 2.77 | 2.61 | 2.51 | 2.41 | 2.32 | 1.82 | 8.84 | 0.66
Staythorpe 132kV | Worksop | WORKSOP WEST 33 11kV S STN | Primary | 11 | -1.1383 | 53.3144 | WPD Best View | Headroom (MW) | Thermal | 8.68 | 8.58 | 5.35 | 5.29 | 5.08 | 4.89 | 4.18 | 3.52 | 2.92 | 2.46 | 2.14 | 1.91 | 1.73 | 1.54 | 1.34 | 0.01 | -0.75 | -1.79
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Consumer Transformation | Headroom (MW) | Thermal | 2.61 | 2.43 | 2.3 | 2.15 | 1.87 | 1.27 | -0.18 | -1.54 | -2.63 | -3.51 | -4.23 | -4.79 | -5.27 | -5.79 | -6.34 | -11.81 | -9.67 | -21.5
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Leading the Way | Headroom (MW) | Thermal | 2.61 | 2.41 | 2.28 | 2.11 | 1.74 | 1.16 | 0.28 | -0.58 | -1.18 | -1.61 | -2.14 | -2.69 | -3.27 | -3.9 | 5.22 | -10.81 | -11.25 | -27.7
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | Steady Progression | Headroom (MW) | Thermal | 2.61 | 2.48 | 2.4 | 2.33 | 2.24 | 2.21 | 0.96 | -0.28 | -1.45 | -2.53 | -3.53 | -4.36 | -4.8 | -5.13 | -5.34 | -5.63 | -6.23 | -6.94
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | System Transformation | Headroom (MW) | Thermal | 2.61 | 2.45 | 2.35 | 2.25 | 2.1 | 2.04 | 1.11 | 0.18 | -0.64 | -1.27 | -1.74 | -2.02 | -2.19 | -2.34 | -0.22 | -8.58 | -5.87 | -13.85
Stoke Bardolph 132kV | Nottingham East | COLWICK 33 11kV S STN | Primary | 11 | -1.0802 | 52.9604 | WPD Best View | Headroom (MW) | Thermal | 2.61 | 2.43 | 2.3 | 2.15 | 1.86 | 1.25 | -0.22 | -1.6 | -2.71 | -3.6 | -4.34 | -4.92 | -5.42 | -5.96 | -6.54 | -12.03 | -9.99 | -22.01
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Consumer Transformation | Headroom (MW) | Thermal | 9.69 | 9.48 | 9.27 | 9.01 | 8.5 | 8.06 | 7.65 | 7.26 | 6.91 | 6.59 | 6.28 | 5.93 | 5.57 | 5.19 | 4.8 | 0.5 | -3.41 | -7.78
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Leading the Way | Headroom (MW) | Thermal | 9.69 | 9.46 | 9.25 | 8.97 | 8.43 | 7.97 | 7.52 | 7.13 | 6.78 | 6.45 | 6.06 | 5.65 | 5.22 | 4.75 | 4.23 | -1.67 | -6.2 | -12.24
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | Steady Progression | Headroom (MW) | N/A | 9.69 | 9.59 | 9.53 | 9.48 | 9.43 | 9.37 | 9.29 | 9.22 | 9.16 | 9.09 | 9.03 | 8.99 | 8.96 | 8.94 | 8.93 | 8.95 | 8.54 | 7.65
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | System Transformation | Headroom (MW) | N/A | 9.69 | 9.54 | 9.42 | 9.29 | 9.09 | 8.9 | 8.68 | 8.48 | 8.3 | 8.13 | 7.97 | 7.84 | 7.73 | 7.62 | 7.49 | 5.51 | 3.62 | 1.77
Stoke Bardolph 132kV | Nottingham East | GEDLING 33 11kV S STN | Primary | 11 | -1.0908 | 52.985 | WPD Best View | Headroom (MW) | Thermal | 9.69 | 9.48 | 9.27 | 9.01 | 8.5 | 8.06 | 7.65 | 7.26 | 6.91 | 6.59 | 6.28 | 5.93 | 5.57 | 5.19 | 4.8 | 0.5 | -3.41 | -7.78
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Consumer Transformation | Headroom (MW) | N/A | 23.2363 | 23.1427 | 23.0304 | 22.8814 | 22.5271 | 22.1721 | 21.8274 | 21.4809 | 21.135 | 20.788 | 20.4122 | 20.0325 | 19.6443 | 19.2538 | 18.8611 | 16.33 | 11.28 | 5.62
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Leading the Way | Headroom (MW) | N/A | 24.44 | 24.27 | 24.14 | 24.34 | 24.43 | 24.04 | 23.5 | 22.99 | 22.5 | 22.03 | 21.55 | 21.07 | 20.56 | 19.99 | 19.33 | 14.82 | 8.96 | 1.25
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | Steady Progression | Headroom (MW) | N/A | 12.8186 | 12.8105 | 12.8049 | 12.799 | 12.7927 | 12.7703 | 12.7448 | 12.7158 | 12.6872 | 12.6508 | 12.6147 | 12.5792 | 12.544 | 12.5092 | 12.4749 | 12.2841 | 12.0584 | 11.8281
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | System Transformation | Headroom (MW) | N/A | 18.3177 | 18.2825 | 18.2438 | 18.1976 | 18.1095 | 17.9974 | 17.8693 | 17.7394 | 17.61 | 17.4796 | 17.3386 | 17.1945 | 17.0459 | 16.8965 | 16.7444 | 15.9428 | 15.0621 | 14.1738
Stoke Bardolph 132kV | Nottingham East | MAPPERLEY 33 11kV S STN | Primary | 11 | -1.1309 | 52.9703 | WPD Best View | Headroom (MW) | N/A | 19.0986 | 19.0203 | 18.9275 | 18.8041 | 18.5129 | 18.2156 | 17.9243 | 17.6345 | 17.3437 | 17.0511 | 16.7306 | 16.4036 | 16.0683 | 15.7237 | 15.374 | 13.5486 | 9.6 | 2.27
Ratcliffe 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Consumer Transformation | Headroom (MW) | N/A | 29.39 | 29.26 | 29.2 | 29.15 | 28.98 | 28.91 | 28.84 | 28.77 | 28.69 | 28.6 | 28.43 | 28.18 | 27.93 | 27.67 | 27.4 | 25.47 | 23.01 | 20.33
Ratcliffe 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Leading the Way | Headroom (MW) | N/A | 29.39 | 29.25 | 29.19 | 29.14 | 28.9 | 28.83 | 28.76 | 28.68 | 28.57 | 28.47 | 28.29 | 28.02 | 27.74 | 27.45 | 27.11 | 24.99 | 22.21 | 18.75
Ratcliffe 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | Steady Progression | Headroom (MW) | N/A | 27.6765 | 27.6655 | 27.6523 | 27.6421 | 27.6294 | 27.6025 | 27.573 | 27.5448 | 27.5179 | 27.4849 | 27.4501 | 27.4162 | 27.3818 | 27.3471 | 27.314 | 27.1524 | 26.9886 | 26.8278
Ratcliffe 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | System Transformation | Headroom (MW) | N/A | 29.39 | 29.27 | 29.22 | 29.18 | 29.05 | 29.01 | 28.95 | 28.89 | 28.83 | 28.77 | 28.71 | 28.65 | 28.58 | 28.51 | 28.44 | 28.08 | 27.49 | 26.18
Ratcliffe 132kV | Nottingham East | ST ANNS 33 11kV S STN | Primary | 11 | -1.1433 | 52.957 | WPD Best View | Headroom (MW) | N/A | 29.39 | 29.25 | 29.19 | 29.14 | 28.9 | 28.83 | 28.76 | 28.68 | 28.57 | 28.47 | 28.29 | 28.02 | 27.74 | 27.45 | 27.11 | 24.99 | 22.21 | 18.75
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Consumer Transformation | Headroom (MW) | Thermal | 21.1606 | 21.0799 | 20.88 | 20.21 | 19.45 | 18.88 | 18.33 | 17.83 | 17.38 | 17.01 | 16.62 | 16.17 | 15.71 | 15.23 | 14.73 | 10.89 | 5.51 | -0.22
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Leading the Way | Headroom (MW) | Thermal | 21.35 | 21.06 | 20.84 | 20.15 | 19.27 | 18.66 | 18.09 | 17.57 | 17.09 | 16.74 | 16.25 | 15.74 | 15.21 | 14.62 | 13.98 | 9.56 | 3.19 | -4.55
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | Steady Progression | Headroom (MW) | N/A | 11.6735 | 11.666 | 7.9235 | 7.9157 | 7.9042 | 7.8762 | 7.8143 | 7.7809 | 7.7486 | 7.7094 | 7.6686 | 7.6281 | 7.5876 | 7.5472 | 7.5073 | 7.3034 | 7.108 | 6.8776
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | System Transformation | Headroom (MW) | N/A | 16.6813 | 16.6507 | 16.6128 | 16.5661 | 16.4629 | 16.3308 | 16.18 | 16.0341 | 15.8874 | 15.7432 | 15.5831 | 15.4185 | 15.2495 | 15.0787 | 14.9048 | 14.0374 | 12.96 | 11.9979
Stoke Bardolph 132kV | Nottingham North 132 11 | NOTTINGHAM NORTH 11kV S STN | Primary | 11 | -1.1734 | 52.979 | WPD Best View | Headroom (MW) | Thermal | 17.3926 | 17.3248 | 17.2386 | 16.8907 | 16.5735 | 16.2331 | 15.9001 | 15.5773 | 15.2504 | 14.9322 | 14.576 | 14.2096 | 13.8349 | 13.4537 | 13.0687 | 9.56 | 3.19 | -4.55
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Consumer Transformation | Headroom (MW) | Thermal | 17.01 | 16.79 | 16.65 | 16.49 | 16.27 | 16.1 | 15.93 | 15.47 | 14.99 | 14.55 | 14.12 | 13.7 | 13.28 | 12.84 | 12.36 | 8.81 | 4.15 | -1.17
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Leading the Way | Headroom (MW) | Thermal | 17.01 | 16.78 | 16.62 | 16.46 | 16.2 | 16 | 15.8 | 15.28 | 14.77 | 14.29 | 13.79 | 13.28 | 12.77 | 12.2 | 11.56 | 7.36 | 2 | -5.14
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | Steady Progression | Headroom (MW) | N/A | 16.7701 | 16.7591 | 16.73 | 16.63 | 16.53 | 16.43 | 16.34 | 16.24 | 16.15 | 16.06 | 15.95 | 15.85 | 15.75 | 15.65 | 15.55 | 15.1 | 14.44 | 13.74
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | System Transformation | Headroom (MW) | N/A | 17.01 | 16.81 | 16.69 | 16.57 | 16.42 | 16.3 | 16.17 | 16.04 | 15.91 | 15.78 | 15.66 | 15.53 | 15.4 | 15.27 | 15.13 | 14.16 | 11.81 | 9.47
Stoke Bardolph 132kV | Nottingham North 33 | ARNOLD 33 11kV S STN | Primary | 11 | -1.1241 | 53.0077 | WPD Best View | Headroom (MW) | Thermal | 17.01 | 16.79 | 16.64 | 16.49 | 16.26 | 16.09 | 15.91 | 15.45 | 14.97 | 14.52 | 14.09 | 13.65 | 13.22 | 12.76 | 12.27 | 8.64 | 3.9 | -1.63
Ratcliffe 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Consumer Transformation | Headroom (MW) | N/A | 13.43 | 13.29 | 13.16 | 12.99 | 12.62 | 12.31 | 12.01 | 11.72 | 11.46 | 11.21 | 11 | 10.75 | 10.5 | 10.22 | 9.93 | 7.8 | 4.9 | 1.68
Ratcliffe 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Leading the Way | Headroom (MW) | Thermal | 13.43 | 13.28 | 13.14 | 12.96 | 12.54 | 12.21 | 11.88 | 11.58 | 11.29 | 11.03 | 10.77 | 10.47 | 10.15 | 9.8 | 9.41 | 6.84 | 3.51 | -0.9
Ratcliffe 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | Steady Progression | Headroom (MW) | N/A | 13.43 | 13.37 | 13.33 | 13.3 | 13.25 | 13.2 | 13.15 | 13.1 | 13.04 | 12.99 | 12.94 | 12.9 | 12.87 | 12.84 | 12.83 | 12.8 | 12.45 | 11.81
Ratcliffe 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | System Transformation | Headroom (MW) | N/A | 13.43 | 13.33 | 13.25 | 13.17 | 13.02 | 12.88 | 12.71 | 12.56 | 12.42 | 12.28 | 12.17 | 12.07 | 11.98 | 11.91 | 11.81 | 11.19 | 9.77 | 8.4
Ratcliffe 132kV | Nottingham North 33 | BILBOROUGH 33 11kV S STN | Primary | 11 | -1.2133 | 52.9619 | WPD Best View | Headroom (MW) | Thermal | 13.43 | 13.28 | 13.14 | 12.96 | 12.54 | 12.21 | 11.88 | 11.58 | 11.29 | 11.03 | 10.77 | 10.48 | 10.16 | 9.81 | 9.42 | 6.87 | 3.55 | -0.83
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Consumer Transformation | Headroom (MW) | N/A | 23.98 | 23.92 | 24.01 | 23.95 | 23.6 | 23.32 | 22.98 | 22.61 | 22.26 | 21.97 | 21.69 | 21.4 | 21.11 | 20.77 | 20.4 | 17.51 | 13.17 | 8.26
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Leading the Way | Headroom (MW) | N/A | 23.98 | 23.91 | 24.03 | 24 | 23.62 | 23.37 | 22.99 | 22.6 | 22.2 | 21.87 | 21.55 | 21.23 | 20.87 | 20.4 | 19.88 | 16.3 | 11.31 | 4.64
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | Steady Progression | Headroom (MW) | N/A | 23.98 | 23.95 | 24.15 | 24.25 | 24.36 | 24.4 | 24.38 | 24.33 | 24.28 | 24.23 | 24.2 | 24.19 | 24.19 | 24.16 | 24.14 | 24.1166 | 23.63 | 22.6
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | System Transformation | Headroom (MW) | N/A | 23.98 | 23.94 | 24.13 | 24.17 | 24.14 | 24.09 | 23.94 | 23.76 | 23.58 | 23.46 | 23.35 | 23.25 | 23.17 | 23.07 | 23 | 22.33 | 20.19 | 18.04
Stoke Bardolph 132kV | Nottingham North 33 | BULWELL 33 11kV S STN | Primary | 11 | -1.1988 | 53.0022 | WPD Best View | Headroom (MW) | N/A | 23.98 | 23.9 | 23.99 | 23.92 | 23.5 | 23.2 | 22.83 | 22.46 | 22.08 | 21.79 | 21.48 | 21.16 | 20.81 | 20.36 | 19.84 | 16.3 | 11.32 | 4.69
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Consumer Transformation | Headroom (MW) | Thermal | 11.84 | 11.62 | 11.42 | 11.17 | 10.66 | 10.2 | 9.75 | 9.29 | 8.9 | 8.53 | 8.21 | 7.85 | 7.47 | 7.06 | 6.63 | 3.45 | -1.06 | -6.1
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Leading the Way | Headroom (MW) | Thermal | 11.84 | 11.6 | 11.39 | 11.13 | 10.58 | 10.08 | 9.59 | 9.09 | 8.66 | 8.27 | 7.87 | 7.43 | 6.96 | 6.44 | 5.86 | 1.95 | -3.27 | -10.25
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | Steady Progression | Headroom (MW) | N/A | 11.84 | 11.72 | 11.66 | 11.6 | 11.55 | 11.47 | 11.39 | 11.31 | 11.24 | 11.17 | 11.1 | 11.05 | 11 | 10.97 | 10.95 | 10.94 | 10.4 | 9.46
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | System Transformation | Headroom (MW) | N/A | 11.84 | 11.67 | 11.55 | 11.42 | 11.22 | 11.01 | 10.78 | 10.54 | 10.32 | 10.13 | 9.96 | 9.82 | 9.69 | 9.57 | 9.42 | 8.51 | 6.36 | 4.21
Stoke Bardolph 132kV | Nottingham North 33 | CINDERHILL 33 11kV S STN | Primary | 11 | -1.2018 | 52.9882 | WPD Best View | Headroom (MW) | Thermal | 11.84 | 11.61 | 11.4 | 11.14 | 10.6 | 10.12 | 9.65 | 9.17 | 8.75 | 8.38 | 8.01 | 7.6 | 7.15 | 6.67 | 6.14 | 2.42 | -2.61 | -9.07
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Consumer Transformation | Headroom (MW) | Thermal | 15.5 | 15.23 | 14.98 | 14.68 | 14.05 | 13.53 | 13.03 | 12.56 | 12.13 | 11.74 | 11.35 | 10.96 | 10.53 | 10.07 | 9.57 | 6.04 | 1.01 | -4.6
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Leading the Way | Headroom (MW) | Thermal | 15.5 | 15.21 | 14.95 | 14.63 | 13.95 | 13.4 | 12.87 | 12.4 | 11.95 | 11.55 | 11.09 | 10.62 | 10.11 | 9.53 | 8.86 | 4.46 | -1.35 | -9.14
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | Steady Progression | Headroom (MW) | N/A | 15.5 | 15.36 | 15.28 | 15.21 | 15.14 | 15.05 | 14.96 | 14.87 | 14.8 | 14.71 | 14.64 | 14.58 | 14.54 | 14.52 | 14.51 | 14.33 | 13.57 | 12.46
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | System Transformation | Headroom (MW) | N/A | 15.5 | 15.29 | 15.14 | 14.98 | 14.74 | 14.5 | 14.25 | 14.01 | 13.79 | 13.59 | 13.41 | 13.25 | 13.1 | 12.98 | 12.86 | 11.75 | 9.36 | 7.1
Stoke Bardolph 132kV | Nottingham North 33 | MARLBOROUGH RD 33 11kV S STN | Primary | 11 | -1.1341 | 52.9902 | WPD Best View | Headroom (MW) | Thermal | 15.5 | 15.22 | 14.97 | 14.66 | 14.01 | 13.47 | 12.96 | 12.49 | 12.05 | 11.66 | 11.23 | 10.81 | 10.35 | 9.83 | 9.26 | 5.33 | -0.05 | -6.66
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Consumer Transformation | Headroom (MW) | Thermal | 6.86 | 6.75 | 6.64 | 6.52 | 6.24 | 6.02 | 5.79 | 5.62 | 5.41 | 5.24 | 5.06 | 4.9 | 4.73 | 4.55 | 4.35 | 3.02 | 1.16 | -0.9
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Leading the Way | Headroom (MW) | Thermal | 6.86 | 6.73 | 6.63 | 6.5 | 6.19 | 5.96 | 5.72 | 5.57 | 5.35 | 5.16 | 4.97 | 4.78 | 4.58 | 4.35 | 4.11 | 2.54 | 0.42 | -2.4
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | Steady Progression | Headroom (MW) | N/A | 6.86 | 6.8 | 6.77 | 6.74 | 6.7 | 6.66 | 6.62 | 6.6 | 6.57 | 6.53 | 6.5 | 6.47 | 6.44 | 6.42 | 6.41 | 6.4 | 6.22 | 5.81
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | System Transformation | Headroom (MW) | N/A | 6.86 | 6.77 | 6.71 | 6.65 | 6.53 | 6.43 | 6.32 | 6.25 | 6.14 | 6.05 | 5.96 | 5.89 | 5.82 | 5.76 | 5.71 | 5.39 | 4.53 | 3.66
Walpole 132kV | Boston | DONINGTON 33 11kV S STN | Primary | 11 | -0.189 | 52.9155 | WPD Best View | Headroom (MW) | N/A | 6.86 | 6.78 | 6.74 | 6.68 | 6.6 | 6.53 | 6.45 | 6.42 | 6.35 | 6.29 | 6.23 | 6.18 | 6.13 | 6.09 | 6.06 | 5.87 | 5.31 | 4.65
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Consumer Transformation | Headroom (MW) | Thermal | 3.27 | 3.3 | 3.25 | 3.17 | 2.98 | 2.73 | 2.46 | 2.21 | 1.95 | 1.7 | 1.43 | 1.17 | 0.91 | 0.64 | 0.38 | -2.08 | -3.49 | -6.28
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Leading the Way | Headroom (MW) | Thermal | 3.27 | 3.31 | 3.25 | 3.16 | 2.93 | 2.59 | 2.25 | 1.92 | 1.59 | 1.26 | 0.91 | 0.58 | 0.25 | -0.09 | -0.43 | -2.76 | -5.52 | -8.99
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | Steady Progression | Headroom (MW) | N/A | 3.27 | 3.32 | 3.31 | 3.31 | 3.29 | 3.27 | 3.24 | 3.21 | 3.17 | 3.13 | 3.09 | 3.05 | 3.01 | 2.98 | 2.96 | 2.88 | 2.72 | 2.39
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | System Transformation | Headroom (MW) | Thermal | 3.27 | 3.32 | 3.29 | 3.26 | 3.19 | 3.11 | 3.01 | 2.87 | 2.7 | 2.6 | 2.49 | 2.4 | 2.31 | 2.22 | 2.14 | 1.17 | 0.66 | -0.7
Walpole 132kV | Boston | KIRTON 33 11kV S STN | Primary | 11 | -0.0575 | 52.9216 | WPD Best View | Headroom (MW) | N/A | 3.27 | 3.32 | 3.31 | 3.31 | 3.29 | 3.26 | 3.23 | 3.19 | 3.14 | 3.08 | 3.04 | 3 | 2.96 | 2.93 | 2.9 | 2.81 | 2.66 | 2.32
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Consumer Transformation | Headroom (MW) | Thermal | 1.58 | 1.54 | 1.5 | 1.47 | 1.37 | 1.19 | 0.98 | 0.76 | 0.53 | 0.28 | 0.16 | 0.03 | -0.1 | -0.23 | -0.38 | -1.82 | -2.51 | -3.25
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Leading the Way | Headroom (MW) | Thermal | 1.58 | 1.53 | 1.5 | 1.46 | 1.35 | 1.09 | 0.8 | 0.48 | 0.12 | -0.28 | -0.44 | -0.61 | -0.79 | -0.98 | -1.17 | -2.48 | -3.25 | -4.15
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | Steady Progression | Headroom (MW) | N/A | 1.58 | 1.55 | 1.54 | 1.52 | 1.5 | 1.48 | 1.45 | 1.43 | 1.4 | 1.37 | 1.35 | 1.32 | 1.29 | 1.26 | 1.23 | 1.15 | 1.04 | 0.89
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | System Transformation | Headroom (MW) | Thermal | 1.58 | 1.55 | 1.52 | 1.5 | 1.45 | 1.33 | 1.19 | 1.05 | 0.9 | 0.74 | 0.67 | 0.6 | 0.52 | 0.44 | 0.37 | -0.09 | -0.41 | -0.72
Walpole 132kV | Boston | LANGRICK 33 11kV S STN | Primary | 11 | -0.1246 | 53.0121 | WPD Best View | Headroom (MW) | N/A | 1.58 | 1.55 | 1.53 | 1.51 | 1.49 | 1.39 | 1.27 | 1.15 | 1.02 | 0.88 | 0.84 | 0.8 | 0.75 | 0.71 | 0.66 | 0.43 | 0.27 | 0.05
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Consumer Transformation | Headroom (MW) | Thermal | -2.55 | -2.68 | -8.92 | -9.03 | -9.29 | -9.53 | -10.85 | -12.36 | -13.7 | -14.66 | -15.32 | -15.74 | -15.89 | -16.07 | -15.57 | -17.2 | -17.06 | -19.52
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Leading the Way | Headroom (MW) | Thermal | -2.55 | -2.69 | -8.94 | -9.06 | -9.36 | -9.63 | -9.91 | -10.65 | -11.38 | -11.62 | -11.81 | -12 | -12.2 | -12.42 | -11.82 | 4.64 | -18.35 | -22.45
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | Steady Progression | Headroom (MW) | Thermal | -2.55 | -2.63 | -8.83 | -8.87 | -8.88 | -8.87 | -10.65 | -12.56 | -14.41 | -16.12 | -17.65 | -18.9 | -19.51 | -19.94 | -20.17 | -20.07 | -20.31 | -20.83
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | System Transformation | Headroom (MW) | Thermal | -2.55 | -2.65 | -8.87 | -8.93 | -9.02 | -9.06 | -10.19 | -11.54 | -12.78 | -13.57 | -14.05 | -14.28 | -14.34 | -14.38 | -14.31 | -1.58 | -14.94 | -16.59
Walpole 132kV | Boston | MARSH LANE 33 11kV S STN | Primary | 11 | -0.0136 | 52.9617 | WPD Best View | Headroom (MW) | Thermal | -2.55 | -2.63 | -8.83 | -8.87 | -8.88 | -8.87 | -10.65 | -12.56 | -14.41 | -16.12 | -17.65 | -18.9 | -19.51 | -19.94 | -20.17 | -20.07 | -20.31 | -20.83
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Consumer Transformation | Headroom (MW) | Thermal | 12.705 | 12.525 | 12.365 | 12.165 | 11.725 | 11.295 | 10.785 | 10.245 | 9.705 | 9.175 | 8.785 | 8.405 | 8.005 | 7.575 | 7.075 | 4.175 | 1.005 | -2.555
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Leading the Way | Headroom (MW) | Thermal | 12.705 | 12.505 | 12.345 | 12.135 | 11.665 | 11.135 | 10.545 | 9.915 | 9.265 | 8.595 | 8.135 | 7.675 | 7.165 | 6.675 | 6.105 | 2.885 | -0.915 | -5.825
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | Steady Progression | Headroom (MW) | N/A | 12.705 | 12.605 | 12.545 | 12.495 | 12.435 | 12.355 | 12.265 | 12.175 | 12.085 | 11.995 | 11.915 | 11.855 | 11.795 | 11.745 | 11.695 | 11.605 | 11.255 | 10.575
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | System Transformation | Headroom (MW) | N/A | 12.705 | 12.565 | 12.465 | 12.365 | 12.165 | 11.925 | 11.655 | 11.345 | 11.045 | 10.735 | 10.515 | 10.335 | 10.175 | 10.025 | 9.835 | 9.095 | 7.625 | 6.135
Walpole 132kV | Boston | MOUNT BRIDGE BOSTON 33 11kV S STN | Primary | 11 | -0.0146 | 52.9693 | WPD Best View | Headroom (MW) | N/A | 12.705 | 12.595 | 12.545 | 12.495 | 12.425 | 12.325 | 12.215 | 12.105 | 11.985 | 11.865 | 11.785 | 11.715 | 11.655 | 11.595 | 11.545 | 11.415 | 11.045 | 10.345
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Consumer Transformation | Headroom (MW) | N/A | 13.73 | 13.59 | 13.47 | 13.33 | 12.96 | 12.65 | 12.36 | 12.06 | 11.77 | 11.69 | 11.44 | 11.2 | 10.94 | 10.66 | 10.35 | 7.89 | 5.01 | 1.84
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Leading the Way | Headroom (MW) | Thermal | 13.73 | 13.57 | 13.45 | 13.29 | 12.88 | 12.55 | 12.25 | 11.94 | 11.63 | 11.64 | 11.36 | 11.07 | 10.75 | 10.39 | 10 | 6.83 | 3.52 | -0.74
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | Steady Progression | Headroom (MW) | N/A | 13.73 | 13.65 | 13.61 | 13.57 | 13.52 | 13.46 | 13.42 | 13.36 | 13.3 | 13.35 | 13.33 | 13.3 | 13.29 | 13.27 | 13.26 | 13.29 | 13.05 | 12.41
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | System Transformation | Headroom (MW) | N/A | 13.73 | 13.62 | 13.54 | 13.47 | 13.31 | 13.16 | 13.02 | 12.86 | 12.71 | 12.76 | 12.65 | 12.55 | 12.45 | 12.35 | 12.26 | 11.41 | 9.98 | 8.53
Walpole 132kV | Boston | SLEAFORD ROAD BOSTON 33 11kV S STN | Primary | 11 | -0.033 | 52.9778 | WPD Best View | Headroom (MW) | N/A | 13.73 | 13.65 | 13.61 | 13.57 | 13.52 | 13.46 | 13.41 | 13.35 | 13.29 | 13.35 | 13.32 | 13.29 | 13.27 | 13.26 | 13.25 | 13.27 | 13.03 | 12.38
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Consumer Transformation | Headroom (MW) | Thermal | -0.8 | -0.92 | -1 | -1.1 | -1.33 | -1.76 | -2.44 | -3.25 | -4.08 | -4.96 | -5.6 | -6.19 | -6.79 | -7.4 | -8.18 | -12.3 | -15.87 | -18.91
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Leading the Way | Headroom (MW) | Thermal | -0.8 | -0.92 | -1.01 | -1.11 | -1.3 | -1.96 | -2.84 | -3.87 | -4.97 | -6.22 | -6.92 | -7.6 | -8.32 | -8.98 | -9.71 | -13.7 | -18.47 | -21.95
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | Steady Progression | Headroom (MW) | Thermal | -0.8 | -0.89 | -0.93 | -0.98 | -1.02 | -1.1 | -1.2 | -1.32 | -1.44 | -1.57 | -1.7 | -1.79 | -1.89 | -1.98 | -2.06 | -2.31 | -2.73 | -3.17
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | System Transformation | Headroom (MW) | Thermal | -0.8 | -0.9 | -0.96 | -1.03 | -1.14 | -1.46 | -1.83 | -2.31 | -2.82 | -3.36 | -3.69 | -3.94 | -4.16 | -4.39 | -4.77 | -5.93 | -7.69 | -8.74
Walpole 132kV | Boston | STICKNEY 33 11kV S STN | Primary | 11 | 0.0197 | 53.0887 | WPD Best View | Headroom (MW) | Thermal | -0.8 | -0.9 | -0.96 | -1.02 | -1.13 | -1.36 | -1.62 | -1.99 | -2.36 | -2.79 | -3.08 | -3.3 | -3.49 | -3.7 | -4.05 | -4.73 | -6.3 | -7.07
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Consumer Transformation | Headroom (MW) | Thermal | 14.23 | 14.02 | 13.85 | 13.63 | 13.14 | 12.59 | 12.09 | 10.64 | 8.99 | 7.13 | 4.74 | 1.96 | -1.03 | -3.78 | -7.11 | -14.84 | -24.71 | -36.62
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Leading the Way | Headroom (MW) | Thermal | 14.23 | 14.01 | 13.82 | 13.58 | 13.05 | 12.37 | 11.75 | 11.12 | 10.51 | 9.91 | 9.27 | 8.63 | 6.17 | 3.8 | 1.29 | -7.79 | -19.99 | -28.46
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Steady Progression | Headroom (MW) | Thermal | 14.23 | 14.12 | 14.07 | 14.03 | 13.96 | 13.89 | 13.83 | 13.53 | 13.25 | 12.88 | 12.38 | 11.76 | 10.32 | 8.91 | 7.01 | 4.51 | 1.69 | -1.53
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | System Transformation | Headroom (MW) | Thermal | 14.23 | 14.08 | 13.97 | 13.86 | 13.66 | 13.47 | 13.3 | 12.13 | 10.61 | 9.02 | 6.92 | 4.48 | 1.87 | -0.48 | -3.43 | -8.14 | -15.42 | -24.18
Walpole 132kV | Bourne | BOURNE 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | WPD Best View | Headroom (MW) | Thermal | 14.23 | 14.02 | 13.85 | 13.63 | 13.14 | 12.59 | 12.09 | 10.64 | 8.99 | 7.13 | 4.74 | 1.96 | -1.03 | -3.78 | -7.11 | -14.84 | -24.71 | -36.62
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Consumer Transformation | Headroom (MW) | Thermal | 3.46 | 3.4 | 3.35 | 3.28 | 3.09 | 2.77 | 2.28 | 1.7 | 1.1 | 0.48 | 0.08 | -0.29 | -0.67 | -1.05 | -1.55 | -3.41 | -4.74 | -6.25
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Leading the Way | Headroom (MW) | Thermal | 3.46 | 3.4 | 3.34 | 3.27 | 3.1 | 2.6 | 1.96 | 1.2 | 0.39 | -0.53 | -1.01 | -1.48 | -1.98 | -2.42 | -2.28 | -4.65 | -6.52 | -8.6
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | Steady Progression | Headroom (MW) | N/A | 3.46 | 3.43 | 3.41 | 3.39 | 3.36 | 3.31 | 3.25 | 3.18 | 3.11 | 3.05 | 2.97 | 2.93 | 2.89 | 2.84 | 2.79 | 2.69 | 3.08 | 2.82
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | System Transformation | Headroom (MW) | Thermal | 3.46 | 3.41 | 3.38 | 3.34 | 3.25 | 3.02 | 2.75 | 2.4 | 2.04 | 1.65 | 1.44 | 1.28 | 1.14 | 0.99 | 0.73 | 0.75 | 0.17 | -0.4
Walpole 132kV | Bourne | DOWSBY FEN 33 11kV S STN | Primary | 11 | -0.2762 | 52.8488 | WPD Best View | Headroom (MW) | Thermal | 3.46 | 3.41 | 3.36 | 3.31 | 3.18 | 3.02 | 2.78 | 2.5 | 2.21 | 1.92 | 1.69 | 1.48 | 1.27 | 1.06 | 0.8 | 0.45 | -0.48 | -1.41
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Consumer Transformation | Headroom (MW) | N/A | 9.83 | 9.74 | 9.68 | 9.62 | 9.43 | 9.36 | 9.16 | 8.84 | 8.49 | 8.12 | 7.78 | 7.48 | 7.18 | 6.91 | 6.57 | 4.35 | 3.42 | 2.41
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Leading the Way | Headroom (MW) | N/A | 9.83 | 9.73 | 9.68 | 9.62 | 9.43 | 9.33 | 9.12 | 8.8 | 8.42 | 7.99 | 7.63 | 7.29 | 6.94 | 6.66 | 6.39 | 3.07 | 1.57 | 0.16
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | Steady Progression | Headroom (MW) | N/A | 9.83 | 9.75 | 9.72 | 9.68 | 9.62 | 9.63 | 9.6 | 9.57 | 9.53 | 9.49 | 9.45 | 9.42 | 9.39 | 9.37 | 9.34 | 9.24 | 9.02 | 8.76
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | System Transformation | Headroom (MW) | N/A | 9.83 | 9.75 | 9.7 | 9.66 | 9.54 | 9.5 | 9.42 | 9.28 | 9.09 | 8.87 | 8.7 | 8.57 | 8.48 | 8.36 | 8.14 | 6.8 | 6.36 | 5.91
Walpole 132kV | Bourne | TUNNEL BANK BOURNE 33 11kV S STN | Primary | 11 | -0.3646 | 52.7586 | WPD Best View | Headroom (MW) | N/A | 9.83 | 9.74 | 9.68 | 9.62 | 9.44 | 9.37 | 9.23 | 8.97 | 8.68 | 8.38 | 8.11 | 7.89 | 7.67 | 7.49 | 7.23 | 5.29 | 4.47 | 3.6
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Consumer Transformation | Headroom (MW) | Thermal | 1.93 | 1.85 | 1.77 | 1.67 | 1.35 | 1.05 | 0.56 | -0.02 | -0.65 | -1.29 | -1.84 | -2.35 | -2.88 | -3.42 | -4.05 | -7.07 | -9.05 | -11.23
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Leading the Way | Headroom (MW) | Thermal | 1.93 | 1.84 | 1.76 | 1.65 | 1.35 | 0.91 | 0.33 | -0.33 | -1.07 | -1.9 | -2.52 | -3.14 | -3.79 | -4.39 | -4.97 | -7.98 | -10.7 | -13.8
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | Steady Progression | Headroom (MW) | N/A | 1.93 | 1.89 | 1.87 | 1.85 | 1.81 | 1.77 | 1.73 | 1.68 | 1.61 | 1.55 | 1.47 | 1.43 | 1.39 | 1.34 | 1.29 | 1.22 | 0.91 | 0.55
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | System Transformation | Headroom (MW) | Thermal | 1.93 | 1.87 | 1.83 | 1.78 | 1.63 | 1.43 | 1.2 | 0.89 | 0.55 | 0.19 | -0.1 | -0.32 | -0.52 | -0.74 | -1.06 | -1.87 | -2.74 | -3.61
Walpole 132kV | Spalding & South Holland | CROWLAND 33 11kV S STN | Primary | 11 | -0.164 | 52.6835 | WPD Best View | Headroom (MW) | Thermal | 1.93 | 1.87 | 1.82 | 1.76 | 1.57 | 1.32 | 1.05 | 0.69 | 0.3 | -0.11 | -0.43 | -0.68 | -0.9 | -1.16 | -1.54 | -3.05 | -4.2 | -5.39
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Consumer Transformation | Headroom (MW) | Thermal | 10.7 | 10.52 | 10.25 | 10.04 | 9.47 | 9.05 | 8.37 | 7.54 | 6.7 | 5.92 | 5.15 | 4.4 | 3.58 | 2.73 | 1.7 | -1.9 | -5.63 | -9.79
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Leading the Way | Headroom (MW) | Thermal | 10.7 | 10.5 | 10.22 | 10.01 | 9.46 | 8.93 | 8.2 | 7.35 | 6.49 | 5.66 | 4.83 | 3.92 | 2.94 | 2.04 | 1.1 | -3.05 | -8.02 | -14.1
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | Steady Progression | Headroom (MW) | N/A | 10.7 | 10.61 | 10.55 | 10.5 | 10.42 | 10.35 | 10.24 | 10.1 | 9.97 | 9.89 | 9.8 | 9.75 | 9.7 | 9.65 | 9.61 | 9.51 | 9.09 | 8.27
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | System Transformation | Headroom (MW) | N/A | 10.7 | 10.57 | 10.46 | 10.25 | 9.98 | 9.75 | 9.46 | 9.01 | 8.57 | 8.17 | 7.8 | 7.49 | 7.22 | 6.93 | 6.46 | 5.43 | 3.69 | 1.99
Walpole 132kV | Spalding & South Holland | HOLBEACH 33 11kV S STN | Primary | 11 | 0.0295 | 52.8169 | WPD Best View | Headroom (MW) | N/A | 10.7 | 10.57 | 10.46 | 10.25 | 9.98 | 9.75 | 9.46 | 9.01 | 8.57 | 8.18 | 7.81 | 7.49 | 7.23 | 6.93 | 6.47 | 5.44 | 3.7 | 2
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Consumer Transformation | Headroom (MW) | Thermal | 8.63 | 8.42 | 8.29 | 8.13 | 7.58 | 7.03 | 6.3 | 5.47 | 4.57 | 3.67 | 2.76 | 1.91 | 1.05 | 0.14 | -1 | -7.36 | -13.12 | -19.18
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Leading the Way | Headroom (MW) | Thermal | 8.63 | 8.41 | 8.26 | 8.1 | 7.54 | 6.76 | 5.91 | 4.97 | 3.94 | 2.8 | 1.71 | 0.64 | -0.48 | -1.52 | -2.69 | -10.51 | -17.7 | -25.74
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | Steady Progression | Headroom (MW) | N/A | 8.63 | 8.5 | 8.44 | 8.4 | 8.3 | 8.22 | 8.15 | 8.08 | 7.99 | 7.91 | 7.82 | 7.78 | 7.74 | 7.72 | 7.7 | 7.68 | 7.26 | 6.5
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | System Transformation | Headroom (MW) | Thermal | 8.63 | 8.46 | 8.38 | 8.28 | 8.02 | 7.77 | 7.56 | 7.16 | 6.66 | 6.25 | 5.85 | 5.57 | 5.34 | 5.08 | 4.63 | 2.54 | -0.22 | -3
Walpole 132kV | Spalding & South Holland | LONG SUTTON 33 11kV S STN | Primary | 11 | 0.1137 | 52.7784 | WPD Best View | Headroom (MW) | Thermal | 8.63 | 8.46 | 8.38 | 8.28 | 8.02 | 7.8 | 7.62 | 7.25 | 6.8 | 6.42 | 6.03 | 5.75 | 5.52 | 5.26 | 4.81 | 2.78 | 0.02 | -2.76
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Consumer Transformation | Headroom (MW) | N/A | 12.17 | 14.06 | 13.93 | 13.78 | 13.48 | 13.17 | 12.86 | 12.56 | 12.29 | 12.46 | 12.25 | 12.05 | 11.81 | 11.56 | 11.29 | 9.11 | 5.88 | 2.11
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Leading the Way | Headroom (MW) | Thermal | 12.17 | 14.05 | 13.92 | 13.76 | 13.42 | 13.05 | 12.68 | 12.32 | 11.98 | 12.3 | 12.02 | 11.74 | 11.39 | 11.02 | 10.62 | 7.84 | 0.98 | -3.85
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | Steady Progression | Headroom (MW) | N/A | 12.17 | 12.07 | 12.01 | 11.96 | 11.9 | 11.87 | 11.83 | 11.79 | 11.77 | 11.99 | 12.03 | 12.08 | 12.12 | 12.16 | 12.23 | 14.46 | 14.15 | 13.53
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | System Transformation | Headroom (MW) | N/A | 12.17 | 12.04 | 11.95 | 11.87 | 11.72 | 11.63 | 11.57 | 11.5 | 11.35 | 11.71 | 11.72 | 11.74 | 11.73 | 11.73 | 11.85 | 13.21 | 9.49 | 7.66
Walpole 132kV | Spalding & South Holland | SPALDING CLAY LAKE 11kV S STN | Primary | 11 | -0.1429 | 52.7733 | WPD Best View | Headroom (MW) | N/A | 12.17 | 12.04 | 11.95 | 11.87 | 11.72 | 11.63 | 11.57 | 11.5 | 11.35 | 11.71 | 11.72 | 11.74 | 11.73 | 11.73 | 11.85 | 13.21 | 9.49 | 7.66
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Consumer Transformation | Headroom (MW) | Thermal | 16.46 | 16.21 | 16 | 15.75 | 15.17 | 14.69 | 14.18 | 13.65 | 13.19 | 12.63 | 12.14 | 11.62 | 11.08 | 10.52 | 9.92 | 6.15 | 1.86 | -2.89
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Leading the Way | Headroom (MW) | Thermal | 16.46 | 16.2 | 15.98 | 15.71 | 15.1 | 14.58 | 14.03 | 13.48 | 13.02 | 12.34 | 11.78 | 11.14 | 10.46 | 9.79 | 9.09 | 4.78 | -0.33 | -6.79
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | Steady Progression | Headroom (MW) | N/A | 11.922 | 11.9053 | 11.8943 | 11.8828 | 11.8624 | 11.8239 | 11.7737 | 11.711 | 11.6483 | 11.5828 | 11.5073 | 11.4465 | 11.3817 | 11.3155 | 11.2526 | 10.9665 | 10.6752 | 10.3754
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | System Transformation | Headroom (MW) | N/A | 15.7898 | 15.7408 | 15.6936 | 15.637 | 15.5018 | 15.3364 | 15.1453 | 14.8784 | 14.6083 | 14.3181 | 14.0096 | 13.7302 | 13.4566 | 13.1692 | 12.8176 | 11.5728 | 10.39 | 8.26
Walpole 132kV | Spalding & South Holland | SPALDING PARK ROAD 33 11kV S STN | Primary | 11 | -0.1543 | 52.7957 | WPD Best View | Headroom (MW) | N/A | 16.2888 | 16.2382 | 16.13 | 15.99 | 15.72 | 15.49 | 15.18 | 14.86 | 14.6 | 14.23 | 13.94 | 13.5568 | 13.1302 | 12.7041 | 12.215 | 10.601 | 8.91 | 6.61
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Consumer Transformation | Headroom (MW) | N/A | 15.12 | 15.08 | 15.03 | 14.98 | 14.89 | 14.96 | 14.95 | 14.91 | 14.85 | 14.8 | 14.76 | 14.69 | 14.63 | 14.55 | 14.48 | 13.94 | 13.24 | 12.48
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Leading the Way | Headroom (MW) | N/A | 15.12 | 15.08 | 15.03 | 14.98 | 14.86 | 15 | 15 | 14.95 | 14.91 | 14.87 | 14.84 | 14.76 | 14.66 | 14.57 | 14.46 | 13.84 | 13.07 | 12.13
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | Steady Progression | Headroom (MW) | N/A | 15.12 | 15.08 | 15.03 | 14.99 | 14.93 | 14.99 | 14.97 | 14.95 | 14.92 | 14.91 | 14.9 | 14.88 | 14.86 | 14.84 | 14.82 | 14.71 | 14.5 | 14.26
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | System Transformation | Headroom (MW) | N/A | 15.12 | 15.08 | 15.03 | 14.99 | 14.92 | 15 | 14.99 | 14.96 | 14.92 | 14.92 | 14.93 | 14.9 | 14.88 | 14.85 | 14.83 | 14.66 | 14.22 | 13.8
Walpole 132kV | Spalding & South Holland | WARDENTREE PARK 33 11kV S STN | Primary | 11 | -0.1342 | 52.8136 | WPD Best View | Headroom (MW) | N/A | 15.12 | 15.08 | 15.03 | 14.99 | 14.92 | 15 | 14.99 | 14.96 | 14.93 | 14.93 | 14.93 | 14.91 | 14.89 | 14.86 | 14.84 | 14.66 | 14.23 | 13.8
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Consumer Transformation | Headroom (MW) | Thermal | 3.11 | 3.07 | 3.03 | 2.99 | 2.82 | 2.66 | 2.34 | 1.92 | 1.49 | 1.04 | 0.65 | 0.31 | -0.04 | -0.41 | -0.91 | -2.42 | -3.39 | -4.49
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Leading the Way | Headroom (MW) | Thermal | 3.11 | 3.06 | 3.02 | 2.98 | 2.84 | 2.59 | 2.22 | 1.75 | 1.26 | 0.69 | 0.26 | -0.16 | -0.59 | -0.96 | -1.38 | -2.99 | -4.53 | -6.23
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | Steady Progression | Headroom (MW) | N/A | 3.11 | 3.08 | 3.06 | 3.05 | 3.01 | 2.98 | 2.93 | 2.86 | 2.8 | 2.75 | 2.68 | 2.65 | 2.63 | 2.6 | 2.57 | 2.49 | 2.34 | 2.15
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | System Transformation | Headroom (MW) | Thermal | 3.11 | 3.07 | 3.05 | 3.02 | 2.93 | 2.81 | 2.67 | 2.43 | 2.19 | 1.92 | 1.72 | 1.58 | 1.47 | 1.34 | 1.08 | 0.68 | 0.26 | -0.15
Walpole 132kV | Spalding & South Holland | WHAPLODE DROVE 33 11kV S STN | Primary | 11 | -0.052 | 52.6979 | WPD Best View | Headroom (MW) | Thermal | 3.11 | 3.07 | 3.05 | 3.02 | 2.93 | 2.8 | 2.65 | 2.4 | 2.15 | 1.87 | 1.67 | 1.53 | 1.41 | 1.28 | 1.01 | 0.48 | 0.04 | -0.38
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Consumer Transformation | Headroom (MW) | N/A | 12.73 | 12.58 | 12.45 | 12.3 | 11.9 | 11.57 | 11.26 | 10.98 | 10.6 | 10.23 | 9.88 | 9.53 | 9.18 | 8.79 | 8.35 | 6.13 | 3.38 | 0.48
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Leading the Way | Headroom (MW) | Thermal | 12.73 | 12.57 | 12.43 | 12.27 | 11.84 | 11.46 | 11.15 | 10.91 | 10.49 | 10.05 | 9.64 | 9.22 | 8.78 | 8.33 | 7.84 | 5.28 | 2 | -2.03
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | Steady Progression | Headroom (MW) | N/A | 12.73 | 12.65 | 12.61 | 12.57 | 12.52 | 12.46 | 12.44 | 12.46 | 12.42 | 12.38 | 12.34 | 12.32 | 12.3 | 12.29 | 12.28 | 12.36 | 12.07 | 11.49
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | System Transformation | Headroom (MW) | N/A | 12.73 | 12.62 | 12.54 | 12.46 | 12.28 | 12.12 | 12.01 | 11.92 | 11.72 | 11.53 | 11.35 | 11.22 | 11.09 | 10.97 | 10.78 | 10.24 | 8.98 | 7.77
Walpole 132kV | Stamford | MARKET DEEPING 33 11kV S STN | Primary | 11 | -0.3012 | 52.6782 | WPD Best View | Headroom (MW) | N/A | 12.73 | 12.58 | 12.45 | 12.3 | 11.91 | 11.58 | 11.32 | 11.1 | 10.78 | 10.46 | 10.18 | 9.91 | 9.64 | 9.34 | 8.97 | 6.95 | 4.38 | 1.6
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Consumer Transformation | Headroom (MW) | Thermal | 16.37 | 16.15 | 15.9 | 15.23 | 14.5 | 13.96 | 12.42 | 9.49 | 7.06 | 4.67 | 2.18 | -0.47 | -3.19 | -5.92 | -9.06 | -21.25 | -35.79 | -51.62
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Leading the Way | Headroom (MW) | Thermal | 16.37 | 16.12 | 15.88 | 15.21 | 14.4 | 13.86 | 12.21 | 10.67 | 9.37 | 7.65 | 6.28 | 4.96 | 2.7 | 0.35 | -2.19 | -13.48 | -27.56 | -40.89
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | Steady Progression | Headroom (MW) | N/A | 16.37 | 16.26 | 16.19 | 16.12 | 16.02 | 15.97 | 15.94 | 15.77 | 15.44 | 14.24 | 13.84 | 13.36 | 12.47 | 11.7 | 10.76 | 9.46 | 7.45 | 4.94
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | System Transformation | Headroom (MW) | Thermal | 16.37 | 16.21 | 16.07 | 15.91 | 15.61 | 15.4 | 15.19 | 14.55 | 12.93 | 11.75 | 10.3 | 8.77 | 7.2 | 5.83 | 4.14 | 0.17 | -5.92 | -12.76
Walpole 132kV | Stamford | STAMFORD 11kV S STN | Primary | 11 | -0.4717 | 52.6516 | WPD Best View | Headroom (MW) | Thermal | 16.37 | 16.16 | 15.93 | 15.29 | 14.63 | 14.15 | 13.2 | 11.33 | 9.23 | 7.35 | 5.29 | 3.1 | 0.81 | -1.39 | -3.96 | -13.14 | -24.5 | -37.04
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Consumer Transformation | Headroom (MW) | Thermal | 5.09 | 5.04 | 5 | 4.94 | 4.78 | 4.67 | 4.57 | 4.33 | 4.07 | 3.77 | 3.42 | 3.03 | 2.59 | 2.19 | 1.7 | 0.48 | -1.04 | -2.82
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Leading the Way | Headroom (MW) | Thermal | 5.09 | 5.03 | 4.99 | 4.92 | 4.74 | 4.63 | 4.53 | 4.43 | 4.34 | 4.25 | 4.16 | 4.06 | 3.71 | 3.36 | 3 | 1.59 | -0.25 | -1.72
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | Steady Progression | Headroom (MW) | N/A | 5.09 | 5.07 | 5.06 | 5.05 | 5.03 | 5.02 | 5.01 | 4.95 | 4.91 | 4.84 | 4.77 | 4.68 | 4.48 | 4.3 | 4.04 | 3.75 | 3.35 | 2.84
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | System Transformation | Headroom (MW) | Thermal | 5.09 | 5.06 | 5.03 | 5 | 4.93 | 4.89 | 4.84 | 4.65 | 4.42 | 4.17 | 3.87 | 3.53 | 3.16 | 2.83 | 2.42 | 1.72 | 0.68 | -0.52
Walpole 132kV | Stamford | TINWELL ROAD KETTON 33 11kV S STN | Primary | 11 | -0.5431 | 52.6377 | WPD Best View | Headroom (MW) | Thermal | 5.09 | 5.06 | 5.03 | 5 | 4.93 | 4.89 | 4.84 | 4.65 | 4.42 | 4.16 | 3.86 | 3.52 | 3.15 | 2.82 | 2.41 | 1.71 | 0.67 | -0.53
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Consumer Transformation | Headroom (MW) | Thermal | 8.97 | 8.87 | 8.8 | 8.71 | 8.5 | 8.34 | 8.19 | 7.74 | 7.23 | 6.65 | 5.94 | 5.12 | 4.24 | 3.43 | 2.43 | 0.23 | -2.52 | -5.8
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Leading the Way | Headroom (MW) | Thermal | 8.97 | 8.87 | 8.79 | 8.69 | 8.47 | 8.3 | 8.14 | 7.99 | 7.85 | 7.72 | 7.58 | 7.43 | 6.74 | 6.06 | 5.34 | 2.84 | -0.56 | -2.78
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | Steady Progression | Headroom (MW) | N/A | 8.97 | 8.91 | 8.88 | 8.85 | 8.82 | 8.78 | 8.75 | 8.64 | 8.53 | 8.4 | 8.23 | 8.03 | 7.57 | 7.13 | 6.53 | 5.78 | 4.92 | 3.85
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | System Transformation | Headroom (MW) | Thermal | 8.97 | 8.9 | 8.85 | 8.8 | 8.71 | 8.63 | 8.55 | 8.17 | 7.7 | 7.18 | 6.53 | 5.77 | 4.96 | 4.23 | 3.31 | 1.87 | -0.22 | -2.68
Walpole 132kV | Stamford | WEST DEEPING 33 11kV S STN | Primary | 11 | -0.356 | 52.6715 | WPD Best View | Headroom (MW) | Thermal | 8.97 | 8.87 | 8.8 | 8.71 | 8.5 | 8.34 | 8.19 | 7.74 | 7.23 | 6.65 | 5.94 | 5.12 | 4.24 | 3.43 | 2.43 | 0.23 | -2.52 | -5.8
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Consumer Transformation | Headroom (MW) | Thermal | 6.58 | 6.51 | 6.47 | 6.42 | 6.3 | 6.21 | 6.12 | 3.34 | 2.91 | 2.41 | 1.81 | 1.11 | 0.36 | -0.32 | -1.18 | -2.8 | -4.8 | -7.24
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Leading the Way | Headroom (MW) | Thermal | 6.58 | 6.51 | 6.46 | 6.42 | 6.28 | 3.78 | 3.68 | 3.6 | 3.52 | 3.45 | 3.38 | 3.31 | 2.74 | 2.19 | 1.59 | -0.27 | -2.79 | -4.15
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | Steady Progression | Headroom (MW) | Thermal | 6.58 | 6.53 | 6.51 | 6.5 | 6.47 | 6.44 | 6.42 | 6.32 | 6.22 | 3.7 | 3.55 | 3.38 | 2.98 | 2.58 | 2.04 | 1.35 | 0.63 | -0.21
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | System Transformation | Headroom (MW) | Thermal | 6.58 | 6.52 | 6.49 | 6.47 | 6.41 | 6.36 | 6.3 | 3.56 | 3.14 | 2.66 | 2.08 | 1.41 | 0.69 | 0.04 | -0.77 | -1.97 | -3.59 | -5.58
Walpole 132kV | Stamford | WITTERING 33 11kV S STN | Primary | 11 | -0.4394 | 52.6116 | WPD Best View | Headroom (MW) | Thermal | 6.58 | 6.52 | 6.47 | 6.44 | 6.34 | 6.27 | 6.19 | 3.42 | 3 | 2.51 | 1.92 | 1.24 | 0.5 | -0.17 | -1.01 | -2.48 | -4.36 | -6.65
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Consumer Transformation | Headroom (MW) | Fault level | 18.8696 | 18.8058 | 18.7112 | 18.597 | 18.2905 | 17.963 | 16.7348 | 14.7484 | 13.2212 | 11.7741 | 10.2504 | 8.7765 | 7.3219 | 5.7504 | 4.0746 | -3.7148 | -10.7885 | -17.7119
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Leading the Way | Headroom (MW) | Fault level | 25.8244 | 25.7325 | 25.617 | 25.4738 | 25.0854 | 24.6293 | 22.8781 | 21.3035 | 19.9846 | 18.1902 | 16.4946 | 14.8449 | 13.0845 | 11.2159 | 9.2622 | 12.72 | -15.3682 | -25.3572
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | Steady Progression | Headroom (MW) | N/A | 10.4096 | 10.4 | 10.3902 | 10.3814 | 10.3691 | 10.3426 | 10.2668 | 10.2287 | 10.1136 | 9.629 | 9.508 | 9.3648 | 9.1821 | 9.0461 | 8.9237 | 8.5047 | 12.0014 | 11.7119
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | System Transformation | Headroom (MW) | N/A | 14.8753 | 14.8464 | 14.8133 | 14.7771 | 14.6982 | 14.5909 | 14.421 | 14.2565 | 13.5447 | 13.1381 | 12.6693 | 12.2246 | 11.7952 | 11.4113 | 11.0076 | 16.3781 | 9.6766 | 7.7686
West Burton 132kV | Lincoln 132 11 | LINCOLN No 2 11kV S STN | Primary | 11 | -0.5216 | 53.2282 | WPD Best View | Headroom (MW) | N/A | 15.5095 | 15.4844 | 15.4578 | 15.4308 | 15.3666 | 15.276 | 15.1377 | 15.0155 | 14.7767 | 13.9889 | 13.7344 | 13.446 | 13.0986 | 12.8185 | 12.553 | 18.9986 | 13.1139 | 12.3287
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Consumer Transformation | Headroom (MW) | Thermal | 15.15 | 14.98 | 14.83 | 14.23 | 13.75 | 13.31 | 12.88 | 12.47 | 12.08 | 11.72 | 11.39 | 11.06 | 10.73 | 10.35 | 9.95 | 7.11 | 3.34 | -0.85
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Leading the Way | Headroom (MW) | Thermal | 15.15 | 14.96 | 14.81 | 14.19 | 13.67 | 13.18 | 12.71 | 12.26 | 11.82 | 11.42 | 11.05 | 10.66 | 10.25 | 9.8 | 9.29 | 5.91 | 1.56 | -4.16
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | Steady Progression | Headroom (MW) | N/A | 15.15 | 15.07 | 15.04 | 14.99 | 14.95 | 14.89 | 14.82 | 14.75 | 14.68 | 14.61 | 14.55 | 14.49 | 14.45 | 14.41 | 14.38 | 14.33 | 13.72 | 12.89
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | System Transformation | Headroom (MW) | N/A | 15.15 | 15.03 | 14.94 | 14.84 | 14.65 | 14.45 | 14.22 | 14 | 13.79 | 13.6 | 13.43 | 13.28 | 13.14 | 13.01 | 12.89 | 12.05 | 10.23 | 8.44
West Burton 132kV | Lincoln 33 | ANDERSON LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5393 | 53.2426 | WPD Best View | Headroom (MW) | N/A | 15.15 | 15.03 | 14.96 | 14.87 | 14.71 | 14.55 | 14.37 | 14.2 | 14.04 | 13.89 | 13.75 | 13.62 | 13.51 | 13.4 | 13.3 | 12.63 | 11 | 9.38
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Consumer Transformation | Headroom (MW) | N/A | 13.74 | 13.7 | 13.67 | 13.64 | 13.59 | 13.48 | 13.35 | 13.24 | 13.13 | 13.03 | 12.92 | 12.82 | 12.72 | 12.61 | 12.49 | 11.65 | 10.49 | 9.18
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Leading the Way | Headroom (MW) | N/A | 13.74 | 13.7 | 13.67 | 13.64 | 13.57 | 13.47 | 13.34 | 13.22 | 13.11 | 13.01 | 12.89 | 12.78 | 12.66 | 12.53 | 12.39 | 11.38 | 10.04 | 8.29
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | Steady Progression | Headroom (MW) | N/A | 13.74 | 13.71 | 13.69 | 13.67 | 13.65 | 13.63 | 13.62 | 13.6 | 13.57 | 13.55 | 13.52 | 13.5 | 13.47 | 13.45 | 13.42 | 13.3 | 13.16 | 12.99
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | System Transformation | Headroom (MW) | N/A | 13.74 | 13.7 | 13.68 | 13.66 | 13.63 | 13.61 | 13.58 | 13.54 | 13.51 | 13.45 | 13.39 | 13.34 | 13.3 | 13.26 | 13.23 | 13.03 | 12.45 | 11.84
West Burton 132kV | Lincoln 33 | BEEVOR STREET 33 11kV S STN | Primary | 11 | -0.5526 | 53.2253 | WPD Best View | Headroom (MW) | N/A | 13.74 | 13.7 | 13.68 | 13.66 | 13.63 | 13.61 | 13.58 | 13.54 | 13.51 | 13.45 | 13.39 | 13.34 | 13.3 | 13.26 | 13.23 | 13.03 | 12.45 | 11.84
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Consumer Transformation | Headroom (MW) | Thermal | 14.32 | 14.11 | 8.79 | 8.57 | 8.06 | 7.67 | 6.19 | 3.87 | 1.93 | 0.14 | -1.73 | -3.53 | -5.35 | -7.24 | -9.41 | -17.88 | -28.71 | -40.04
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Leading the Way | Headroom (MW) | Thermal | 14.32 | 14.09 | 8.78 | 8.55 | 8.03 | 7.61 | 6.31 | 5.15 | 4.16 | 3 | 1.9 | 0.86 | -0.66 | -2.22 | -3.95 | -11.88 | -19.8 | -27.87
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | Steady Progression | Headroom (MW) | Thermal | 14.32 | 14.19 | 8.99 | 8.93 | 8.84 | 8.76 | 8.15 | 7.49 | 6.74 | 5.47 | 4.77 | 4.11 | 3.39 | 2.81 | 2.2 | 1.4 | 0.2 | -1.42
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | System Transformation | Headroom (MW) | Thermal | 14.32 | 14.15 | 8.91 | 8.78 | 8.56 | 8.37 | 7.8 | 7.02 | 5.66 | 4.67 | 3.62 | 2.63 | 1.7 | 0.9 | -0.09 | -2.63 | -6.45 | -10.55
West Burton 132kV | Lincoln 33 | DODDINGTON PARK 33 11kV S STN | Primary | 11 | -0.6155 | 53.2061 | WPD Best View | Headroom (MW) | Thermal | 14.32 | 14.16 | 8.93 | 8.82 | 8.62 | 8.45 | 7.7 | 6.88 | 5.96 | 4.51 | 3.64 | 2.82 | 1.92 | 1.18 | 0.36 | -1.24 | -4.04 | -6.49
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Consumer Transformation | Headroom (MW) | Thermal | 10.57 | 10.39 | 9.98 | 9.82 | 9.41 | 9.06 | 8.71 | 7.72 | 6.59 | 5.31 | 3.83 | 2.15 | 0.32 | -1.43 | -3.56 | -8.18 | -13.94 | -20.79
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Leading the Way | Headroom (MW) | Thermal | 10.57 | 10.38 | 9.96 | 9.81 | 9.36 | 8.99 | 8.62 | 8.27 | 7.93 | 7.61 | 7.29 | 6.97 | 5.52 | 4.1 | 2.54 | -2.84 | -9.97 | -15.02
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | Steady Progression | Headroom (MW) | N/A | 10.57 | 10.48 | 10.44 | 10.44 | 10.39 | 10.34 | 10.28 | 10.06 | 9.84 | 9.57 | 9.23 | 8.84 | 7.92 | 7.03 | 5.83 | 4.34 | 2.58 | 0.44
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | System Transformation | Headroom (MW) | Thermal | 10.57 | 10.44 | 10.35 | 10.03 | 9.88 | 9.72 | 9.54 | 8.72 | 7.71 | 6.57 | 5.22 | 3.67 | 1.99 | 0.49 | -1.38 | -4.44 | -8.69 | -13.65
West Burton 132kV | Lincoln 33 | FISKERTON 33 11kV S STN | Primary | 11 | -0.4154 | 53.2382 | WPD Best View | Headroom (MW) | N/A | 10.57 | 10.48 | 10.44 | 10.44 | 10.39 | 10.34 | 10.28 | 10.06 | 9.84 | 9.57 | 9.23 | 8.84 | 7.92 | 7.03 | 5.83 | 4.34 | 2.58 | 0.44
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Consumer Transformation | Headroom (MW) | Thermal | 7.41 | 7.28 | 7.17 | 7.03 | 6.66 | 6.38 | 5.99 | 5.02 | 3.93 | 2.73 | 1.24 | -0.39 | -2.18 | -3.85 | -5.96 | -10.19 | -15.21 | -21.22
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Leading the Way | Headroom (MW) | Thermal | 7.41 | 7.27 | 7.15 | 7.01 | 6.64 | 6.3 | 5.89 | 5.42 | 4.96 | 4.44 | 3.91 | 3.41 | 1.93 | 0.51 | -1.02 | -6.01 | -12.63 | -17.17
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | Steady Progression | Headroom (MW) | Thermal | 7.41 | 7.35 | 7.32 | 7.29 | 7.24 | 7.19 | 7.12 | 6.92 | 6.72 | 6.5 | 6.19 | 5.86 | 5.09 | 4.34 | 3.33 | 2.03 | 0.49 | -1.32
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | System Transformation | Headroom (MW) | Thermal | 7.41 | 7.32 | 7.25 | 7.18 | 7.02 | 6.87 | 6.71 | 5.97 | 5.09 | 4.1 | 2.83 | 1.45 | -0.01 | -1.34 | -3.09 | -5.74 | -9.42 | -13.74
West Burton 132kV | Lincoln 33 | METHERINGHAM 33 11kV S STN | Primary | 11 | -0.4092 | 53.1352 | WPD Best View | Headroom (MW) | Thermal | 7.41 | 7.35 | 7.32 | 7.29 | 7.24 | 7.19 | 7.12 | 6.92 | 6.72 | 6.5 | 6.19 | 5.86 | 5.09 | 4.34 | 3.33 | 2.03 | 0.49 | -1.32
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Consumer Transformation | Headroom (MW) | Thermal | 12.17 | 11.92 | 11.73 | 11.49 | 10.84 | 10.37 | 9.91 | 9.13 | 8.26 | 7.31 | 6.15 | 4.84 | 3.46 | 2.13 | 0.62 | -3.99 | -9.68 | -16.25
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Leading the Way | Headroom (MW) | Thermal | 12.17 | 11.9 | 11.7 | 11.44 | 10.7 | 10.2 | 9.71 | 9.22 | 8.72 | 8.22 | 7.67 | 7.14 | 5.93 | 4.71 | 3.48 | -1.68 | -8.51 | -14.85
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | Steady Progression | Headroom (MW) | N/A | 12.17 | 12.03 | 11.98 | 11.94 | 11.86 | 11.79 | 11.72 | 11.57 | 11.42 | 11.24 | 11.01 | 10.75 | 10.21 | 9.67 | 8.97 | 8.05 | 6.81 | 5.05
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | System Transformation | Headroom (MW) | Thermal | 12.17 | 11.98 | 11.87 | 11.75 | 11.5 | 11.29 | 11.06 | 10.49 | 9.84 | 9.11 | 8.18 | 7.15 | 6.06 | 5.04 | 3.82 | 1.47 | -2.16 | -6.22
West Burton 132kV | Lincoln 33 | NORTH HYKEHAM 33 11kV S STN | Primary | 11 | -0.5996 | 53.1926 | WPD Best View | Headroom (MW) | N/A | 12.17 | 12.02 | 11.97 | 11.91 | 11.82 | 11.73 | 11.64 | 11.47 | 11.3 | 11.1 | 10.87 | 10.59 | 10.03 | 9.49 | 8.78 | 7.73 | 6.24 | 4.33
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Consumer Transformation | Headroom (MW) | Thermal | 13.32 | 13.24 | 13.08 | 12.87 | 12.67 | 12.41 | 12.13 | 11.75 | 11.39 | 11.03 | 10.66 | 10.25 | 9.81 | 9.28 | 8.72 | 5.37 | 1.68 | -2.34
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Leading the Way | Headroom (MW) | Thermal | 13.32 | 13.23 | 13.06 | 12.84 | 12.67 | 12.44 | 12.19 | 11.76 | 11.34 | 10.91 | 10.45 | 9.95 | 9.39 | 8.74 | 8.05 | 4.19 | -0.02 | -5.54
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | Steady Progression | Headroom (MW) | N/A | 13.32 | 13.26 | 13.23 | 13.19 | 13.27 | 13.34 | 13.38 | 13.38 | 13.38 | 13.38 | 13.38 | 13.37 | 13.35 | 13.31 | 13.27 | 13.18 | 12.71 | 11.85
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | System Transformation | Headroom (MW) | N/A | 13.32 | 13.25 | 13.19 | 13.08 | 13.14 | 13.12 | 13.05 | 12.87 | 12.7 | 12.52 | 12.34 | 12.13 | 11.92 | 11.71 | 11.48 | 10.24 | 8.38 | 6.58
West Burton 132kV | Lincoln 33 | ROOKERY LANE LINCOLN 33 11kV S STN | Primary | 11 | -0.5613 | 53.2103 | WPD Best View | Headroom (MW) | N/A | 13.32 | 13.25 | 13.2 | 13.1 | 13.17 | 13.16 | 13.1 | 12.93 | 12.77 | 12.59 | 12.42 | 12.23 | 12.03 | 11.81 | 11.59 | 10.41 | 8.67 | 6.95
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Consumer Transformation | Headroom (MW) | N/A | 10.52 | 10.5 | 10.49 | 10.48 | 10.47 | 10.46 | 10.45 | 10.44 | 10.43 | 10.42 | 10.41 | 10.4 | 10.39 | 10.38 | 10.37 | 10.32 | 10.28 | 10.25
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Leading the Way | Headroom (MW) | N/A | 10.52 | 10.5 | 10.49 | 10.48 | 10.46 | 10.45 | 10.45 | 10.43 | 10.42 | 10.41 | 10.4 | 10.39 | 10.38 | 10.37 | 10.36 | 10.32 | 10.28 | 10.24
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | Steady Progression | Headroom (MW) | N/A | 10.52 | 10.5 | 10.49 | 10.48 | 10.47 | 10.47 | 10.46 | 10.45 | 10.44 | 10.43 | 10.42 | 10.42 | 10.41 | 10.4 | 10.39 | 10.36 | 10.32 | 10.29
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | System Transformation | Headroom (MW) | N/A | 10.52 | 10.5 | 10.49 | 10.48 | 10.47 | 10.46 | 10.45 | 10.44 | 10.44 | 10.43 | 10.42 | 10.41 | 10.4 | 10.39 | 10.38 | 10.35 | 10.31 | 10.28
West Burton 132kV | Lincoln 33 | RUSTON HORNSBY 33 6 6kV S STN | Primary | 6.6 | -0.5525 | 53.2252 | WPD Best View | Headroom (MW) | N/A | 10.52 | 10.5 | 10.49 | 10.48 | 10.47 | 10.46 | 10.45 | 10.44 | 10.44 | 10.43 | 10.42 | 10.41 | 10.4 | 10.39 | 10.38 | 10.35 | 10.31 | 10.28
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Consumer Transformation | Headroom (MW) | Thermal | 6.21 | 6.1 | 5.84 | 5.71 | 5.34 | 4.99 | 4.65 | 3.45 | 2.05 | 0.45 | -1.51 | -3.79 | -6.23 | -8.48 | -11.23 | -17.54 | -25.11 | -33.72
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Leading the Way | Headroom (MW) | Thermal | 6.21 | 6.08 | 5.82 | 5.68 | 5.25 | 4.83 | 4.43 | 4.03 | 3.66 | 3.3 | 2.9 | 2.47 | 0.49 | -1.4 | -3.39 | -10.64 | -19.95 | -25.47
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | Steady Progression | Headroom (MW) | Thermal | 6.21 | 6.17 | 6.15 | 6.13 | 6.1 | 6.06 | 6.03 | 5.77 | 5.53 | 5.2 | 4.8 | 4.29 | 3.08 | 1.89 | 0.28 | -1.79 | -3.97 | -6.42
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | System Transformation | Headroom (MW) | Thermal | 6.21 | 6.14 | 6.08 | 5.87 | 5.72 | 5.61 | 5.49 | 4.47 | 3.15 | 1.73 | -0.02 | -2.06 | -4.26 | -6.24 | -8.73 | -12.83 | -18.5 | -25.08
West Burton 132kV | Lincoln 33 | SOUTH CARLTON 33 11kV S STN | Primary | 11 | -0.576 | 53.2728 | WPD Best View | Headroom (MW) | Thermal | 6.21 | 6.17 | 6.15 | 6.13 | 6.08 | 6.03 | 5.99 | 5.62 | 5.22 | 4.72 | 4.08 | 3.3 | 1.92 | 0.59 | -1.16 | -3.59 | -6.66 | -9.74
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Consumer Transformation | Headroom (MW) | Thermal | 13.64 | 13.48 | 13.3 | 13.08 | 12.64 | 12.26 | 10.22 | 6.33 | 3.35 | 0.49 | -2.71 | -5.87 | -9.03 | -12.3 | -16.02 | -31.25 | -51.4 | -72.82
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Leading the Way | Headroom (MW) | Thermal | 13.64 | 13.67 | 13.51 | 13.3 | 12.88 | 12.53 | 10.34 | 8.55 | 7.21 | 5.22 | 3.41 | 1.71 | -0.76 | -3.37 | -6.22 | -19.33 | -36.68 | -53.72
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | Steady Progression | Headroom (MW) | N/A | 13.64 | 13.56 | 13.51 | 13.47 | 13.42 | 13.36 | 13.3 | 13.15 | 12.74 | 10.94 | 10.46 | 9.89 | 8.9 | 8.14 | 7.29 | 6.22 | 4.51 | 2.39
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | System Transformation | Headroom (MW) | Thermal | 13.64 | 13.52 | 13.43 | 13.33 | 13.17 | 13.02 | 12.86 | 12.38 | 10.41 | 9.19 | 7.68 | 6.16 | 4.66 | 3.43 | 1.97 | -1.77 | -8.11 | -15.24
West Burton 132kV | Lincoln 33 | WADDINGTON 33 11kV S STN | Primary | 11 | -0.5358 | 53.1752 | WPD Best View | Headroom (MW) | N/A | 13.64 | 13.56 | 13.51 | 13.47 | 13.42 | 13.36 | 13.3 | 13.15 | 12.74 | 10.94 | 10.46 | 9.88 | 8.89 | 8.13 | 7.29 | 6.22 | 4.51 | 2.39
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Consumer Transformation | Headroom (MW) | Thermal | 2.02 | 1.96 | 1.91 | 1.85 | 1.71 | 1.6 | 1.49 | 0.67 | -0.31 | -1.46 | -2.93 | -4.65 | -6.52 | -8.23 | -10.36 | -14.49 | -18.73 | -23.97
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Leading the Way | Headroom (MW) | Thermal | 2.02 | 1.96 | 1.9 | 1.85 | 1.69 | 1.57 | 1.45 | 1.34 | 1.24 | 1.14 | 1.04 | 0.95 | -0.46 | -1.79 | -3.2 | -8.58 | -14.03 | -15.98
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | Steady Progression | Headroom (MW) | Thermal | 2.02 | 1.98 | 1.96 | 1.95 | 1.92 | 1.9 | 1.87 | 1.67 | 1.46 | 1.2 | 0.86 | 0.43 | -0.59 | -1.61 | -2.98 | -4.75 | -6.53 | -8.45
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | System Transformation | Headroom (MW) | Thermal | 2.02 | 1.97 | 1.94 | 1.91 | 1.84 | 1.79 | 1.73 | 0.97 | -0.01 | -1.11 | -2.54 | -4.21 | -6.02 | -7.66 | -9.73 | -13.37 | -17.14 | -21.84
West Burton 132kV | Lincoln 33 | WRAGBY 33 11kV S STN | Primary | 11 | -0.3076 | 53.2867 | WPD Best View | Headroom (MW) | Thermal | 2.02 | 1.98 | 1.95 | 1.93 | 1.88 | 1.84 | 1.8 | 1.27 | 0.63 | -0.12 | -1.12 | -2.3 | -3.8 | -5.19 | -6.98 | -10.17 | -13.16 | -16.79
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Consumer Transformation | Headroom (MW) | N/A | 47.59 | 47.35 | 47.22 | 47.07 | 46.71 | 46.3 | 45.51 | 44.78 | 44.08 | 43.43 | 42.75 | 42.08 | 41.4 | 40.69 | 39.94 | 34.01 | 27.19 | 19.47
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Leading the Way | Headroom (MW) | N/A | 47.59 | 47.32 | 47.18 | 47.02 | 46.52 | 45.97 | 45.07 | 44.22 | 43.4 | 42.63 | 41.81 | 40.99 | 40.14 | 39.24 | 38.26 | 31.72 | 23.92 | 14.18
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | Steady Progression | Headroom (MW) | N/A | 30.8946 | 30.8598 | 30.8431 | 30.8255 | 30.8026 | 30.7528 | 30.6978 | 30.6414 | 30.589 | 30.5238 | 30.4573 | 30.3917 | 30.3256 | 30.2591 | 30.1944 | 29.8636 | 29.5047 | 29.1409
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | System Transformation | Headroom (MW) | N/A | 40.9176 | 40.843 | 40.7811 | 40.7059 | 40.542 | 40.3378 | 40.1016 | 39.8807 | 39.665 | 39.447 | 39.2081 | 38.9627 | 38.7137 | 38.4613 | 38.2105 | 36.856 | 35.5325 | 34.1985
Willington 132kV | Derby 132 11 (No. 1 Switchboard) | DERBY 11kV S STN | Primary | 11 | -1.4762 | 52.9261 | WPD Best View | Headroom (MW) | N/A | 42.2106 | 42.0891 | 41.9639 | 41.7966 | 41.3184 | 40.8274 | 40.3384 | 39.8736 | 39.4178 | 38.9596 | 38.4577 | 37.9478 | 37.4336 | 36.9153 | 36.4014 | 33.5826 | 27.19 | 19.47
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Consumer Transformation | Headroom (MW) | Thermal | 12.93 | 12.78 | 12.61 | 12.33 | 11.78 | 11.31 | 10.87 | 10.44 | 10.05 | 9.75 | 9.49 | 9.2 | 8.9 | 8.57 | 8.18 | 2.69 | -1.93 | -7.11
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Leading the Way | Headroom (MW) | Thermal | 12.93 | 12.77 | 12.58 | 12.29 | 11.69 | 11.19 | 10.72 | 10.27 | 9.85 | 9.57 | 9.28 | 8.93 | 8.54 | 8.1 | 7.54 | 1.78 | -3.58 | -10.69
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | Steady Progression | Headroom (MW) | N/A | 12.93 | 12.82 | 12.76 | 12.7 | 12.63 | 12.57 | 12.51 | 12.42 | 12.33 | 12.28 | 12.25 | 12.22 | 12.22 | 12.23 | 12.23 | 12.15 | 10.4 | 9.35
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | System Transformation | Headroom (MW) | N/A | 12.93 | 12.8 | 12.71 | 12.6 | 12.37 | 12.15 | 11.91 | 11.69 | 11.48 | 11.36 | 11.28 | 11.18 | 11.09 | 11.03 | 10.95 | 8.96 | 6.77 | 4.59
Willington 132kV | Derby 33 | CHADDESDEN 33 11kV S STN | Primary | 11 | -1.4409 | 52.925 | WPD Best View | Headroom (MW) | Thermal | 12.93 | 12.78 | 12.61 | 12.33 | 11.78 | 11.31 | 10.87 | 10.44 | 10.05 | 9.75 | 9.49 | 9.2 | 8.9 | 8.57 | 8.18 | 2.69 | -1.93 | -7.11
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Consumer Transformation | Headroom (MW) | Thermal | 16.27 | 16.13 | 15.99 | 15.72 | 15.18 | 14.7 | 14.23 | 13.78 | 13.35 | 12.96 | 12.58 | 12.21 | 11.82 | 11.42 | 10.98 | 7.23 | 2.84 | -2.04
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Leading the Way | Headroom (MW) | Thermal | 16.27 | 16.12 | 15.96 | 15.67 | 15.11 | 14.57 | 14.04 | 13.53 | 13.05 | 12.57 | 12.11 | 11.64 | 11.13 | 10.58 | 9.96 | 5.77 | 0.69 | -5.76
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | Steady Progression | Headroom (MW) | N/A | 16.27 | 16.17 | 16.11 | 16.05 | 15.98 | 15.93 | 15.87 | 15.81 | 15.75 | 15.68 | 15.6 | 15.54 | 15.47 | 15.39 | 15.31 | 15.01 | 14.3 | 13.33
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | System Transformation | Headroom (MW) | N/A | 16.27 | 16.15 | 16.06 | 15.98 | 15.76 | 15.53 | 15.26 | 15.02 | 14.79 | 14.57 | 14.38 | 14.21 | 14.05 | 13.91 | 13.77 | 12.72 | 10.67 | 8.65
Willington 132kV | Derby 33 | DARLEY ABBEY 33 11kV S STN | Primary | 11 | -1.4857 | 52.9441 | WPD Best View | Headroom (MW) | Thermal | 16.27 | 16.13 | 15.99 | 15.72 | 15.18 | 14.7 | 14.23 | 13.78 | 13.35 | 12.96 | 12.58 | 12.21 | 11.82 | 11.42 | 10.98 | 7.23 | 2.84 | -2.04
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Consumer Transformation | Headroom (MW) | N/A | 14.32 | 14.26 | 14.23 | 14.2 | 14.14 | 14 | 13.87 | 13.76 | 13.65 | 13.54 | 13.44 | 13.33 | 13.23 | 13.12 | 13.01 | 12.27 | 11.31 | 10.3
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Leading the Way | Headroom (MW) | N/A | 14.32 | 14.26 | 14.22 | 14.19 | 14.11 | 13.97 | 13.84 | 13.73 | 13.61 | 13.5 | 13.39 | 13.28 | 13.17 | 13.05 | 12.92 | 12.09 | 11.04 | 9.76
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | Steady Progression | Headroom (MW) | N/A | 14.32 | 14.27 | 14.24 | 14.21 | 14.18 | 14.15 | 14.13 | 14.1 | 14.07 | 14.05 | 14.02 | 13.99 | 13.96 | 13.93 | 13.91 | 13.77 | 13.62 | 13.46
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | System Transformation | Headroom (MW) | N/A | 14.32 | 14.26 | 14.23 | 14.2 | 14.16 | 14.13 | 14.1 | 14.03 | 13.96 | 13.9 | 13.84 | 13.78 | 13.72 | 13.67 | 13.63 | 13.38 | 12.89 | 12.36
Willington 132kV | Derby 33 | EAGLE CENTRE 33 11kV S STN | Primary | 11 | -1.4715 | 52.9198 | WPD Best View | Headroom (MW) | N/A | 14.32 | 14.26 | 14.23 | 14.2 | 14.14 | 14 | 13.87 | 13.76 | 13.65 | 13.54 | 13.44 | 13.33 | 13.23 | 13.12 | 13.01 | 12.27 | 11.31 | 10.3
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Consumer Transformation | Headroom (MW) | Thermal | 14.16 | 13.86 | 13.58 | 13.23 | 12.61 | 12.01 | 11.45 | 10.65 | 9.8 | 8.97 | 7.98 | 6.83 | 5.59 | 4.39 | 2.99 | -2.06 | -8.87 | -16.72
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Leading the Way | Headroom (MW) | Thermal | 14.16 | 13.84 | 13.55 | 13.17 | 12.54 | 11.91 | 11.32 | 10.8 | 10.29 | 9.87 | 9.38 | 8.88 | 7.78 | 6.63 | 5.37 | -0.76 | -8.82 | -17.39
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | Steady Progression | Headroom (MW) | N/A | 14.16 | 14.02 | 13.95 | 13.88 | 13.89 | 13.8 | 13.69 | 13.51 | 13.35 | 13.17 | 12.97 | 12.73 | 12.28 | 11.84 | 11.27 | 10.64 | 9.28 | 7.31
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | System Transformation | Headroom (MW) | Thermal | 14.16 | 13.95 | 13.78 | 13.6 | 13.43 | 13.17 | 12.87 | 12.32 | 11.71 | 11.09 | 10.32 | 9.44 | 8.53 | 7.72 | 6.68 | 4.42 | 0.37 | -4.02
Willington 132kV | Derby 33 | MACKWORTH 33 11kV S STN | Primary | 11 | -1.5199 | 52.9211 | WPD Best View | Headroom (MW) | Thermal | 14.16 | 13.86 | 13.58 | 13.23 | 12.61 | 12.01 | 11.45 | 10.65 | 9.8 | 8.97 | 7.98 | 6.83 | 5.59 | 4.39 | 2.99 | -2.06 | -8.87 | -16.72
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Consumer Transformation | Headroom (MW) | N/A | 31.42 | 31.22 | 31.09 | 30.95 | 30.26 | 29.66 | 29.08 | 28.55 | 28.05 | 27.58 | 27.12 | 26.67 | 26.21 | 25.71 | 25.18 | 21.46 | 16.14 | 10.2
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Leading the Way | Headroom (MW) | N/A | 31.42 | 31.2 | 31.06 | 30.9 | 30.12 | 29.49 | 28.89 | 28.35 | 27.83 | 27.34 | 26.82 | 26.29 | 25.74 | 25.12 | 24.43 | 19.94 | 13.87 | 5.76
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | Steady Progression | Headroom (MW) | N/A | 31.42 | 31.27 | 31.19 | 31.11 | 31 | 30.93 | 30.85 | 30.77 | 30.7 | 30.61 | 30.53 | 30.44 | 30.35 | 30.27 | 30.18 | 29.78 | 29.23 | 28.19
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | System Transformation | Headroom (MW) | N/A | 31.42 | 31.24 | 31.14 | 31.04 | 30.87 | 30.7 | 30.38 | 30.09 | 29.82 | 29.57 | 29.33 | 29.11 | 28.91 | 28.73 | 28.55 | 27.49 | 24.92 | 22.33
Willington 132kV | Derby South | ALLENTON 33 11kV S STN | Primary | 11 | -1.4531 | 52.8939 | WPD Best View | Headroom (MW) | N/A | 31.42 | 31.22 | 31.09 | 30.95 | 30.26 | 29.66 | 29.08 | 28.55 | 28.05 | 27.58 | 27.12 | 26.67 | 26.21 | 25.71 | 25.18 | 21.46 | 16.14 | 10.2
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Consumer Transformation | Headroom (MW) | Thermal | 25.45 | 25.27 | 25.15 | 24.83 | 24.09 | 23.23 | 22.35 | 21.49 | 20.66 | 19.87 | 18.97 | 18.1 | 17.24 | 16.33 | 15.37 | 8.57 | -0.53 | -10.95
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Leading the Way | Headroom (MW) | Thermal | 25.45 | 25.25 | 25.13 | 24.77 | 23.98 | 22.92 | 21.83 | 20.76 | 19.73 | 18.73 | 17.58 | 16.47 | 15.33 | 14.13 | 12.85 | 4.64 | -5.8 | -19.25
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | Steady Progression | Headroom (MW) | N/A | 25.45 | 25.32 | 25.26 | 25.19 | 25.11 | 25.06 | 24.99 | 24.91 | 24.83 | 24.75 | 24.67 | 24.58 | 24.49 | 24.4 | 24.31 | 23.88 | 23.13 | 21.69
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | System Transformation | Headroom (MW) | N/A | 25.45 | 25.29 | 25.21 | 25.11 | 24.9 | 24.64 | 24.31 | 23.87 | 23.35 | 23.04 | 22.69 | 22.37 | 22.08 | 21.82 | 21.56 | 19.87 | 15.28 | 10.43
Willington 132kV | Derby South | NORMANTON 33 11kV S STN | Primary | 11 | -1.4924 | 52.8992 | WPD Best View | Headroom (MW) | Thermal | 25.45 | 25.27 | 25.15 | 24.83 | 24.09 | 23.23 | 22.35 | 21.49 | 20.66 | 19.87 | 18.97 | 18.1 | 17.24 | 16.33 | 15.37 | 8.57 | -0.53 | -10.95
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Consumer Transformation | Headroom (MW) | Thermal | 11.15 | 11.06 | 10.99 | 10.84 | 10.63 | 10.35 | 10.1 | 9.87 | 9.7 | 9.55 | 9.31 | 9.04 | 8.71 | 8.38 | 8 | 6.15 | 2.97 | -0.71
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Leading the Way | Headroom (MW) | Thermal | 11.15 | 11.05 | 10.97 | 10.8 | 10.58 | 10.28 | 10.01 | 9.81 | 9.7 | 9.6 | 9.52 | 9.44 | 9.14 | 8.81 | 8.45 | 6.19 | 2.41 | -1.79
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | Steady Progression | Headroom (MW) | N/A | 11.15 | 11.08 | 11.05 | 11.01 | 11.05 | 11.02 | 11 | 10.99 | 11.01 | 11.04 | 11.03 | 11.03 | 10.97 | 10.92 | 10.83 | 10.93 | 10.44 | 9.51
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | System Transformation | Headroom (MW) | N/A | 11.15 | 11.07 | 11.02 | 10.98 | 10.98 | 10.85 | 10.71 | 10.6 | 10.53 | 10.49 | 10.34 | 10.18 | 9.97 | 9.8 | 9.6 | 9.14 | 7.33 | 5.3
Willington 132kV | Derby South | SINFIN LANE 33 11kV S STN | Primary | 11 | -1.4745 | 52.8877 | WPD Best View | Headroom (MW) | Thermal | 11.15 | 11.06 | 10.99 | 10.84 | 10.63 | 10.35 | 10.1 | 9.87 | 9.7 | 9.55 | 9.31 | 9.04 | 8.71 | 8.38 | 8 | 6.15 | 2.97 | -0.71
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Consumer Transformation | Headroom (MW) | N/A | 14.12 | 14.01 | 13.92 | 13.49 | 13.24 | 13.08 | 12.94 | 12.62 | 12.27 | 11.94 | 11.51 | 11.02 | 10.46 | 9.94 | 9.32 | 7.39 | 4.87 | 1.93
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Leading the Way | Headroom (MW) | N/A | 14.12 | 14 | 13.9 | 13.47 | 13.19 | 13.04 | 12.92 | 12.73 | 12.54 | 12.44 | 12.28 | 12.1 | 11.64 | 11.17 | 10.67 | 8.41 | 5.36 | 2.54
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | Steady Progression | Headroom (MW) | N/A | 14.12 | 14.06 | 14.02 | 13.99 | 13.95 | 13.94 | 13.94 | 13.87 | 13.81 | 13.77 | 13.7 | 13.6 | 13.38 | 13.16 | 12.88 | 12.57 | 11.97 | 11.14
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | System Transformation | Headroom (MW) | N/A | 14.12 | 14.04 | 13.98 | 13.91 | 13.8 | 13.75 | 13.7 | 13.47 | 13.2 | 12.96 | 12.62 | 12.21 | 11.77 | 11.38 | 10.91 | 9.96 | 8.33 | 6.51
Willington 132kV | Heanor | DENBY 33 11kV S STN | Primary | 11 | -1.4299 | 53.0157 | WPD Best View | Headroom (MW) | N/A | 14.12 | 14.01 | 13.92 | 13.49 | 13.24 | 13.08 | 12.94 | 12.62 | 12.27 | 11.94 | 11.51 | 11.02 | 10.46 | 9.94 | 9.32 | 7.39 | 4.87 | 1.93
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Consumer Transformation | Headroom (MW) | Thermal | 10.75 | 10.52 | 10.32 | 10.08 | 9.48 | 9.01 | 8.06 | 7.17 | 6.36 | 5.73 | 5.2 | 4.8 | 4.43 | 4.01 | 3.57 | 0.33 | -3.39 | -7.74
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Leading the Way | Headroom (MW) | Thermal | 10.75 | 10.5 | 10.29 | 10.03 | 9.36 | 8.87 | 8.26 | 7.69 | 7.12 | 6.74 | 6.29 | 5.87 | 5.43 | 4.91 | 4.32 | 0.39 | 3.04 | -14.86
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | Steady Progression | Headroom (MW) | N/A | 10.75 | 10.63 | 10.56 | 10.5 | 10.42 | 10.34 | 9.52 | 8.7 | 7.92 | 7.18 | 6.53 | 6 | 5.72 | 5.52 | 5.41 | 5.3 | 4.64 | 3.69
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | System Transformation | Headroom (MW) | N/A | 10.75 | 10.58 | 10.45 | 10.32 | 10.07 | 9.87 | 9.12 | 8.44 | 7.83 | 7.38 | 7.05 | 6.85 | 6.72 | 6.61 | 6.5 | 5.48 | 11.19 | 1.78
Willington 132kV | Heanor | HEANOR 11kV S STN | Primary | 11 | -1.3625 | 53.0211 | WPD Best View | Headroom (MW) | Thermal | 10.75 | 10.52 | 10.32 | 10.08 | 9.48 | 9.01 | 8.06 | 7.17 | 6.36 | 5.73 | 5.2 | 4.8 | 4.43 | 4.01 | 3.57 | 0.33 | -3.39 | -7.74
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Consumer Transformation | Headroom (MW) | Thermal | 13.17 | 13.06 | 12.98 | 12.88 | 12.44 | 12.05 | 11.68 | 11.32 | 10.98 | 10.66 | 10.36 | 10.07 | 9.77 | 9.44 | 9.1 | 4.1 | 0.58 | -3.33
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Leading the Way | Headroom (MW) | Thermal | 13.17 | 13.05 | 12.95 | 12.85 | 12.37 | 11.96 | 11.56 | 11.2 | 10.84 | 10.5 | 10.16 | 9.8 | 9.43 | 9.02 | 8.56 | 3.07 | -0.98 | -6.3
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | Steady Progression | Headroom (MW) | N/A | 13.17 | 13.09 | 13.04 | 13 | 12.94 | 12.89 | 12.85 | 12.8 | 12.75 | 12.71 | 12.66 | 12.61 | 12.56 | 12.5 | 12.45 | 12.23 | 11.89 | 11.12
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | System Transformation | Headroom (MW) | N/A | 13.17 | 13.07 | 13.01 | 12.94 | 12.85 | 12.75 | 12.55 | 12.36 | 12.18 | 12.02 | 11.87 | 11.74 | 11.62 | 11.52 | 11.43 | 9.51 | 7.81 | 6.16
Willington 132kV | Heanor | MOORGREEN 33 11kV S STN | Primary | 11 | -1.2954 | 53.0231 | WPD Best View | Headroom (MW) | Thermal | 13.17 | 13.06 | 12.98 | 12.88 | 12.44 | 12.05 | 11.68 | 11.32 | 10.98 | 10.66 | 10.36 | 10.07 | 9.77 | 9.44 | 9.1 | 4.1 | 0.58 | -3.33
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Consumer Transformation | Headroom (MW) | Thermal | 7.09 | 7.01 | 6.94 | 6.86 | 6.68 | 6.53 | 6.39 | 5.98 | 5.52 | 5 | 4.34 | 3.56 | 2.72 | 1.95 | 1.01 | -1.16 | -3.7 | -6.74
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Leading the Way | Headroom (MW) | Thermal | 7.09 | 7 | 6.93 | 6.85 | 6.64 | 6.48 | 6.33 | 6.18 | 6.04 | 5.91 | 5.77 | 5.63 | 4.98 | 4.33 | 3.64 | 1.21 | -1.95 | -3.94
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | Steady Progression | Headroom (MW) | N/A | 7.09 | 7.04 | 7.02 | 6.99 | 6.96 | 6.93 | 6.9 | 6.81 | 6.72 | 6.6 | 6.45 | 6.26 | 5.84 | 5.43 | 4.88 | 4.16 | 3.29 | 2.31
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | System Transformation | Headroom (MW) | Thermal | 7.09 | 7.03 | 6.99 | 6.94 | 6.86 | 6.79 | 6.71 | 6.38 | 5.96 | 5.49 | 4.89 | 4.19 | 3.43 | 2.75 | 1.88 | 0.46 | -1.47 | -3.76
Willington 132kV | Heanor | MORLEY 33 11kV S STN | Primary | 11 | -1.4137 | 52.9685 | WPD Best View | Headroom (MW) | Thermal | 7.09 | 7.01 | 6.94 | 6.86 | 6.68 | 6.53 | 6.39 | 5.98 | 5.52 | 5 | 4.34 | 3.56 | 2.72 | 1.95 | 1.01 | -1.16 | -3.7 | -6.74
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Consumer Transformation | Headroom (MW) | Thermal | 9.2 | 9.08 | 9 | 8.91 | 8.74 | 8.45 | 7.72 | 6.88 | 6.05 | 5.3 | 4.52 | 3.77 | 3.03 | 2.31 | 1.47 | -1.74 | -5.46 | -9.87
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Leading the Way | Headroom (MW) | Thermal | 9.2 | 9.07 | 8.98 | 8.88 | 8.66 | 8.35 | 7.86 | 7.4 | 6.96 | 6.64 | 6.27 | 5.93 | 5.24 | 4.54 | 3.78 | 0.07 | 0.47 | -12.42
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | Steady Progression | Headroom (MW) | N/A | 7.3265 | 7.3206 | 7.3135 | 7.3088 | 7.3038 | 7.2879 | 6.647 | 5.993 | 5.3583 | 4.7588 | 4.2082 | 3.7363 | 3.4147 | 3.1489 | 2.9157 | 2.6088 | 2.2804 | 1.9486
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | System Transformation | Headroom (MW) | Thermal | 9.2 | 9.09 | 9.03 | 8.96 | 8.85 | 8.79 | 8.37 | 7.87 | 7.19 | 6.59 | 5.96 | 5.38 | 4.8 | 4.29 | 3.68 | 2.28 | 5.17 | -2.73
Willington 132kV | Heanor | RIPLEY 33 11kV S STN | Primary | 11 | -1.4065 | 53.0575 | WPD Best View | Headroom (MW) | Thermal | 9.2 | 9.08 | 9 | 8.91 | 8.74 | 8.45 | 7.72 | 6.88 | 6.05 | 5.3 | 4.52 | 3.77 | 3.03 | 2.31 | 1.47 | -1.74 | -5.46 | -9.87
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Consumer Transformation | Headroom (MW) | N/A | 12.5 | 12.43 | 12.38 | 12.3 | 12.1 | 11.94 | 11.78 | 11.63 | 11.5 | 11.37 | 11.24 | 11.1 | 10.96 | 10.81 | 10.66 | 9.5 | 8.03 | 6.39
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Leading the Way | Headroom (MW) | N/A | 12.5 | 12.43 | 12.37 | 12.28 | 12.04 | 11.86 | 11.7 | 11.55 | 11.41 | 11.27 | 11.12 | 10.96 | 10.79 | 10.61 | 10.42 | 9.05 | 7.36 | 5.1
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | Steady Progression | Headroom (MW) | N/A | 12.5 | 12.47 | 12.47 | 12.46 | 12.45 | 12.44 | 12.43 | 12.4 | 12.38 | 12.36 | 12.33 | 12.32 | 12.31 | 12.3 | 12.3 | 12.22 | 12.01 | 11.7
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | System Transformation | Headroom (MW) | N/A | 12.5 | 12.46 | 12.43 | 12.4 | 12.32 | 12.25 | 12.17 | 12.1 | 12.03 | 11.97 | 11.91 | 11.86 | 11.81 | 11.76 | 11.71 | 11.34 | 10.65 | 9.99
Willington 132kV | Heanor | WATNALL 33 11KV S STN | Primary | 11 | -1.2505 | 53.008 | WPD Best View | Headroom (MW) | N/A | 12.5 | 12.43 | 12.38 | 12.3 | 12.09 | 11.93 | 11.77 | 11.63 | 11.49 | 11.36 | 11.23 | 11.09 | 10.95 | 10.8 | 10.65 | 9.5 | 8.03 | 6.39
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Consumer Transformation | Headroom (MW) | N/A | 14.66 | 14.5 | 14.37 | 14.21 | 13.86 | 13.58 | 13.3 | 13 | 12.72 | 12.44 | 12.05 | 11.64 | 11.19 | 10.72 | 10.19 | 7.78 | 4.51 | 0.77
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Leading the Way | Headroom (MW) | Thermal | 14.66 | 14.49 | 14.36 | 14.19 | 13.8 | 13.49 | 13.19 | 12.9 | 12.63 | 12.37 | 12.12 | 11.86 | 11.43 | 10.97 | 10.45 | 7.59 | 3.71 | -0.49
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | Steady Progression | Headroom (MW) | N/A | 14.66 | 14.57 | 14.52 | 14.48 | 14.43 | 14.38 | 14.32 | 14.26 | 14.2 | 14.14 | 14.05 | 13.96 | 13.8 | 13.65 | 13.46 | 13.24 | 12.65 | 11.75
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | System Transformation | Headroom (MW) | N/A | 14.66 | 14.54 | 14.45 | 14.37 | 14.22 | 14.08 | 13.94 | 13.77 | 13.59 | 13.43 | 13.15 | 12.85 | 12.54 | 12.28 | 11.94 | 11.02 | 9.13 | 7.08
Willington 132kV | Heanor | WESTWOOD 33 11kV S STN | Primary | 11 | -1.315 | 53.0564 | WPD Best View | Headroom (MW) | N/A | 14.66 | 14.5 | 14.37 | 14.21 | 13.86 | 13.58 | 13.3 | 13 | 12.72 | 12.44 | 12.05 | 11.64 | 11.19 | 10.72 | 10.19 | 7.78 | 4.51 | 0.77
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Consumer Transformation | Headroom (MW) | Thermal | 15.65 | 15.51 | 15.4 | 15.27 | 14.64 | 14.1 | 13.58 | 12.96 | 12.61 | 12.14 | 11.48 | 10.77 | 9.97 | 9.19 | 8.29 | 4.38 | -1.17 | -7.53
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Leading the Way | Headroom (MW) | Thermal | 15.65 | 15.49 | 15.37 | 15.23 | 14.54 | 13.97 | 13.44 | 12.95 | 12.92 | 12.72 | 12.29 | 11.86 | 11.12 | 10.34 | 9.45 | 4.59 | -1.99 | -9.55
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | Steady Progression | Headroom (MW) | N/A | 15.65 | 15.55 | 15.5 | 15.44 | 15.37 | 15.32 | 15.27 | 15.21 | 15.27 | 15.29 | 15.26 | 15.23 | 15.19 | 15 | 14.76 | 14.53 | 13.48 | 12.05
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | System Transformation | Headroom (MW) | N/A | 15.65 | 15.53 | 15.45 | 15.36 | 15.24 | 15.11 | 14.85 | 14.46 | 14.32 | 14.07 | 13.63 | 13.16 | 12.67 | 12.24 | 11.71 | 10.32 | 7.25 | 3.97
Willington 132kV | Spondon | BELPER 33 11kV S STN | Primary | 11 | -1.4767 | 53.0154 | WPD Best View | Headroom (MW) | Thermal | 15.65 | 15.51 | 15.4 | 15.27 | 14.64 | 14.1 | 13.58 | 12.96 | 12.61 | 12.14 | 11.48 | 10.77 | 9.97 | 9.19 | 8.29 | 4.38 | -1.17 | -7.53
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Consumer Transformation | Headroom (MW) | N/A | 9.02 | 8.92 | 8.85 | 11.11 | 11.02 | 10.96 | 10.9 | 10.67 | 10.46 | 10.16 | 9.59 | 8.98 | 8.33 | 7.72 | 6.99 | 5.44 | 3.16 | 0.48
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Leading the Way | Headroom (MW) | N/A | 9.02 | 8.92 | 8.84 | 11.77 | 11.64 | 11.57 | 11.34 | 11.1 | 10.96 | 10.74 | 10.49 | 10.28 | 9.73 | 9.2 | 10.7 | 6.64 | 4 | 1.9
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | Steady Progression | Headroom (MW) | N/A | 9.02 | 8.95 | 8.91 | 10.89 | 10.99 | 11.09 | 11.18 | 11.22 | 11.3 | 11.33 | 11.33 | 11.31 | 10.99 | 10.67 | 10.26 | 9.63 | 10.88 | 9.93
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | System Transformation | Headroom (MW) | N/A | 9.02 | 8.94 | 8.88 | 11.18 | 11.21 | 11.25 | 11.28 | 11.12 | 10.99 | 10.76 | 10.28 | 9.74 | 9.18 | 8.66 | 8.04 | 7.91 | 6.25 | 4.3
Willington 132kV | Spondon | CASTLE DONINGTON 33 11kV S STN | Primary | 11 | -1.3617 | 52.841 | WPD Best View | Headroom (MW) | N/A | 9.02 | 8.92 | 8.85 | 11.11 | 11.02 | 10.96 | 10.9 | 10.67 | 10.46 | 10.16 | 9.59 | 8.98 | 8.33 | 7.72 | 6.99 | 5.44 | 3.16 | 0.48
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Consumer Transformation | Headroom (MW) | N/A | 15.06 | 14.97 | 14.88 | 14.79 | 14.58 | 14.42 | 14.26 | 14.08 | 13.9 | 13.72 | 13.43 | 13.11 | 12.77 | 12.45 | 12.07 | 10.79 | 9.03 | 6.98
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Leading the Way | Headroom (MW) | N/A | 15.06 | 14.96 | 14.87 | 14.77 | 14.55 | 14.38 | 14.22 | 14.06 | 13.9 | 13.76 | 13.6 | 13.44 | 13.13 | 12.82 | 12.5 | 11.02 | 8.96 | 7.01
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | Steady Progression | Headroom (MW) | N/A | 15.06 | 14.99 | 14.95 | 14.9 | 14.86 | 14.8 | 14.75 | 14.7 | 14.65 | 14.59 | 14.51 | 14.42 | 14.27 | 14.13 | 13.95 | 13.66 | 13.18 | 12.57
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | System Transformation | Headroom (MW) | N/A | 15.06 | 14.98 | 14.92 | 14.85 | 14.75 | 14.67 | 14.57 | 14.46 | 14.34 | 14.22 | 13.99 | 13.74 | 13.47 | 13.24 | 12.95 | 12.29 | 11.15 | 9.87
Willington 132kV | Spondon | MELBOURNE 33 11kV S STN | Primary | 11 | -1.4337 | 52.8092 | WPD Best View | Headroom (MW) | N/A | 15.06 | 14.97 | 14.88 | 14.79 | 14.58 | 14.42 | 14.26 | 14.08 | 13.9 | 13.72 | 13.43 | 13.11 | 12.77 | 12.45 | 12.07 | 10.79 | 9.03 | 6.98
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Consumer Transformation | Headroom (MW) | Thermal | 7.02 | 7.08 | 7.17 | 7.34 | 7.71 | 7.29 | 6.84 | 6.22 | 5.56 | 4.84 | 3.9 | 2.85 | 1.76 | 0.69 | -0.38 | -5.13 | -10.81 | -17.56
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Leading the Way | Headroom (MW) | Thermal | 7.02 | 7.09 | 7.2 | 7.4 | 7.9 | 7.23 | 6.53 | 5.76 | 4.97 | 4.14 | 3.22 | 2.28 | 1.05 | -0.17 | -1.27 | -6.69 | -13.17 | -20.01
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | Steady Progression | Headroom (MW) | N/A | 7.02 | 7.07 | 7.15 | 7.32 | 7.81 | 7.81 | 7.81 | 7.77 | 7.72 | 7.66 | 7.57 | 7.45 | 7.2 | 6.91 | 6.55 | 5.85 | 5.16 | 4.42
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | System Transformation | Headroom (MW) | Thermal | 7.02 | 7.08 | 7.18 | 7.37 | 7.85 | 7.82 | 7.77 | 7.4 | 6.86 | 6.52 | 6.02 | 5.43 | 4.79 | 4.18 | 3.55 | 1.94 | -1.47 | -5.53
Willington 132kV | Spondon | RATCLIFFE ON SOAR 33 11kV S STN | Primary | 11 | -1.2615 | 52.8613 | WPD Best View | Headroom (MW) | Thermal | 7.02 | 7.08 | 7.17 | 7.34 | 7.71 | 7.29 | 6.84 | 6.22 | 5.56 | 4.84 | 3.9 | 2.85 | 1.76 | 0.69 | -0.38 | -5.13 | -10.81 | -17.56
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Consumer Transformation | Headroom (MW) | Thermal | 26.27 | 26.09 | 25.93 | 25.66 | 24.75 | 23.94 | 23.16 | 21.98 | 20.74 | 19.39 | 17.81 | 16.06 | 14.09 | 12.22 | 10.01 | 2.36 | -7.37 | -18.54
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Leading the Way | Headroom (MW) | Thermal | 26.27 | 26.07 | 25.89 | 25.59 | 24.62 | 23.79 | 22.96 | 22.18 | 21.45 | 20.68 | 19.89 | 19.08 | 17.37 | 15.66 | 13.74 | 4.75 | -6.84 | -18.51
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | Steady Progression | Headroom (MW) | N/A | 26.27 | 26.15 | 26.06 | 26.05 | 26.03 | 26 | 25.96 | 25.91 | 25.78 | 25.51 | 25.19 | 24.83 | 24.1 | 23.39 | 22.46 | 21.35 | 19.27 | 16.33
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | System Transformation | Headroom (MW) | Thermal | 26.27 | 26.12 | 26 | 25.96 | 25.82 | 25.48 | 25.09 | 24.29 | 23.39 | 22.38 | 21.16 | 19.76 | 18.28 | 16.97 | 15.31 | 11.7 | 5.76 | -0.72
Willington 132kV | Spondon | SPONDON 11kV S STN | Primary | 11 | -1.3985 | 52.9065 | WPD Best View | Headroom (MW) | Thermal | 26.27 | 26.09 | 25.93 | 25.66 | 24.75 | 23.94 | 23.16 | 21.98 | 20.74 | 19.39 | 17.81 | 16.06 | 14.09 | 12.22 | 10.01 | 2.36 | -7.37 | -18.54
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Consumer Transformation | Headroom (MW) | N/A | 14.37 | 14.56 | 14.37 | 14.32 | 14.2 | 14.1 | 14 | 13.89 | 13.79 | 13.69 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 12.57 | 11.82 | 11.03
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Leading the Way | Headroom (MW) | N/A | 14.37 | 14.59 | 14.4 | 14.35 | 14.2 | 14.08 | 13.97 | 13.86 | 13.76 | 13.66 | 13.56 | 13.45 | 13.34 | 13.23 | 13.11 | 12.41 | 11.59 | 10.58
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | Steady Progression | Headroom (MW) | N/A | 14.37 | 14.54 | 14.52 | 14.49 | 14.46 | 14.44 | 14.41 | 14.38 | 14.34 | 14.29 | 14.25 | 14.21 | 14.17 | 14.13 | 14.09 | 13.95 | 13.75 | 13.49
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | System Transformation | Headroom (MW) | N/A | 14.37 | 14.57 | 14.54 | 14.35 | 14.29 | 14.24 | 14.17 | 14.1 | 14.04 | 13.97 | 13.91 | 13.85 | 13.79 | 13.73 | 13.68 | 13.4 | 12.97 | 12.56
Willington 132kV | Spondon | TRENT LANE 33 11kV S STN | Primary | 11 | -1.3453 | 52.8503 | WPD Best View | Headroom (MW) | N/A | 14.37 | 14.56 | 14.37 | 14.32 | 14.2 | 14.1 | 14 | 13.89 | 13.79 | 13.69 | 13.6 | 13.5 | 13.4 | 13.3 | 13.2 | 12.57 | 11.82 | 11.03
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Consumer Transformation | Headroom (MW) | Fault level | -37.8328 | -37.9248 | -38.0354 | -38.1747 | -38.5172 | -38.8552 | -40.3437 | -41.7081 | -42.8964 | -43.7722 | -44.1999 | -44.6146 | -45.04 | -45.4683 | -45.896 | -48.0537 | -21.2346 | -55.4004
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Leading the Way | Headroom (MW) | Fault level | -51.777 | -51.9075 | -52.0635 | -52.2588 | -52.7183 | -53.2002 | -53.9902 | -54.7269 | -55.3439 | -55.9269 | -56.5486 | -57.1633 | -57.7988 | -58.4382 | -23.5243 | -92.471 | -95.5514 | -98.6766
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | Steady Progression | Headroom (MW) | Fault level | -20.8708 | -20.8821 | -20.8911 | -20.8989 | -20.9082 | -20.9312 | -21.903 | -22.7967 | -23.6481 | -24.4437 | -25.1556 | -25.7467 | -26.0462 | -26.269 | -26.3967 | -26.6164 | -26.8225 | -27.0338
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | System Transformation | Headroom (MW) | Fault level | -29.8243 | -29.8622 | -29.904 | -29.9507 | -30.0396 | -30.1499 | -31.1859 | -32.1209 | -32.9105 | -33.4491 | -33.6297 | -33.7983 | -33.9736 | -34.1511 | -30.8972 | -57.059 | -57.885 | -58.7039
Willington 132kV | Stanton | ILKESTON 33 11kV S STN | Primary | 11 | -1.3249 | 52.9758 | WPD Best View | Headroom (MW) | Fault level | -31.0959 | -31.1715 | -31.2624 | -31.377 | -31.6585 | -31.9363 | -33.1597 | -34.2811 | -35.2579 | -35.9776 | -36.3292 | -36.6701 | -37.0198 | -37.3718 | -37.7233 | -39.4968 | -17.4534 | -45.5352
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Consumer Transformation | Headroom (MW) | Thermal | 17.62 | 17.31 | 17.11 | 16.87 | 16.28 | 15.84 | 15.27 | 14.6 | 14.04 | 13.5 | 12.95 | 12.42 | 11.88 | 11.33 | 10.74 | 6.73 | 1.31 | -4.6
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Leading the Way | Headroom (MW) | Thermal | 17.62 | 17.28 | 17.08 | 16.83 | 16.16 | 15.69 | 15.09 | 14.59 | 14.15 | 13.62 | 13.08 | 12.56 | 11.99 | 11.42 | 10.78 | 6.61 | 0.94 | -6.26
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | Steady Progression | Headroom (MW) | N/A | 17.62 | 17.49 | 17.34 | 17.28 | 17.19 | 17.11 | 17.02 | 16.96 | 16.89 | 16.7 | 16.64 | 16.59 | 16.56 | 16.55 | 16.56 | 16.78 | 16.2 | 15.21
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | System Transformation | Headroom (MW) | N/A | 17.62 | 17.44 | 17.24 | 17.11 | 16.85 | 16.65 | 16.43 | 16.25 | 15.97 | 15.76 | 15.55 | 15.36 | 15.19 | 15.07 | 14.97 | 14.09 | 11.88 | 9.63
Willington 132kV | Stanton | LITTLE HALLAM 33 11kV S STN | Primary | 11 | -1.3091 | 52.9598 | WPD Best View | Headroom (MW) | Thermal | 17.62 | 17.31 | 17.11 | 16.87 | 16.28 | 15.84 | 15.27 | 14.6 | 14.04 | 13.49 | 12.94 | 12.41 | 11.87 | 11.32 | 10.73 | 6.71 | 1.27 | -4.67
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Consumer Transformation | Headroom (MW) | N/A | 14.49 | 14.32 | 14.19 | 14 | 13.57 | 13.21 | 12.87 | 12.55 | 12.28 | 12.04 | 11.81 | 11.56 | 11.28 | 10.98 | 10.66 | 8.2 | 4.85 | 1.11
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Leading the Way | Headroom (MW) | Thermal | 14.49 | 14.31 | 14.17 | 13.97 | 13.49 | 13.11 | 12.74 | 12.39 | 12.11 | 11.86 | 11.6 | 11.3 | 10.95 | 10.56 | 10.11 | 7.17 | 3.3 | -1.79
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | Steady Progression | Headroom (MW) | N/A | 14.49 | 14.41 | 14.37 | 14.33 | 14.28 | 14.22 | 14.17 | 14.11 | 14.08 | 14.04 | 14.02 | 14 | 13.98 | 13.98 | 13.99 | 13.92 | 13.4 | 12.69
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | System Transformation | Headroom (MW) | N/A | 14.49 | 14.37 | 14.29 | 14.19 | 14.02 | 13.86 | 13.68 | 13.52 | 13.39 | 13.29 | 13.21 | 13.12 | 13.03 | 12.96 | 12.9 | 12.16 | 10.61 | 9.1
Willington 132kV | Stanton | SANDIACRE 33 11kV S STN | Primary | 11 | -1.2964 | 52.9228 | WPD Best View | Headroom (MW) | N/A | 14.49 | 14.32 | 14.19 | 14 | 13.57 | 13.21 | 12.87 | 12.55 | 12.28 | 12.04 | 11.81 | 11.56 | 11.28 | 10.98 | 10.66 | 8.2 | 4.85 | 1.11
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Consumer Transformation | Headroom (MW) | Thermal | 13.19 | 13.04 | 12.88 | 12.68 | 12.22 | 11.97 | 11.56 | 10.76 | 9.9 | 8.96 | 7.91 | 6.77 | 5.56 | 4.4 | 2.94 | -0.83 | -6.16 | -11.33
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Leading the Way | Headroom (MW) | Thermal | 13.19 | 13.03 | 12.86 | 12.66 | 12.18 | 11.94 | 11.51 | 11.07 | 10.65 | 10.22 | 9.78 | 9.33 | 8.27 | 7.24 | 6.11 | 1.68 | -5.57 | -10.38
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | Steady Progression | Headroom (MW) | N/A | 13.19 | 13.11 | 13.04 | 12.99 | 12.92 | 12.93 | 12.85 | 12.68 | 12.51 | 12.3 | 12.07 | 11.82 | 11.3 | 10.8 | 10.14 | 9.31 | 8.14 | 6.62
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | System Transformation | Headroom (MW) | Thermal | 13.19 | 13.08 | 12.97 | 12.86 | 12.66 | 12.58 | 12.38 | 11.79 | 11.1 | 10.35 | 9.48 | 8.54 | 7.56 | 6.66 | 5.52 | 3.53 | -0.28 | -3.64
Willington 132kV | Uttoxeter | CHURCH ST 33 11kV S STN | Primary | 11 | -1.8608 | 52.8996 | WPD Best View | Headroom (MW) | Thermal | 13.19 | 13.07 | 12.96 | 12.84 | 12.6 | 12.52 | 12.24 | 11.57 | 10.8 | 9.96 | 9.01 | 7.96 | 6.87 | 5.87 | 4.62 | 2.24 | -1.82 | -5.49
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Consumer Transformation | Headroom (MW) | Thermal | 1.59 | 1.52 | 1.46 | 1.41 | 1.27 | 1.19 | 1 | -0.16 | -1.55 | -3.18 | -5.18 | -7.49 | -10 | -12.29 | -15.19 | -20.96 | -26.27 | -32.84
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Leading the Way | Headroom (MW) | Thermal | 1.59 | 1.51 | 1.45 | 1.4 | 1.27 | 1.18 | 0.99 | 0.76 | 0.52 | 0.27 | 0.02 | -0.23 | -2.15 | -3.95 | -5.88 | -13.44 | -20.47 | -21.89
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | Steady Progression | Headroom (MW) | Thermal | 1.59 | 1.54 | 1.51 | 1.5 | 1.52 | 1.52 | 1.49 | 1.21 | 0.94 | 0.59 | 0.15 | -0.4 | -1.71 | -3.02 | -4.78 | -7.09 | -9.4 | -11.82
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | System Transformation | Headroom (MW) | Thermal | 1.59 | 1.53 | 1.49 | 1.46 | 1.43 | 1.4 | 1.32 | 0.26 | -1.08 | -2.6 | -4.49 | -6.68 | -9.05 | -11.2 | -13.96 | -18.95 | -23.68 | -29.57
Willington 132kV | Uttoxeter | MARCHINGTON 33 11kV S STN | Primary | 11 | -1.8028 | 52.8789 | WPD Best View | Headroom (MW) | Thermal | 1.59 | 1.53 | 1.48 | 1.45 | 1.39 | 1.35 | 1.2 | 0.07 | -1.32 | -2.91 | -4.88 | -7.16 | -9.63 | -11.88 | -14.73 | -20.09 | -25.05 | -31.21
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Consumer Transformation | Headroom (MW) | Thermal | 12.47 | 12.36 | 12.27 | 12.17 | 11.97 | 11.81 | 11 | 9.4 | 8.08 | 6.77 | 5.33 | 3.88 | 2.42 | 0.95 | -0.78 | -6.78 | -14.98 | -22.84
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Leading the Way | Headroom (MW) | Thermal | 12.47 | 12.36 | 12.27 | 12.18 | 12 | 11.82 | 10.96 | 10.19 | 9.57 | 8.69 | 7.88 | 7.12 | 5.93 | 4.74 | 3.46 | -1.79 | -10.18 | -16.18
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | Steady Progression | Headroom (MW) | N/A | 12.47 | 12.38 | 12.33 | 12.28 | 12.22 | 12.16 | 12.09 | 11.96 | 11.74 | 11.04 | 10.78 | 10.49 | 9.98 | 9.56 | 9.05 | 8.2 | 7.27 | 6.25
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | System Transformation | Headroom (MW) | Thermal | 12.47 | 12.37 | 12.31 | 12.24 | 12.13 | 12.03 | 11.92 | 11.54 | 10.62 | 9.92 | 9.12 | 8.32 | 7.51 | 6.81 | 5.92 | 4.03 | 0.57 | -2.42
Willington 132kV | Uttoxeter | ROCESTER 33 11kV S STN | Primary | 11 | -1.8506 | 52.9501 | WPD Best View | Headroom (MW) | Thermal | 12.47 | 12.37 | 12.29 | 12.21 | 12.07 | 11.95 | 11.19 | 9.64 | 8.35 | 7.08 | 5.67 | 4.27 | 2.86 | 1.43 | -0.24 | -5.77 | -13.64 | -21.06
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Consumer Transformation | Headroom (MW) | Thermal | 13.98 | 13.84 | 13.7 | 13.52 | 13.09 | 12.9 | 12.4 | 11.09 | 9.76 | 8.34 | 6.6 | 4.68 | 2.62 | 0.67 | -1.72 | -8.06 | -15.79 | -24.08
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Leading the Way | Headroom (MW) | Thermal | 13.98 | 13.83 | 13.69 | 13.5 | 13.04 | 12.91 | 12.42 | 11.81 | 11.25 | 10.67 | 10.04 | 9.43 | 7.73 | 6.07 | 4.3 | -2.51 | -11.93 | -18.06
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | Steady Progression | Headroom (MW) | N/A | 13.98 | 13.9 | 13.85 | 13.8 | 13.77 | 13.84 | 13.83 | 13.63 | 13.41 | 13.04 | 12.71 | 12.32 | 11.44 | 10.59 | 9.46 | 8.03 | 6.24 | 3.98
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | System Transformation | Headroom (MW) | Thermal | 13.98 | 13.87 | 13.79 | 13.69 | 13.53 | 13.53 | 13.42 | 12.65 | 11.59 | 10.53 | 9.14 | 7.58 | 5.92 | 4.41 | 2.5 | -0.79 | -5.91 | -11.28
Willington 132kV | Winster | ASHBOURNE 33 11kV S STN | Primary | 11 | -1.7116 | 53.014 | WPD Best View | Headroom (MW) | Thermal | 13.98 | 13.84 | 13.71 | 13.54 | 13.15 | 12.97 | 12.71 | 11.8 | 10.62 | 9.43 | 7.9 | 6.21 | 4.4 | 2.71 | 0.6 | -4.51 | -10.98 | -17.95
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Consumer Transformation | Headroom (MW) | N/A | 7.14 | 7.08 | 7.03 | 6.97 | 6.74 | 6.55 | 6.38 | 6.21 | 6.05 | 5.89 | 5.74 | 5.59 | 5.44 | 5.28 | 5.11 | 3.78 | 2.33 | 0.77
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Leading the Way | Headroom (MW) | Thermal | 7.14 | 7.07 | 7.02 | 6.95 | 6.68 | 6.48 | 6.29 | 6.11 | 5.93 | 5.75 | 5.58 | 5.41 | 5.23 | 5.03 | 4.82 | 3.43 | 1.81 | -0.15
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | Steady Progression | Headroom (MW) | N/A | 7.14 | 7.11 | 7.09 | 7.08 | 7.05 | 7.02 | 6.99 | 6.97 | 6.94 | 6.92 | 6.89 | 6.87 | 6.85 | 6.84 | 6.83 | 6.78 | 6.54 | 6.27
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | System Transformation | Headroom (MW) | N/A | 7.14 | 7.1 | 7.06 | 7.03 | 6.93 | 6.85 | 6.76 | 6.67 | 6.59 | 6.52 | 6.45 | 6.39 | 6.33 | 6.27 | 6.22 | 5.85 | 5.21 | 4.58
Willington 132kV | Winster | BAKEWELL 33 11kV S STN | Primary | 11 | -1.6893 | 53.2165 | WPD Best View | Headroom (MW) | N/A | 7.14 | 7.08 | 7.03 | 6.97 | 6.74 | 6.55 | 6.38 | 6.21 | 6.05 | 5.89 | 5.74 | 5.59 | 5.44 | 5.28 | 5.11 | 3.78 | 2.33 | 0.77
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Consumer Transformation | Headroom (MW) | N/A | 7.06 | 7.01 | 6.96 | 6.9 | 6.7 | 6.57 | 6.45 | 6.33 | 6.2 | 6.08 | 5.97 | 5.85 | 5.73 | 5.6 | 5.47 | 4.56 | 3.38 | 2.08
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Leading the Way | Headroom (MW) | N/A | 7.06 | 7.01 | 6.96 | 6.89 | 6.66 | 6.54 | 6.42 | 6.31 | 6.18 | 6.06 | 5.94 | 5.81 | 5.67 | 5.53 | 5.37 | 4.36 | 3.04 | 1.33
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | Steady Progression | Headroom (MW) | N/A | 7.06 | 7.05 | 7.03 | 7.02 | 7 | 7 | 6.99 | 6.98 | 6.97 | 6.96 | 6.95 | 6.94 | 6.93 | 6.93 | 6.93 | 6.98 | 6.86 | 6.61
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | System Transformation | Headroom (MW) | N/A | 7.06 | 7.03 | 7 | 6.97 | 6.89 | 6.85 | 6.8 | 6.75 | 6.7 | 6.65 | 6.6 | 6.55 | 6.51 | 6.47 | 6.44 | 6.23 | 5.69 | 5.16
Willington 132kV | Winster | CROMFORD 33 11kV S STN | Primary | 11 | -1.565 | 53.1022 | WPD Best View | Headroom (MW) | N/A | 7.06 | 7.01 | 6.96 | 6.9 | 6.7 | 6.57 | 6.45 | 6.33 | 6.2 | 6.08 | 5.97 | 5.85 | 5.73 | 5.6 | 5.47 | 4.56 | 3.38 | 2.08
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Consumer Transformation | Headroom (MW) | Thermal | -2.9 | -3.01 | -3.13 | -3.21 | -3.33 | -3.44 | -3.61 | -4.07 | -4.62 | -5.24 | -6.02 | -6.91 | -7.87 | -8.76 | -9.85 | -20.43 | -23.19 | -26.44
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Leading the Way | Headroom (MW) | Thermal | -2.9 | -3.01 | -3.13 | -3.22 | -3.34 | -3.44 | -3.63 | -3.84 | -4.06 | -4.28 | -4.47 | -4.68 | -5.46 | -6.23 | -7.04 | -16.98 | -20.4 | -22.24
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | Steady Progression | Headroom (MW) | Thermal | -2.9 | -2.98 | -3.03 | -3.07 | -3.08 | -3.08 | -3.12 | -3.23 | -3.34 | -3.48 | -3.66 | -3.88 | -4.38 | -4.86 | -5.51 | -6.43 | -9.56 | -10.68
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | System Transformation | Headroom (MW) | Thermal | -2.9 | -2.99 | -3.05 | -3.16 | -3.19 | -3.23 | -3.33 | -3.73 | -4.22 | -4.78 | -5.49 | -6.32 | -7.21 | -8.01 | -9.01 | -14.69 | -16.84 | -19.4
Willington 132kV | Winster | HOPTON 33 11kV S STN | Primary | 11 | -1.6098 | 53.0887 | WPD Best View | Headroom (MW) | Thermal | -2.9 | -3.01 | -3.13 | -3.21 | -3.33 | -3.44 | -3.61 | -4.07 | -4.62 | -5.24 | -6.02 | -6.91 | -7.87 | -8.76 | -9.85 | -20.43 | -23.19 | -26.44
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Consumer Transformation | Headroom (MW) | Thermal | 12.49 | 12.42 | 12.38 | 12.33 | 12.18 | 12.07 | 11.81 | 11.27 | 10.71 | 10.1 | 9.29 | 8.45 | 7.58 | 6.73 | 5.66 | 3.06 | -1.27 | -4.55
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Leading the Way | Headroom (MW) | Thermal | 12.49 | 12.42 | 12.37 | 12.32 | 12.2 | 12.05 | 11.79 | 11.46 | 11.14 | 10.75 | 10.29 | 9.85 | 9.1 | 8.41 | 7.65 | 5.01 | 0.29 | -2.2
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | Steady Progression | Headroom (MW) | N/A | 12.49 | 12.43 | 12.39 | 12.36 | 12.31 | 12.26 | 12.2 | 12.09 | 11.98 | 11.83 | 11.67 | 11.52 | 11.21 | 10.93 | 10.55 | 9.93 | 9.28 | 8.58
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | System Transformation | Headroom (MW) | N/A | 12.49 | 12.42 | 12.39 | 12.35 | 12.26 | 12.16 | 12.07 | 11.74 | 11.33 | 10.9 | 10.34 | 9.77 | 9.2 | 8.66 | 7.91 | 6.67 | 4.47 | 2.72
Willington 132kV | Winster | LONGCLIFFE 33 11kV S STN | Primary | 11 | -1.6592 | 53.0948 | WPD Best View | Headroom (MW) | Thermal | 12.49 | 12.42 | 12.38 | 12.33 | 12.21 | 12.1 | 11.9 | 11.46 | 11 | 10.5 | 9.8 | 9.08 | 8.32 | 7.59 | 6.69 | 4.35 | 0.15 | -2.97
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Consumer Transformation | Headroom (MW) | Thermal | 13.66 | 13.52 | 13.37 | 13.19 | 12.8 | 12.44 | 11.55 | 10.2 | 9.18 | 8.24 | 7.27 | 6.31 | 5.37 | 4.35 | 3.27 | -2.68 | -10.29 | -18.33
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Leading the Way | Headroom (MW) | Thermal | 13.66 | 13.5 | 13.36 | 13.17 | 12.77 | 12.4 | 11.45 | 10.61 | 9.96 | 9.12 | 8.31 | 7.51 | 6.68 | 5.78 | 4.81 | -0.54 | -7.4 | -15.39
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | Steady Progression | Headroom (MW) | N/A | 13.66 | 13.59 | 13.56 | 13.52 | 13.52 | 13.48 | 13.43 | 13.37 | 13.24 | 12.7 | 12.57 | 12.43 | 12.25 | 12.15 | 12.08 | 11.92 | 11.33 | 10.53
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | System Transformation | Headroom (MW) | N/A | 13.66 | 13.56 | 13.48 | 13.39 | 13.28 | 13.12 | 12.94 | 12.76 | 12.18 | 11.85 | 11.48 | 11.15 | 10.87 | 10.66 | 10.42 | 9.14 | 6.8 | 4.34
Willington 132kV | Winster | MATLOCK 33 11kV S STN | Primary | 11 | -1.5509 | 53.1388 | WPD Best View | Headroom (MW) | Thermal | 13.66 | 13.52 | 13.37 | 13.19 | 12.8 | 12.44 | 11.55 | 10.2 | 9.18 | 8.24 | 7.27 | 6.31 | 5.37 | 4.35 | 3.27 | -2.68 | -10.29 | -18.33
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Consumer Transformation | Headroom (MW) | N/A | 8.87 | 8.77 | 8.69 | 8.59 | 8.34 | 8.14 | 7.95 | 7.77 | 7.6 | 7.44 | 7.29 | 7.13 | 6.97 | 6.81 | 6.63 | 5.43 | 3.82 | 2.04
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Leading the Way | Headroom (MW) | N/A | 8.87 | 8.76 | 8.68 | 8.57 | 8.29 | 8.09 | 7.89 | 7.72 | 7.55 | 7.39 | 7.22 | 7.05 | 6.87 | 6.68 | 6.46 | 5.08 | 3.28 | 0.9
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | Steady Progression | Headroom (MW) | N/A | 8.87 | 8.81 | 8.78 | 8.75 | 8.71 | 8.67 | 8.63 | 8.58 | 8.55 | 8.51 | 8.48 | 8.45 | 8.43 | 8.41 | 8.39 | 8.37 | 8.15 | 7.77
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | System Transformation | Headroom (MW) | N/A | 8.87 | 8.79 | 8.74 | 8.68 | 8.57 | 8.48 | 8.38 | 8.28 | 8.19 | 8.12 | 8.04 | 7.97 | 7.9 | 7.85 | 7.79 | 7.46 | 6.71 | 5.95
Willington 132kV | Winster | MILLCLOSE 33 11kV S STN | Primary | 11 | -1.6161 | 53.1575 | WPD Best View | Headroom (MW) | N/A | 8.87 | 8.77 | 8.69 | 8.59 | 8.34 | 8.14 | 7.95 | 7.77 | 7.6 | 7.44 | 7.29 | 7.13 | 6.97 | 6.81 | 6.63 | 5.43 | 3.82 | 2.04
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Consumer Transformation | Headroom (MW) | Thermal | 42.72 | 42.06 | 40.08 | 36.46 | 35.12 | 34.29 | 31.97 | 27.97 | 23.99 | 20.13 | 15.46 | 10.76 | 5.89 | 1.21 | -4.39 | -23.56 | -45.54 | -70.78
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Leading the Way | Headroom (MW) | Thermal | 42.72 | 42.02 | 40.03 | 36.39 | 34.94 | 34.21 | 32.35 | 30.72 | 28.85 | 26.97 | 24.85 | 23.03 | 18.92 | 14.8 | 10.37 | -9.37 | -22.87 | -59.9
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | Steady Progression | Headroom (MW) | N/A | 42.72 | 42.33 | 40.59 | 37.23 | 36.97 | 37.04 | 35.97 | 34.74 | 33.28 | 31.14 | 29.53 | 27.88 | 25.57 | 23.45 | 20.9 | 17.81 | 13.12 | 7.43
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | System Transformation | Headroom (MW) | Thermal | 42.72 | 42.23 | 40.34 | 36.91 | 36.38 | 36.27 | 35.28 | 33.29 | 30.11 | 27.45 | 24.08 | 20.59 | 16.99 | 13.83 | 9.97 | 1.84 | 0.38 | -24.57
Chesterfield 132kV | Alfreton | Alfreton | Bulk Supply Point | 33 | -1.385 | 53.1088 | WPD Best View | Headroom (MW) | Thermal | 42.72 | 42.06 | 40.08 | 36.46 | 35.12 | 34.29 | 31.97 | 27.97 | 23.99 | 20.13 | 15.46 | 10.76 | 5.89 | 1.21 | -4.39 | -23.56 | -45.54 | -70.78
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Consumer Transformation | Headroom (MW) | Thermal | 35.17 | 34.69 | 34.22 | 33.63 | 32.43 | 31.47 | 29.3 | 25.44 | 22.27 | 19.16 | 15.5 | 11.74 | 7.86 | 3.93 | -0.6 | -20.57 | -44.82 | -70.86
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Leading the Way | Headroom (MW) | Thermal | 35.17 | 34.66 | 34.18 | 33.59 | 32.31 | 31.34 | 29.02 | 27.09 | 25.53 | 23.53 | 21.59 | 19.71 | 16.53 | 13.19 | 9.54 | -9.98 | -33.78 | -57.05
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Steady Progression | Headroom (MW) | N/A | 35.17 | 34.92 | 34.78 | 34.64 | 34.48 | 34.32 | 34.17 | 33.89 | 33.41 | 31.89 | 31.28 | 30.56 | 29.22 | 28.11 | 26.73 | 25.08 | 21.94 | 17.9
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | System Transformation | Headroom (MW) | Thermal | 35.17 | 34.82 | 34.54 | 34.24 | 33.76 | 33.34 | 32.89 | 31.93 | 29.78 | 28.17 | 26.04 | 23.81 | 21.54 | 19.62 | 17.33 | 10.72 | 0.7 | -10.23
Chesterfield 132kV | Annesley (1 & 2) | Annesley (1 & 2) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | WPD Best View | Headroom (MW) | Thermal | 35.17 | 34.69 | 34.22 | 33.63 | 32.43 | 31.47 | 29.3 | 25.44 | 22.27 | 19.16 | 15.5 | 11.74 | 7.87 | 3.94 | -0.6 | -20.57 | -44.82 | -70.85
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Consumer Transformation | Headroom (MW) | Thermal | 22.06 | 21.54 | 21.11 | 17.27 | 15.71 | 14.44 | 12.62 | 10.47 | 8.39 | 6.46 | 4.5 | 2.55 | 0.51 | -1.51 | -3.84 | -15.05 | -21.53 | -46.77
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Leading the Way | Headroom (MW) | Thermal | 22.06 | 21.51 | 21.05 | 17.16 | 15.36 | 14.04 | 12.63 | 11.17 | 9.74 | 8.6 | 1.89 | -0.89 | -2.87 | -4.92 | 2.78 | -24.3 | -44.32 | -62.44
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | Steady Progression | Headroom (MW) | N/A | 22.06 | 21.75 | 21.69 | 18.21 | 17.94 | 17.75 | 16.63 | 15.41 | 14.25 | 13.11 | 11.99 | 10.91 | 9.86 | 8.95 | 7.95 | 6.81 | 4.39 | 0.55
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | System Transformation | Headroom (MW) | Thermal | 22.06 | 21.65 | 21.5 | 17.75 | 17.13 | 16.71 | 15.44 | 13.85 | 12.27 | 10.86 | 9.38 | 7.92 | 6.51 | 5.26 | 5.58 | -8.19 | -17.84 | -26.4
Chesterfield 132kV | Annesley (3 & 4) | Annesley (3 & 4) | Bulk Supply Point | 33 | -1.2458 | 53.0885 | WPD Best View | Headroom (MW) | Thermal | 22.06 | 21.54 | 21.11 | 17.27 | 15.71 | 14.44 | 12.62 | 10.47 | 8.39 | 6.46 | 4.5 | 2.55 | 0.51 | -1.51 | -3.84 | -15.05 | -21.53 | -46.77
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Consumer Transformation | Headroom (MW) | Thermal | 40.42 | 39.73 | 32.93 | 32.15 | 30.28 | 28.22 | 24.71 | 20.91 | 17.21 | 14.09 | 11.58 | 9.4 | 7.43 | 5.35 | 3.65 | -12.69 | -26.13 | -43.95
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Leading the Way | Headroom (MW) | Thermal | 40.42 | 39.66 | 32.85 | 32 | 29.98 | 27.36 | 24.44 | 20.93 | 17.23 | 14.16 | 11.83 | 9.52 | 7.06 | 4.57 | 2.71 | 3.58 | -36.94 | -60.88
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | Steady Progression | Headroom (MW) | N/A | 40.42 | 40.03 | 33.64 | 33.41 | 33.17 | 32.88 | 30.77 | 28.52 | 26.3 | 24.31 | 22.46 | 20.93 | 20.05 | 19.38 | 18.95 | 18.57 | 16.87 | 13.7
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | System Transformation | Headroom (MW) | Thermal | 40.42 | 39.9 | 33.32 | 32.91 | 32.11 | 31.06 | 28.8 | 26.15 | 23.52 | 21.58 | 20.17 | 19.18 | 18.4 | 17.65 | 16.86 | 25.09 | 5.38 | -2.8
Walpole 132kV | Boston | Boston | Bulk Supply Point | 33 | -0.0142 | 52.9665 | WPD Best View | Headroom (MW) | N/A | 40.42 | 39.99 | 33.57 | 33.3 | 32.94 | 32.36 | 29.93 | 27.29 | 24.64 | 22.18 | 20.11 | 18.41 | 17.39 | 16.57 | 15.82 | 14.62 | 11.33 | 7.47
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Consumer Transformation | Headroom (MW) | Thermal | 40.52 | 40.16 | 39.88 | 39.53 | 38.66 | 37.72 | 36.53 | 34.18 | 31.58 | 28.73 | 25.6 | 22.15 | 18.48 | 15.08 | 10.91 | -0.9 | -13.03 | -27.46
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Leading the Way | Headroom (MW) | Thermal | 40.52 | 40.14 | 39.84 | 39.47 | 38.58 | 37.3 | 35.83 | 34.12 | 32.32 | 30.37 | 28.89 | 27.44 | 24.13 | 21.04 | 18.4 | 3.63 | -11.94 | -23.9
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | Steady Progression | Headroom (MW) | N/A | 40.52 | 40.3 | 40.2 | 40.1 | 39.94 | 39.83 | 39.68 | 39.28 | 38.89 | 38.42 | 37.8 | 37.11 | 35.6 | 34.12 | 32.14 | 29.44 | 26.79 | 23.05
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | System Transformation | Headroom (MW) | Thermal | 40.52 | 40.24 | 40.05 | 39.86 | 39.45 | 38.99 | 38.47 | 36.81 | 34.74 | 32.54 | 30.06 | 27.33 | 24.49 | 21.87 | 18.44 | 12.41 | 4.11 | -5.67
Walpole 132kV | Bourne | Bourne | Bulk Supply Point | 33 | -0.3838 | 52.7656 | WPD Best View | Headroom (MW) | Thermal | 40.52 | 40.17 | 39.89 | 39.56 | 38.76 | 37.98 | 37.1 | 35.11 | 32.88 | 30.43 | 27.54 | 24.33 | 20.91 | 17.77 | 13.92 | 3.9 | -7.72 | -21.43
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Consumer Transformation | Headroom (MW) | Thermal | 65.72 | 65.06 | 64.64 | 64.05 | 63.32 | 62.53 | 60.55 | 57.39 | 54.71 | 52.09 | 49.53 | 46.82 | 44.05 | 41.2 | 38.06 | 22.13 | 3.18 | -16.71
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Leading the Way | Headroom (MW) | Thermal | 65.72 | 65.18 | 64.76 | 64.12 | 63.34 | 62.63 | 60.48 | 58.33 | 56.41 | 54.23 | 52.24 | 46.14 | 43.51 | 40.71 | 37.67 | 27.51 | -3.56 | -27.03
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | Steady Progression | Headroom (MW) | N/A | 65.72 | 65.25 | 65.07 | 64.8 | 64.94 | 64.93 | 64.67 | 64.46 | 64.06 | 62.93 | 62.5 | 62.02 | 61.3 | 60.66 | 59.92 | 58.36 | 55.88 | 52.58
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | System Transformation | Headroom (MW) | N/A | 65.72 | 65.15 | 64.9 | 64.51 | 64.42 | 64.26 | 63.72 | 62.86 | 61.24 | 60 | 58.71 | 57.4 | 56.11 | 54.94 | 53.56 | 52.3 | 36.86 | 27.7
East Claydon 132kV | Bradwell Abbey | Bradwell Abbey | Bulk Supply Point | 33 | -0.7968 | 52.0493 | WPD Best View | Headroom (MW) | Thermal | 65.72 | 65.18 | 64.76 | 64.12 | 63.34 | 62.63 | 60.48 | 58.33 | 56.41 | 54.23 | 52.24 | 46.14 | 43.51 | 40.71 | 37.67 | 27.51 | -3.56 | -27.03
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Consumer Transformation | Headroom (MW) | Thermal | 68.07 | 67.73 | 67.35 | 66.98 | 65.85 | 64.5 | 63.22 | 61.38 | 59.43 | 57.42 | 55 | 52.35 | 49.49 | 46.72 | 43.49 | 31.91 | 15.57 | -2.12
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Leading the Way | Headroom (MW) | Thermal | 68.07 | 67.69 | 67.29 | 66.57 | 65.05 | 63.55 | 62.1 | 60.75 | 59.41 | 58.12 | 56.86 | 50.76 | 48.13 | 45.45 | 42.54 | 28.88 | 8.65 | -9.49
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | Steady Progression | Headroom (MW) | N/A | 68.07 | 67.99 | 68.09 | 68.18 | 68.26 | 61.83 | 61.85 | 61.42 | 61.02 | 60.54 | 59.99 | 59.37 | 58.22 | 57.11 | 55.68 | 53.76 | 50.5 | 46.26
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | System Transformation | Headroom (MW) | N/A | 68.07 | 67.87 | 67.82 | 67.62 | 67.3 | 66.71 | 59.6 | 58.32 | 56.84 | 55.35 | 53.48 | 51.39 | 49.18 | 47.22 | 44.86 | 39.76 | 29.37 | 18.87
Drakelow 132kV | Burton 33 | Burton 33 | Bulk Supply Point | 33 | -1.6229 | 52.8172 | WPD Best View | Headroom (MW) | N/A | 68.07 | 67.75 | 67.4 | 67.07 | 66.07 | 64.82 | 63.61 | 61.85 | 59.98 | 58.02 | 55.66 | 53.08 | 50.3 | 47.61 | 44.48 | 33.76 | 18.26 | 1.57
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Consumer Transformation | Headroom (MW) | N/A | 69.72 | 69.56 | 69.44 | 69.33 | 69.21 | 69.14 | 68.91 | 67.92 | 66.78 | 65.43 | 63.78 | 62.12 | 60.34 | 58.69 | 56.68 | 51.71 | 44.52 | 35.84
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Leading the Way | Headroom (MW) | N/A | 69.72 | 69.57 | 69.45 | 69.38 | 69.3 | 69.39 | 69.21 | 68.87 | 68.5 | 68.03 | 67.45 | 67.18 | 65.76 | 64.4 | 62.95 | 57.3 | 48.57 | 41.45
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | Steady Progression | Headroom (MW) | N/A | 69.72 | 69.63 | 69.62 | 69.66 | 69.94 | 70.09 | 70.19 | 70.17 | 70.17 | 70.07 | 69.91 | 69.69 | 69.04 | 68.38 | 67.44 | 67.31 | 65.06 | 62.16
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | System Transformation | Headroom (MW) | N/A | 69.72 | 69.62 | 69.56 | 69.56 | 69.76 | 69.91 | 69.94 | 69.31 | 68.5 | 67.5 | 66.19 | 64.78 | 63.26 | 61.92 | 60.27 | 57.89 | 52.78 | 46.63
Drakelow 132kV | Burton South | Burton South | Bulk Supply Point | 33 | -1.6462 | 52.7725 | WPD Best View | Headroom (MW) | N/A | 69.72 | 69.62 | 69.56 | 69.56 | 69.74 | 69.88 | 69.91 | 69.28 | 68.46 | 67.46 | 66.14 | 64.73 | 63.21 | 61.87 | 60.2 | 57.75 | 52.57 | 46.33
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Consumer Transformation | Headroom (MW) | Thermal | 46.24 | 45.65 | 45.33 | 45.08 | 43.65 | 42.49 | 40.71 | 35.72 | 30.26 | 24.37 | 16.77 | 8.19 | -1.19 | -9.94 | -20.48 | -48.63 | -79.62 | -115.38
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Leading the Way | Headroom (MW) | Thermal | 46.24 | 46.11 | 45.76 | 45.59 | 44.13 | 43.05 | 41.51 | 40.05 | 38.56 | 37.13 | 35.83 | 34.53 | 27.2 | 19.91 | 12.07 | -14.22 | -61.02 | -83.13
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | Steady Progression | Headroom (MW) | Thermal | 46.24 | 45.9 | 45.86 | 46.01 | 45.96 | 45.88 | 45.21 | 43.78 | 42.35 | 40.54 | 38.61 | 36.39 | 31.62 | 26.91 | 20.66 | 12.99 | 4.21 | -6.04
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | System Transformation | Headroom (MW) | Thermal | 46.24 | 45.8 | 45.65 | 45.67 | 45.18 | 44.78 | 43.91 | 40.08 | 35.13 | 29.94 | 23.18 | 15.39 | 6.94 | -0.72 | -10.18 | -23.6 | -52.03 | -78.67
Staythorpe 132kV | Checkerhouse | Checkerhouse | Bulk Supply Point | 33 | -0.9957 | 53.3071 | WPD Best View | Headroom (MW) | Thermal | 46.24 | 45.66 | 45.35 | 45.12 | 43.75 | 42.63 | 40.88 | 35.97 | 30.53 | 24.68 | 17.13 | 8.6 | -0.74 | -9.43 | -19.94 | -47.72 | -78.37 | -113.79
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Consumer Transformation | Headroom (MW) | Thermal | 40.45 | 39.91 | 32.76 | 32.17 | 30.82 | 29.55 | 28.23 | 25.93 | 23.33 | 20.53 | 16.89 | 12.78 | 8.41 | 4.32 | 0.06 | -15.95 | -33.33 | -53.8
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Leading the Way | Headroom (MW) | Thermal | 40.45 | 39.89 | 32.71 | 32.1 | 30.6 | 29.19 | 27.82 | 26.66 | 25.46 | 24.29 | 23.1 | 21.84 | 18.21 | 14.65 | 11.67 | -2.61 | -31.09 | -49.23
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | Steady Progression | Headroom (MW) | N/A | 40.45 | 40.16 | 33.37 | 33.23 | 33.04 | 32.82 | 32.49 | 32.03 | 31.54 | 30.91 | 30.08 | 29.09 | 27.03 | 25.03 | 22.4 | 18.86 | 14.17 | 8.27
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | System Transformation | Headroom (MW) | Thermal | 40.45 | 40.07 | 33.14 | 32.78 | 32.23 | 31.65 | 31 | 29.33 | 27.18 | 24.95 | 21.83 | 18.3 | 14.57 | 11.22 | 7.23 | 0.97 | -15.92 | -30.26
Chesterfield 132kV | Clipstone | Clipstone | Bulk Supply Point | 33 | -1.1033 | 53.1658 | WPD Best View | Headroom (MW) | Thermal | 40.45 | 39.91 | 32.76 | 32.17 | 30.82 | 29.55 | 28.23 | 25.93 | 23.33 | 20.53 | 16.89 | 12.78 | 8.41 | 4.32 | 0.06 | -15.95 | -33.33 | -53.8
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Consumer Transformation | Headroom (MW) | Thermal | 59.44 | 58.69 | 57.88 | 56.67 | 54.48 | 52.36 | 48 | 39.95 | 32.98 | 26.02 | 17.9 | 9.32 | 0.35 | -8.56 | -18.9 | -61.57 | -111.99 | -163.96
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Leading the Way | Headroom (MW) | Thermal | 59.44 | 58.65 | 57.84 | 56.66 | 54.3 | 52.09 | 47.4 | 43.31 | 39.93 | 35.68 | 31.68 | 24.45 | 17 | 9.37 | 1.1 | -40.66 | -94.16 | -137.92
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | Steady Progression | Headroom (MW) | N/A | 59.44 | 58.99 | 58.75 | 58.81 | 58.51 | 58.18 | 57.87 | 57.13 | 56.07 | 52.98 | 51.53 | 49.84 | 46.54 | 43.62 | 39.94 | 34.68 | 27.16 | 17.88
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | System Transformation | Headroom (MW) | Thermal | 59.44 | 58.86 | 58.41 | 58.22 | 57.4 | 56.55 | 55.63 | 53.05 | 48.12 | 44.07 | 38.93 | 33.35 | 27.58 | 22.51 | 16.35 | -0.19 | -24.74 | -48.67
Enderby 132kV | Coalville | Coalville | Bulk Supply Point | 33 | -1.3271 | 52.6883 | WPD Best View | Headroom (MW) | Thermal | 59.44 | 58.69 | 57.88 | 56.67 | 54.48 | 52.36 | 48 | 39.95 | 32.98 | 26.02 | 17.9 | 9.32 | 0.35 | -8.56 | -18.9 | -61.57 | -111.99 | -163.96
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Consumer Transformation | Headroom (MW) | Thermal | 96.38 | 95.59 | 94.83 | 94.12 | 92.49 | 91.61 | 90.49 | 87.73 | 84.91 | 82.14 | 78.88 | 74.89 | 70.44 | 66.21 | 61.09 | 46.11 | 22.76 | -4.69
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Leading the Way | Headroom (MW) | N/A | 96.38 | 95.51 | 94.74 | 93.96 | 92.06 | 91.34 | 90.36 | 89.6 | 88.89 | 88.51 | 87.86 | 86.91 | 83.6 | 80.25 | 76.54 | 59.67 | 33.02 | 8.37
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | Steady Progression | Headroom (MW) | N/A | 96.38 | 95.88 | 95.63 | 89.25 | 89.02 | 89.17 | 88.69 | 87.95 | 87.23 | 86.34 | 85.78 | 85.02 | 83.56 | 82.24 | 80.39 | 80.64 | 75.95 | 69.21
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | System Transformation | Headroom (MW) | N/A | 96.38 | 95.75 | 95.34 | 94.79 | 94.08 | 94 | 94.05 | 92.77 | 90.72 | 89.08 | 86.93 | 84.16 | 81.03 | 78.26 | 74.7 | 69.84 | 56.29 | 39.94
Grendon 132kV | Corby | Corby | Bulk Supply Point | 33 | -0.6685 | 52.4916 | WPD Best View | Headroom (MW) | N/A | 96.38 | 95.55 | 94.98 | 94.12 | 92.45 | 91.87 | 91.02 | 89.39 | 87.52 | 85.78 | 83.59 | 80.8 | 77.04 | 73.4 | 69.03 | 54 | 29.77 | 3.13
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Consumer Transformation | Headroom (MW) | N/A | 88.05 | 87.62 | 87.35 | 87.03 | 86.34 | 85.99 | 85.72 | 85.18 | 84.32 | 83.47 | 82.63 | 81.83 | 81.02 | 80.1 | 79.11 | 71.08 | 59.47 | 46.46
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Leading the Way | Headroom (MW) | N/A | 88.05 | 87.55 | 87.27 | 86.93 | 85.98 | 85.58 | 85.34 | 84.77 | 83.88 | 82.99 | 82 | 81.04 | 80.03 | 78.85 | 77.49 | 68.02 | 54.68 | 37.46
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | Steady Progression | Headroom (MW) | N/A | 88.05 | 87.69 | 87.5 | 87.31 | 87 | 86.79 | 86.74 | 86.66 | 86.54 | 86.48 | 86.34 | 86.19 | 86.06 | 85.91 | 85.75 | 85.04 | 83.62 | 82
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | System Transformation | Headroom (MW) | N/A | 88.05 | 87.66 | 87.43 | 87.18 | 86.71 | 86.45 | 86.41 | 86.33 | 86.23 | 86.12 | 85.91 | 85.68 | 85.43 | 85.18 | 84.93 | 82.98 | 77.55 | 72.05
Berkswell 132kV | Coventry Central | Coventry Central | Bulk Supply Point | 33 | -1.5074 | 52.42 | WPD Best View | Headroom (MW) | N/A | 88.05 | 87.62 | 87.35 | 87.03 | 86.33 | 85.98 | 85.71 | 85.17 | 84.32 | 83.47 | 82.62 | 81.82 | 81 | 80.08 | 79.09 | 71.03 | 59.4 | 46.31
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Consumer Transformation | Headroom (MW) | N/A | 66.51 | 66.69 | 66.97 | 63.64 | 63.07 | 62.61 | 61.95 | 60.67 | 59.25 | 57.46 | 55.29 | 52.97 | 50.51 | 48.07 | 51.37 | 40.7 | 27.03 | 11.38
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Leading the Way | Headroom (MW) | N/A | 66.51 | 72.87 | 73.2 | 69.97 | 69.26 | 68.82 | 68.08 | 67.29 | 66.44 | 65.23 | 63.94 | 62.77 | 60.5 | 58.16 | 55.64 | 43.36 | 18.3 | 1.28
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | Steady Progression | Headroom (MW) | N/A | 66.51 | 66.79 | 67.25 | 64.22 | 64.54 | 64.75 | 64.85 | 64.8 | 64.74 | 64.51 | 64.19 | 63.82 | 62.95 | 62.08 | 60.89 | 65.11 | 62.06 | 58.23
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | System Transformation | Headroom (MW) | N/A | 66.51 | 66.78 | 67.23 | 64.13 | 64.18 | 64.17 | 64.02 | 63.31 | 62.49 | 61.27 | 59.71 | 57.96 | 56.12 | 54.41 | 58.5 | 54.05 | 40.11 | 30.84
Coventry 132kV | Coventry North | Coventry North | Bulk Supply Point | 33 | -1.4678 | 52.4536 | WPD Best View | Headroom (MW) | N/A | 66.51 | 66.64 | 66.9 | 63.56 | 62.94 | 62.53 | 61.86 | 61 | 60.09 | 58.96 | 57.63 | 56.33 | 54.52 | 52.57 | 56.38 | 46.71 | 33.62 | 17.69
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Consumer Transformation | Headroom (MW) | N/A | 68.62 | 68.26 | 67.97 | 67.63 | 66.86 | 66.23 | 64.72 | 62.13 | 60 | 57.87 | 55.59 | 53.45 | 51.26 | 48.97 | 46.46 | 33.89 | 17.92 | 0.78
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Leading the Way | Headroom (MW) | N/A | 68.62 | 68.23 | 67.94 | 67.59 | 66.73 | 66.1 | 64.57 | 63.1 | 61.78 | 59.98 | 58.23 | 56.74 | 54.85 | 52.85 | 50.66 | 38.89 | 23.73 | 6.96
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | Steady Progression | Headroom (MW) | N/A | 68.62 | 68.4 | 68.28 | 68.19 | 68.05 | 68 | 68.02 | 68.01 | 67.84 | 66.9 | 66.67 | 66.43 | 65.93 | 65.54 | 65.13 | 64.4 | 62.8 | 60.43
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | System Transformation | Headroom (MW) | N/A | 68.62 | 68.34 | 68.15 | 67.97 | 67.62 | 67.43 | 67.34 | 67.05 | 65.78 | 64.85 | 63.76 | 62.79 | 61.84 | 61.04 | 60.15 | 56.8 | 50.98 | 44.76
Berkswell 132kV | Coventry West | Coventry West | Bulk Supply Point | 33 | -1.605 | 52.4017 | WPD Best View | Headroom (MW) | N/A | 68.62 | 68.26 | 67.97 | 67.63 | 66.86 | 66.23 | 64.72 | 62.13 | 60 | 57.87 | 55.59 | 53.45 | 51.26 | 48.97 | 46.46 | 33.89 | 17.92 | 0.78
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Consumer Transformation | Headroom (MW) | Thermal | 53.53 | 52.92 | 52.29 | 50.01 | 48.37 | 47.06 | 43.18 | 34.89 | 27.51 | 19.77 | 10.75 | 1.17 | -8.86 | -18.67 | -30.77 | -75.08 | -120.38 | -170.36
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Leading the Way | Headroom (MW) | Thermal | 53.53 | 53.27 | 52.62 | 50.34 | 48.58 | 47.29 | 43.12 | 39.31 | 36.2 | 31.93 | 28.21 | 23.7 | 15.67 | 7.54 | -1.07 | -40.9 | -88.88 | -126.03
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | Steady Progression | Headroom (MW) | N/A | 53.53 | 53.18 | 52.97 | 51.29 | 51.19 | 51.2 | 51.05 | 50.37 | 49.36 | 46.2 | 44.7 | 42.82 | 38.86 | 35.25 | 30.62 | 24.81 | 16.91 | 7.64
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | System Transformation | Headroom (MW) | Thermal | 53.53 | 53.06 | 52.72 | 50.81 | 50.21 | 49.74 | 49.06 | 46.18 | 40.7 | 35.91 | 29.86 | 23.15 | 16.06 | 9.85 | 1.98 | -14.06 | -38.56 | -63.59
Coventry 132kV | Daventry | Daventry | Bulk Supply Point | 33 | -1.1548 | 52.2593 | WPD Best View | Headroom (MW) | Thermal | 53.53 | 53.05 | 52.69 | 50.75 | 50.08 | 49.62 | 49 | 46.35 | 41.24 | 36.82 | 31.17 | 24.93 | 18.02 | 11.94 | 4.27 | -11.67 | -36.99 | -62.06
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Consumer Transformation | Headroom (MW) | Thermal | 71.48 | 70.83 | 70.21 | 69.28 | 67.51 | 65.82 | 64.22 | 62.43 | 60.65 | 59.02 | 57.29 | 55.37 | 53.34 | 51.3 | 48.96 | 33.93 | 17.15 | -1.77
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Leading the Way | Headroom (MW) | Thermal | 71.48 | 70.79 | 70.11 | 69.12 | 67.25 | 65.44 | 63.72 | 62.13 | 60.6 | 59.31 | 57.96 | 56.53 | 54.42 | 52.16 | 49.59 | 32.68 | 13.13 | -10.28
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | Steady Progression | Headroom (MW) | N/A | 71.48 | 71.08 | 70.86 | 70.64 | 70.48 | 70.25 | 70 | 69.64 | 69.3 | 68.98 | 68.64 | 68.28 | 67.73 | 67.19 | 66.52 | 65.37 | 61.4 | 57.25
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | System Transformation | Headroom (MW) | N/A | 71.48 | 70.96 | 70.58 | 70.18 | 69.52 | 68.78 | 67.94 | 66.86 | 65.74 | 64.72 | 63.62 | 62.41 | 61.19 | 60.13 | 58.83 | 53.28 | 44.5 | 35.38
Willington 132kV | Derby 33 | Derby 33 | Bulk Supply Point | 33 | -1.4763 | 52.9256 | WPD Best View | Headroom (MW) | Thermal | 71.48 | 70.83 | 70.21 | 69.28 | 67.51 | 65.82 | 64.22 | 62.43 | 60.65 | 59.02 | 57.29 | 55.37 | 53.34 | 51.3 | 48.96 | 33.93 | 17.15 | -1.77
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Consumer Transformation | Headroom (MW) | N/A | 69.83 | 69.12 | 68.4 | 67.55 | 65.64 | 64.07 | 62.39 | 60.71 | 59.12 | 57.66 | 56.22 | 54.83 | 53.33 | 51.73 | 50.03 | 38.04 | 22.56 | 5.42
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Leading the Way | Headroom (MW) | Thermal | 69.83 | 69.05 | 68.3 | 67.4 | 65.28 | 63.63 | 61.84 | 60.08 | 58.36 | 56.76 | 55.08 | 53.5 | 51.7 | 49.74 | 47.6 | 33.73 | 16.07 | -7.08
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | Steady Progression | Headroom (MW) | N/A | 69.83 | 69.47 | 69.2 | 68.99 | 68.74 | 68.48 | 68.17 | 67.88 | 67.59 | 67.3 | 67.03 | 66.83 | 66.64 | 66.49 | 66.35 | 65.91 | 63.56 | 60.21
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | System Transformation | Headroom (MW) | N/A | 69.83 | 69.3 | 68.84 | 68.36 | 67.6 | 66.9 | 66.08 | 65.26 | 64.5 | 63.75 | 63.04 | 62.47 | 61.83 | 61.31 | 60.73 | 57.13 | 49.7 | 42.37
Chesterfield 132kV | Goitside | Goitside | Bulk Supply Point | 33 | -1.4438 | 53.2336 | WPD Best View | Headroom (MW) | N/A | 69.83 | 69.12 | 68.4 | 67.55 | 65.64 | 64.07 | 62.39 | 60.71 | 59.13 | 57.66 | 56.23 | 54.85 | 53.35 | 51.74 | 50.05 | 38.05 | 22.58 | 5.44
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Consumer Transformation | Headroom (MW) | Thermal | 39.19 | 38.8 | 38.4 | 37.93 | 36.9 | 35.64 | 30.98 | 21.1 | 12.49 | 3.63 | -6.5 | -17.23 | -28.31 | -39.25 | -52.03 | -93.07 | -143.4 | -198.68
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Leading the Way | Headroom (MW) | Thermal | 39.19 | 38.77 | 38.41 | 37.96 | 36.92 | 35.4 | 30.16 | 25.55 | 21.68 | 16.42 | 12.04 | 7.82 | -0.99 | -9.95 | -19.49 | -56.35 | -103.94 | -142.12
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | Steady Progression | Headroom (MW) | Thermal | 39.19 | 38.97 | 38.85 | 38.75 | 38.6 | 38.43 | 38.24 | 37.5 | 36.23 | 32.13 | 30.36 | 28.17 | 23.73 | 19.76 | 14.74 | 7.6 | -0.21 | -8.69
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | System Transformation | Headroom (MW) | Thermal | 39.19 | 38.88 | 38.67 | 38.45 | 38.04 | 37.5 | 36.86 | 33.91 | 27.44 | 22.21 | 15.69 | 8.54 | 1.04 | -5.54 | -13.6 | -29.13 | -51.09 | -76.93
Bicker Fen 132kV | Grantham | Grantham | Bulk Supply Point | 33 | -0.5889 | 52.9243 | WPD Best View | Headroom (MW) | Thermal | 39.19 | 38.81 | 38.43 | 37.97 | 37.01 | 36.01 | 31.67 | 22.57 | 14.92 | 7.13 | -1.74 | -11.03 | -21.12 | -31.22 | -43.1 | -80.81 | -127.29 | -177.4
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Consumer Transformation | Headroom (MW) | Thermal | 45.58 | 45.07 | 44.52 | 44.33 | 43 | 41.25 | 39.1 | 35.79 | 32.83 | 29.6 | 25.81 | 21.77 | 17.49 | 13.21 | 8.39 | -13.47 | -39.89 | -66.18
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Leading the Way | Headroom (MW) | Thermal | 45.58 | 45 | 44.44 | 44 | 42.3 | 40.35 | 37.96 | 35.65 | 33.81 | 31.34 | 28.9 | 26.39 | 22.32 | 18.13 | 13.8 | -11.1 | -39.97 | -69.88
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | Steady Progression | Headroom (MW) | N/A | 45.58 | 45.39 | 45.48 | 45.84 | 46.05 | 46.03 | 46.03 | 45.59 | 45.24 | 44.22 | 43.55 | 42.79 | 41.37 | 40.02 | 38.4 | 36.17 | 32.27 | 26.85
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | System Transformation | Headroom (MW) | Thermal | 45.58 | 45.25 | 45.13 | 45.15 | 44.9 | 44.16 | 43.41 | 41.92 | 39.96 | 38.01 | 35.56 | 32.86 | 30.09 | 27.64 | 24.8 | 15.24 | 2.31 | -13.4
Drakelow 132kV | Gresley | Gresley | Bulk Supply Point | 33 | -1.5897 | 52.7585 | WPD Best View | Headroom (MW) | Thermal | 45.58 | 45.09 | 44.56 | 44.39 | 43.14 | 41.48 | 39.42 | 36.19 | 33.33 | 30.2 | 26.46 | 22.5 | 18.32 | 14.1 | 9.38 | -11.38 | -37.12 | -62.46
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Consumer Transformation | Headroom (MW) | N/A | 63.7 | 63.67 | 63.24 | 63.12 | 62.7 | 62.25 | 61.81 | 60.57 | 59.14 | 57.56 | 55.73 | 53.63 | 51.35 | 49.25 | 46.62 | 39.82 | 31.93 | 22.64
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Leading the Way | Headroom (MW) | N/A | 63.7 | 63.68 | 63.28 | 63.16 | 62.65 | 62.14 | 61.63 | 61.15 | 60.67 | 60.2 | 59.76 | 59.3 | 57.45 | 55.63 | 53.67 | 46.22 | 36.63 | 29.79
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | Steady Progression | Headroom (MW) | N/A | 63.7 | 63.75 | 63.87 | 63.52 | 63.58 | 63.35 | 63.32 | 63.07 | 62.81 | 62.47 | 62.05 | 61.56 | 60.44 | 59.34 | 57.86 | 56.06 | 53.52 | 50.62
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | System Transformation | Headroom (MW) | N/A | 63.7 | 63.72 | 63.83 | 63.36 | 63.27 | 63.09 | 62.65 | 61.62 | 60.35 | 58.93 | 57.28 | 55.35 | 53.26 | 51.4 | 49.07 | 45.21 | 39.54 | 32.89
Berkswell 132kV | Harbury | Harbury | Bulk Supply Point | 33 | -1.4329 | 52.2278 | WPD Best View | Headroom (MW) | N/A | 63.7 | 63.75 | 63.87 | 63.52 | 63.57 | 63.33 | 63.25 | 62.95 | 62.66 | 62.27 | 61.84 | 61.33 | 60.2 | 59.08 | 57.58 | 55.5 | 52.91 | 49.92
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Consumer Transformation | Headroom (MW) | Thermal | 53.17 | 52.32 | 51.72 | 43.71 | 41.45 | 38.79 | 34.74 | 25.66 | 16.1 | 5.75 | -6.88 | -20.88 | -35.67 | -49.58 | -65.82 | -112.66 | -164.1 | -226.49
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Leading the Way | Headroom (MW) | Thermal | 53.17 | 52.37 | 51.68 | 43.62 | 41.15 | 37.86 | 33.5 | 29.23 | 25.1 | 20.8 | 16.93 | 13.13 | 1.12 | -10.62 | -22.3 | -72.48 | -129.98 | -174.02
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | Steady Progression | Headroom (MW) | Thermal | 53.17 | 52.82 | 52.75 | 45.47 | 45.28 | 44.98 | 43.91 | 41.82 | 39.61 | 36.38 | 33.35 | 29.82 | 22.76 | 15.94 | 6.99 | -4.42 | -17.98 | -33.48
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | System Transformation | Headroom (MW) | Thermal | 53.17 | 52.64 | 52.27 | 44.72 | 43.9 | 42.92 | 41.32 | 35.24 | 26.96 | 18.86 | 8.51 | -3.27 | -15.77 | -26.96 | -40.95 | -65.81 | -99.16 | -140.61
Staythorpe 132kV | Hawton | Hawton | Bulk Supply Point | 33 | -0.805 | 53.0506 | WPD Best View | Headroom (MW) | Thermal | 53.17 | 52.33 | 51.75 | 43.76 | 41.56 | 38.93 | 34.91 | 26.09 | 16.86 | 6.88 | -5.27 | -18.72 | -33.1 | -46.72 | -62.65 | -108.31 | -158.7 | -219.65
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Consumer Transformation | Headroom (MW) | Thermal | 63.89 | 63.01 | 62.31 | 61.13 | 58.94 | 57.04 | 54.27 | 51 | 47.8 | 44.84 | 41.62 | 38.36 | 34.96 | 31.58 | 27.72 | 8.6 | -12.16 | -36.19
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Leading the Way | Headroom (MW) | Thermal | 63.89 | 62.94 | 62.18 | 60.95 | 58.46 | 56.45 | 54.22 | 52.05 | 49.94 | 48.27 | 46.41 | 44.55 | 41.34 | 37.95 | 34.24 | 12.19 | -0.59 | -47.97
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | Steady Progression | Headroom (MW) | N/A | 63.89 | 63.37 | 63.09 | 62.83 | 62.49 | 62.21 | 60.69 | 59.01 | 57.4 | 55.88 | 54.38 | 53.02 | 51.51 | 50.06 | 48.44 | 46.26 | 42.2 | 36.26
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | System Transformation | Headroom (MW) | N/A | 63.89 | 63.21 | 62.74 | 62.24 | 61.37 | 60.68 | 58.96 | 56.79 | 54.38 | 52.24 | 49.85 | 47.48 | 45.09 | 42.99 | 40.45 | 32.45 | 33.21 | 7.43
Willington 132kV | Heanor | Heanor | Bulk Supply Point | 33 | -1.3627 | 53.0213 | WPD Best View | Headroom (MW) | Thermal | 63.89 | 63.01 | 62.31 | 61.13 | 58.93 | 57.03 | 54.26 | 51 | 47.79 | 44.83 | 41.61 | 38.35 | 34.95 | 31.57 | 27.71 | 8.6 | -12.16 | -36.19
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Consumer Transformation | Headroom (MW) | Thermal | 41.77 | 41.5 | 41.22 | 40.88 | 39.99 | 39.25 | 38.52 | 37.41 | 36.23 | 34.96 | 33.4 | 31.66 | 29.78 | 27.97 | 25.83 | 18.01 | 8.24 | -1.98
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Leading the Way | Headroom (MW) | Thermal | 41.77 | 41.47 | 41.18 | 40.81 | 39.85 | 39.07 | 38.3 | 37.6 | 36.98 | 36.32 | 35.55 | 34.76 | 33.07 | 31.33 | 29.45 | 19.79 | 7.49 | -3.08
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | Steady Progression | Headroom (MW) | N/A | 41.77 | 41.66 | 41.62 | 41.58 | 41.53 | 41.45 | 41.37 | 41.19 | 41.05 | 40.84 | 40.57 | 40.26 | 39.56 | 38.88 | 37.98 | 36.94 | 35.38 | 32.91
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | System Transformation | Headroom (MW) | N/A | 41.77 | 41.58 | 41.44 | 41.28 | 40.96 | 40.66 | 40.32 | 39.58 | 38.76 | 37.84 | 36.63 | 35.26 | 33.82 | 32.52 | 30.91 | 26.94 | 20.76 | 14.86
Coventry 132kV | Hinckley 33 | Hinckley 33 | Bulk Supply Point | 33 | -1.3953 | 52.5287 | WPD Best View | Headroom (MW) | Thermal | 41.77 | 41.5 | 41.22 | 40.88 | 39.99 | 39.25 | 38.52 | 37.41 | 36.23 | 34.96 | 33.4 | 31.66 | 29.78 | 27.97 | 25.83 | 18.01 | 8.24 | -1.98
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Consumer Transformation | Headroom (MW) | Thermal | 74.38 | -32.52 | -33.11 | -33.8 | -35.52 | -37.11 | -39.9 | -45.41 | -50.64 | -56.03 | -61.88 | -68.11 | -74.65 | -81.07 | -88.62 | -155.09 | -187.86 | -224.56
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Leading the Way | Headroom (MW) | Thermal | 74.38 | -32.56 | -33.17 | -33.86 | -35.76 | -37.43 | -40.48 | -43.1 | -45.53 | -48.33 | -51.12 | -53.85 | -59.43 | -65.1 | -71.19 | -142.14 | -176.89 | -210.13
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | Steady Progression | Headroom (MW) | Thermal | 74.38 | -19.96 | -20.09 | -20.28 | -32.87 | -33.1 | -33.33 | -33.86 | -34.62 | -36.54 | -37.52 | -38.69 | -41.12 | -43.45 | -46.48 | -50.39 | -71.11 | -78.28
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | System Transformation | Headroom (MW) | Thermal | 74.38 | -32.38 | -32.63 | -33.14 | -33.81 | -34.3 | -34.9 | -37.04 | -41.03 | -44.53 | -48.52 | -52.9 | -57.48 | -61.54 | -66.47 | -101.7 | -118.41 | -137.22
Grendon 132kV | Irthlingborough | Irthlingborough | Bulk Supply Point | 33 | -0.614 | 52.3189 | WPD Best View | Headroom (MW) | Thermal | 74.38 | -32.41 | -32.85 | -33.3 | -34.13 | -34.92 | -36.21 | -38.59 | -42.23 | -45.74 | -49.53 | -53.62 | -58.49 | -62.98 | -68.22 | -107.46 | -128.37 | -150.25
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Consumer Transformation | Headroom (MW) | Thermal | 77.11 | 66.31 | 66.32 | 66.04 | 64.75 | 62.23 | 59.61 | 55.24 | 50.63 | 45.97 | 40.57 | 34.64 | 28.36 | 22.39 | 15.24 | -5.96 | -32.45 | -63.1
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Leading the Way | Headroom (MW) | Thermal | 77.11 | 66.3 | 66.38 | 66.18 | 63.74 | 62.29 | 60.15 | 58.08 | 56.11 | 54.62 | 52.73 | 50.82 | 45.43 | 40.03 | 34.21 | 9.35 | -15.3 | -42.28
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | Steady Progression | Headroom (MW) | N/A | 77.11 | 66.6 | 66.98 | 67.27 | 61.84 | 61.95 | 60.17 | 57.95 | 55.82 | 53.64 | 51.41 | 49.22 | 46.25 | 43.14 | 39.33 | 34.72 | 28.02 | 18.79
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | System Transformation | Headroom (MW) | Thermal | 77.11 | 66.51 | 66.79 | 66.89 | 66.71 | 66.49 | 64.14 | 61.08 | 57.26 | 53.42 | 48.86 | 43.82 | 38.58 | 33.84 | 28.05 | 16.9 | 1.21 | -19.59
Grendon 132kV | Kettering | Kettering | Bulk Supply Point | 33 | -0.7381 | 52.4017 | WPD Best View | Headroom (MW) | Thermal | 77.11 | 66.39 | 66.55 | 66.49 | 65.46 | 63.27 | 60.77 | 57.67 | 54.51 | 51.62 | 48.22 | 44.66 | 39 | 33.54 | 27.31 | 5.42 | -21.89 | -51.94
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Consumer Transformation | Headroom (MW) | Thermal | 61.97 | 61.61 | 61.31 | 60.9 | 59.93 | 59.01 | 58.12 | 55 | 51.38 | 47.42 | 41.95 | 35.5 | 28.47 | 22.01 | 14.02 | -2.78 | -22.86 | -47.24
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Leading the Way | Headroom (MW) | Thermal | 61.97 | 61.59 | 61.26 | 60.83 | 59.79 | 58.77 | 57.77 | 56.82 | 55.92 | 55.27 | 54.51 | 53.55 | 48.19 | 42.98 | 37.35 | 17.96 | -7.3 | -21.2
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | Steady Progression | Headroom (MW) | N/A | 61.97 | 61.8 | 61.72 | 61.64 | 61.55 | 61.43 | 61.3 | 60.59 | 59.92 | 59.11 | 57.98 | 56.49 | 52.97 | 49.49 | 44.77 | 38.86 | 31.92 | 24.1
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | System Transformation | Headroom (MW) | Thermal | 61.97 | 61.71 | 61.53 | 61.34 | 60.96 | 60.62 | 60.22 | 57.54 | 54.15 | 50.58 | 45.56 | 39.53 | 33.03 | 27.19 | 19.9 | 8.24 | -7.84 | -27.36
Grendon 132kV | Kibworth | Kibworth | Bulk Supply Point | 33 | -1.0237 | 52.537 | WPD Best View | Headroom (MW) | Thermal | 61.97 | 61.62 | 61.31 | 60.9 | 59.95 | 59.03 | 58.15 | 55.34 | 52.08 | 48.55 | 43.63 | 37.81 | 31.02 | 24.71 | 17.01 | 0.12 | -20.35 | -43.32
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Consumer Transformation | Headroom (MW) | N/A | 107.19 | 106.47 | 106.09 | 105.66 | 104.48 | 103.32 | 101.97 | 100.35 | 98.81 | 97.21 | 95.61 | 93.78 | 91.88 | 90.03 | 88.13 | 74.95 | 58.3 | 39.75
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Leading the Way | Headroom (MW) | N/A | 107.19 | 106.42 | 106.02 | 105.55 | 104.05 | 102.82 | 101.42 | 99.76 | 98.14 | 96.4 | 94.6 | 92.41 | 90.14 | 87.95 | 85.67 | 71.16 | 52.34 | 27.79
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | Steady Progression | Headroom (MW) | N/A | 107.19 | 106.62 | 106.37 | 106.1 | 105.73 | 105.52 | 105.32 | 105.18 | 105.07 | 104.94 | 104.82 | 104.62 | 104.44 | 104.24 | 104.03 | 102.98 | 100.86 | 98.23
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | System Transformation | Headroom (MW) | N/A | 107.19 | 106.56 | 106.26 | 105.91 | 105.32 | 105.05 | 104.75 | 104.4 | 103.89 | 103.32 | 102.64 | 101.74 | 100.89 | 100.2 | 99.55 | 95.97 | 87.94 | 79.43
Enderby 132kV | Leicester | Leicester | Bulk Supply Point | 33 | -1.1416 | 52.623 | WPD Best View | Headroom (MW) | N/A | 107.19 | 106.47 | 106.09 | 105.66 | 104.48 | 103.33 | 101.99 | 100.37 | 98.84 | 97.25 | 95.66 | 93.83 | 91.94 | 90.09 | 88.21 | 75.25 | 58.67 | 40.21
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Consumer Transformation | Headroom (MW) | Thermal | 98.02 | 96.97 | 96.26 | 95.41 | 93.08 | 90.87 | 88.5 | 85.92 | 83.36 | 80.84 | 78.31 | 75.7 | 72.95 | 70.18 | 67.04 | 46.7 | 24.32 | -0.22
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Leading the Way | Headroom (MW) | Thermal | 98.02 | 96.89 | 96.13 | 95.21 | 92.48 | 90.07 | 87.48 | 84.88 | 82.29 | 79.74 | 77.36 | 74.95 | 71.83 | 68.6 | 65.03 | 45.02 | 13.16 | -18.15
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | Steady Progression | Headroom (MW) | N/A | 98.02 | 97.29 | 96.92 | 96.53 | 96.04 | 95.77 | 95.4 | 94.96 | 94.58 | 94.14 | 93.64 | 93.15 | 92.43 | 91.78 | 90.98 | 89.16 | 85.71 | 80.77
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | System Transformation | Headroom (MW) | N/A | 98.02 | 97.13 | 96.62 | 96.05 | 95.07 | 94.33 | 93.27 | 91.91 | 90.33 | 88.78 | 87.22 | 85.64 | 84.06 | 82.58 | 80.95 | 75.18 | 60.11 | 48.62
Enderby 132kV | Leicester East | Leicester East | Bulk Supply Point | 33 | -1.1013 | 52.6297 | WPD Best View | Headroom (MW) | N/A | 98.02 | 96.98 | 96.28 | 95.43 | 93.2 | 91.06 | 88.74 | 86.21 | 83.69 | 81.2 | 78.74 | 76.16 | 73.47 | 70.77 | 67.68 | 47.94 | 26.02 | 2.05
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Consumer Transformation | Headroom (MW) | N/A | 71.99 | 71.42 | 71.18 | 70.84 | 69.58 | 68.48 | 67.74 | 66.89 | 65.88 | 64.75 | 63.64 | 62.42 | 61.14 | 59.76 | 58.34 | 47.59 | 33.4 | 18.1
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Leading the Way | Headroom (MW) | N/A | 71.99 | 71.38 | 71.15 | 70.89 | 69.49 | 68.4 | 67.75 | 66.93 | 65.79 | 64.41 | 63.03 | 61.54 | 59.91 | 58.14 | 56.23 | 45.2 | 27.41 | 2.72
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | Steady Progression | Headroom (MW) | N/A | 71.99 | 71.71 | 71.82 | 71.96 | 72.11 | 72.12 | 72.18 | 72.26 | 72.25 | 72.17 | 72.11 | 72.06 | 72 | 71.94 | 71.9 | 71.91 | 70.07 | 67
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | System Transformation | Headroom (MW) | N/A | 71.99 | 71.59 | 71.59 | 71.55 | 71.29 | 70.97 | 70.86 | 70.61 | 70.24 | 69.77 | 69.34 | 68.9 | 68.49 | 68.12 | 67.75 | 66.11 | 58.77 | 49.51
Enderby 132kV | Leicester North | Leicester North | Bulk Supply Point | 33 | -1.1433 | 52.6467 | WPD Best View | Headroom (MW) | N/A | 71.99 | 71.42 | 71.18 | 70.84 | 69.58 | 68.48 | 67.74 | 66.89 | 65.88 | 64.75 | 63.64 | 62.42 | 61.14 | 59.76 | 58.34 | 47.59 | 33.4 | 18.1
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Consumer Transformation | Headroom (MW) | Thermal | 144.67 | 143.26 | 136.39 | 134.37 | 130.74 | 127.59 | 121.57 | 109.69 | 98.43 | 86.77 | 73.32 | 58.89 | 43.72 | 28.82 | 11.21 | -43.47 | -111.39 | -186.97
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Leading the Way | Headroom (MW) | Thermal | 144.67 | 143.34 | 136.45 | 134.39 | 130.52 | 127.17 | 121.04 | 115.25 | 110.17 | 104.28 | 98.51 | 92.89 | 80.27 | 67.58 | 53.93 | -3.56 | -74.11 | -135.65
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | Steady Progression | Headroom (MW) | N/A | 144.67 | 143.9 | 138.4 | 138.08 | 137.71 | 137.33 | 136.35 | 134.41 | 132.12 | 127.69 | 124.79 | 121.55 | 115.28 | 109.44 | 101.98 | 92.27 | 79.6 | 63.89
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | System Transformation | Headroom (MW) | Thermal | 144.67 | 143.6 | 137.73 | 136.51 | 135.18 | 133.91 | 132.09 | 126.47 | 117.89 | 109.86 | 100.15 | 89.55 | 78.48 | 68.59 | 56.35 | 31.96 | -3.5 | -43.58
West Burton 132kV | Lincoln 33 | Lincoln 33 | Bulk Supply Point | 33 | -0.5186 | 53.2284 | WPD Best View | Headroom (MW) | N/A | 144.67 | 143.8 | 138.2 | 137.7 | 137.03 | 136.32 | 134.93 | 132.08 | 128.77 | 123.18 | 118.93 | 114.19 | 106.81 | 100.03 | 91.55 | 77.34 | 57.99 | 36.87
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Consumer Transformation | Headroom (MW) | Thermal | 53.59 | 53.31 | 53.27 | 43.93 | 42.88 | 41.9 | 40.26 | 37.41 | 35.32 | 33.4 | 31.26 | 29.04 | 26.69 | 24.35 | 21.61 | 10.7 | -2.37 | -17.45
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Leading the Way | Headroom (MW) | Thermal | 53.59 | 53.29 | 53.29 | 43.97 | 42.77 | 40.92 | 39.63 | 38.4 | 37.15 | 36.15 | 35.02 | 33.88 | 31.69 | 29.43 | 26.94 | 14.67 | 3.86 | -8.64
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | Steady Progression | Headroom (MW) | N/A | 53.59 | 53.5 | 53.71 | 44.63 | 44.58 | 44.57 | 43.64 | 42.61 | 41.61 | 39.82 | 38.79 | 37.88 | 36.85 | 35.95 | 34.91 | 33.93 | 31.24 | 27.63
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | System Transformation | Headroom (MW) | N/A | 53.59 | 53.44 | 53.56 | 44.45 | 44.12 | 43.84 | 42.87 | 40.6 | 39.02 | 37.6 | 36.04 | 34.44 | 32.81 | 31.36 | 29.56 | 25.4 | 18.55 | 10.73
Ratcliffe 132kV | Loughborough 33 | Loughborough 33 | Bulk Supply Point | 33 | -1.2097 | 52.7866 | WPD Best View | Headroom (MW) | Thermal | 53.59 | 53.31 | 53.27 | 43.93 | 42.88 | 41.9 | 40.26 | 37.41 | 35.32 | 33.4 | 31.26 | 29.04 | 26.69 | 24.35 | 21.61 | 10.7 | -2.37 | -17.45
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Consumer Transformation | Headroom (MW) | Thermal | 49.62 | 40.77 | 40.34 | 39.85 | 38.25 | 36.83 | 34.52 | 32.16 | 30.01 | 28.12 | 26.31 | 24.59 | 22.93 | 21.14 | 19.22 | 11.39 | -4.76 | -26.06
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Leading the Way | Headroom (MW) | Thermal | 49.62 | 40.74 | 40.29 | 39.81 | 37.96 | 36.44 | 34.64 | 32.78 | 31.06 | 29.67 | 23.17 | 21.44 | 19.49 | 17.35 | 24.01 | 16.59 | -27.06 | -48.53
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | Steady Progression | Headroom (MW) | N/A | 49.62 | 41.04 | 40.94 | 40.9 | 40.62 | 40.39 | 37.94 | 35.55 | 33.28 | 32.02 | 30.83 | 29.81 | 29.12 | 28.55 | 28.08 | 27.3 | 26.2 | 22.64
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | System Transformation | Headroom (MW) | Thermal | 49.62 | 40.93 | 40.7 | 40.5 | 39.79 | 39.29 | 37.85 | 36.48 | 35.19 | 34.11 | 29.93 | 29.03 | 28.27 | 27.57 | 27.82 | 30.03 | 3.58 | -4.71
Chesterfield 132kV | Mansfield | Mansfield | Bulk Supply Point | 33 | -1.1995 | 53.1558 | WPD Best View | Headroom (MW) | Thermal | 49.62 | 40.77 | 40.34 | 39.85 | 38.25 | 36.83 | 34.52 | 32.16 | 30.01 | 28.12 | 26.31 | 24.59 | 22.93 | 21.14 | 19.22 | 11.39 | -4.76 | -26.06
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Consumer Transformation | Headroom (MW) | Thermal | 28.3 | 27.83 | 26.94 | 26.4 | 25.3 | 23.98 | 20.6 | 13.22 | 6.42 | -0.72 | -9.03 | -18.02 | -27.4 | -36.52 | -47.44 | -80.22 | -121.2 | -164.75
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Leading the Way | Headroom (MW) | Thermal | 28.3 | 27.81 | 26.87 | 26.36 | 25.24 | 23.72 | 19.93 | 16.51 | 13.56 | 9.77 | 6.68 | 3.68 | -3.77 | -11.34 | -19.43 | -50.65 | -94.15 | -123.85
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | Steady Progression | Headroom (MW) | Thermal | 28.3 | 28.02 | 27.49 | 27.36 | 27.19 | 26.97 | 26.74 | 25.94 | 24.85 | 21.98 | 20.46 | 18.54 | 14.52 | 10.8 | 6.01 | -0.56 | -8.13 | -16.46
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | System Transformation | Headroom (MW) | Thermal | 28.3 | 27.93 | 27.23 | 26.97 | 26.51 | 25.91 | 25.2 | 22.27 | 16.93 | 12.23 | 6.34 | -0.3 | -7.31 | -13.53 | -21.17 | -35.5 | -57.27 | -80.59
Grendon 132kV | Melton Mowbray | Melton Mowbray | Bulk Supply Point | 33 | -0.8698 | 52.7647 | WPD Best View | Headroom (MW) | Thermal | 28.3 | 27.83 | 26.96 | 26.44 | 25.37 | 24.08 | 21.24 | 14.86 | 8.34 | 1.7 | -6.13 | -14.64 | -23.54 | -32.09 | -42.37 | -72 | -109.12 | -148.75
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Consumer Transformation | Headroom (MW) | N/A | 73.08 | 72.46 | 72.47 | 71.81 | 70.35 | 69.27 | 68.12 | 66.22 | 64.24 | 62.13 | 59.75 | 57.13 | 54.38 | 51.72 | 48.55 | 37.3 | 24.03 | 9.51
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Leading the Way | Headroom (MW) | N/A | 73.08 | 72.43 | 72.44 | 71.73 | 69.99 | 68.83 | 67.6 | 66.41 | 65.25 | 64.13 | 62.95 | 61.75 | 59.27 | 56.77 | 54.02 | 44.51 | 23.8 | 5.12
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | Steady Progression | Headroom (MW) | N/A | 73.08 | 72.64 | 72.81 | 72.6 | 72.3 | 72.05 | 71.77 | 71.39 | 71.02 | 70.59 | 69.99 | 69.34 | 68.14 | 67 | 65.51 | 63.27 | 60.25 | 56.13
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | System Transformation | Headroom (MW) | N/A | 73.08 | 72.57 | 72.71 | 72.4 | 71.79 | 71.32 | 70.73 | 69.44 | 67.96 | 66.36 | 64.51 | 62.43 | 60.23 | 58.27 | 55.9 | 52.38 | 41.31 | 30.33
Grendon 132kV | Northampton | Northampton | Bulk Supply Point | 33 | -0.8835 | 52.2301 | WPD Best View | Headroom (MW) | N/A | 73.08 | 72.43 | 72.44 | 71.73 | 69.99 | 68.83 | 67.6 | 66.41 | 65.25 | 64.13 | 62.95 | 61.75 | 59.27 | 56.77 | 54.02 | 44.51 | 23.8 | 5.12
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Consumer Transformation | Headroom (MW) | Thermal | 70.56 | 69.86 | 69.24 | 68.25 | 66.37 | 64.67 | 62.3 | 57.31 | 52.33 | 47.02 | 41.12 | 34.58 | 27.6 | 20.89 | 12.86 | -11.89 | -42.22 | -76.62
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Leading the Way | Headroom (MW) | Thermal | 70.56 | 69.8 | 69.18 | 68.14 | 66.05 | 64.22 | 61.65 | 59.29 | 57.21 | 54.92 | 52.69 | 50.46 | 44.76 | 38.96 | 32.64 | 6.36 | -27.07 | -56.62
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | Steady Progression | Headroom (MW) | N/A | 70.56 | 70.18 | 70.03 | 69.88 | 69.63 | 69.39 | 69.13 | 68.36 | 67.51 | 65.89 | 64.71 | 63.29 | 60.28 | 57.39 | 53.65 | 48.7 | 42.51 | 34.75
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | System Transformation | Headroom (MW) | Thermal | 70.56 | 70.05 | 69.68 | 69.31 | 68.58 | 67.91 | 67.09 | 64.25 | 60.23 | 56.19 | 51.59 | 46.43 | 41 | 36.19 | 30.2 | 18.42 | 1.66 | -17.47
Grendon 132kV | Northampton East | Northampton East | Bulk Supply Point | 33 | -0.8368 | 52.2431 | WPD Best View | Headroom (MW) | Thermal | 70.56 | 69.86 | 69.29 | 68.63 | 66.82 | 65.25 | 63.73 | 61.95 | 59.53 | 57.49 | 55.22 | 52.85 | 47.63 | 42.52 | 36.79 | 15.62 | -11.52 | -36.31
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Consumer Transformation | Headroom (MW) | N/A | 79.29 | 79.09 | 78.7 | 78.25 | 76.91 | 75.55 | 74.06 | 72.39 | 70.72 | 69.01 | 67.2 | 65.31 | 63.28 | 61.34 | 59.21 | 46.67 | 29.38 | 10.88
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Leading the Way | Headroom (MW) | N/A | 79.29 | 79.09 | 78.73 | 78.21 | 76.55 | 75.06 | 73.49 | 71.98 | 70.51 | 69.02 | 67.4 | 65.72 | 63.55 | 61.46 | 59.12 | 44.63 | 23.97 | 0.28
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | Steady Progression | Headroom (MW) | N/A | 79.29 | 79.28 | 79.37 | 79.32 | 79.1 | 78.89 | 78.71 | 78.45 | 78.17 | 77.83 | 77.47 | 77.11 | 76.55 | 76.02 | 75.41 | 73.99 | 71.48 | 67.73
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | System Transformation | Headroom (MW) | N/A | 79.29 | 79.22 | 79.22 | 78.81 | 78.21 | 77.78 | 77.28 | 76.5 | 75.46 | 74.36 | 73.19 | 71.97 | 70.72 | 69.66 | 68.51 | 64.11 | 55.43 | 46.99
Grendon 132kV | Northampton West | Northampton West | Bulk Supply Point | 33 | -0.9134 | 52.245 | WPD Best View | Headroom (MW) | N/A | 79.29 | 79.1 | 78.74 | 78.24 | 76.6 | 75.12 | 73.56 | 72.06 | 70.59 | 69.12 | 67.51 | 65.83 | 63.67 | 61.58 | 59.26 | 44.83 | 24.24 | 0.67
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Consumer Transformation | Headroom (MW) | Thermal | 50.83 | 50.15 | 49.64 | 49.32 | 48.42 | 46.87 | 44.48 | 42.24 | 40.34 | 38.7 | 37.13 | 35.58 | 34.08 | 32.49 | 30.79 | 15.19 | 5.91 | -18.63
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Leading the Way | Headroom (MW) | Thermal | 50.83 | 50.09 | 49.56 | 49.26 | 48.2 | 46.7 | 44.76 | 42.92 | 41.37 | 40.04 | 38.46 | 36.75 | 34.95 | 32.99 | 40.59 | 12.03 | -1.58 | -35.24
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | Steady Progression | Headroom (MW) | N/A | 50.83 | 50.38 | 50.13 | 50.13 | 50.08 | 49.92 | 48.51 | 47.11 | 45.8 | 44.57 | 43.42 | 42.45 | 41.86 | 41.37 | 41.02 | 40.12 | 38.21 | 35.49
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | System Transformation | Headroom (MW) | N/A | 50.83 | 50.27 | 49.91 | 49.82 | 49.49 | 49.13 | 47.84 | 46.57 | 45.43 | 44.43 | 43.57 | 42.93 | 42.42 | 41.96 | 43.76 | 31.66 | 29.6 | 16.31
Stoke Bardolph 132kV | Nottingham East | Nottingham East | Bulk Supply Point | 33 | -1.1023 | 52.9655 | WPD Best View | Headroom (MW) | Thermal | 50.83 | 50.13 | 49.61 | 49.35 | 48.4 | 46.92 | 44.46 | 42.13 | 40.12 | 38.38 | 36.71 | 35.06 | 33.45 | 31.72 | 29.8 | 13.42 | 3.11 | -24.07
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Consumer Transformation | Headroom (MW) | Thermal | 79.31 | 78.4 | 77.77 | 76.83 | 74.75 | 73.01 | 71.25 | 69.2 | 67.29 | 65.55 | 63.92 | 62.21 | 60.44 | 58.51 | 56.44 | 41.16 | 19.72 | -4.38
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Leading the Way | Headroom (MW) | Thermal | 79.31 | 78.33 | 77.68 | 76.73 | 74.44 | 72.61 | 70.68 | 68.5 | 66.42 | 64.56 | 62.62 | 60.58 | 58.41 | 55.92 | 53.12 | 34.46 | 9.75 | -23.24
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | Steady Progression | Headroom (MW) | N/A | 79.31 | 78.78 | 78.7 | 78.54 | 78.38 | 78.1 | 77.77 | 77.4 | 77.06 | 76.71 | 76.38 | 76.12 | 75.9 | 75.69 | 75.53 | 74.84 | 72.04 | 67.62
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | System Transformation | Headroom (MW) | N/A | 79.31 | 78.59 | 78.31 | 77.86 | 77.09 | 76.33 | 75.4 | 74.46 | 73.57 | 72.79 | 72.1 | 71.47 | 70.89 | 70.35 | 69.77 | 65.49 | 55.04 | 44.77
Stoke Bardolph 132kV | Nottingham North 33 | Nottingham North 33 | Bulk Supply Point | 33 | -1.1742 | 52.9784 | WPD Best View | Headroom (MW) | Thermal | 79.31 | 78.35 | 77.69 | 76.72 | 74.46 | 72.64 | 70.78 | 68.7 | 66.69 | 64.93 | 63.13 | 61.25 | 59.24 | 56.98 | 54.48 | 37.11 | 13.66 | -15.95
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Consumer Transformation | Headroom (MW) | Thermal | 73.73 | 73.27 | 72.88 | 71.99 | 70.66 | 69.05 | 67.14 | 64.8 | 62.63 | 60.45 | 58.08 | 55.66 | 53.15 | 51.11 | 45.19 | 31.12 | 10.08 | -11.38
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Leading the Way | Headroom (MW) | Thermal | 73.73 | 73.22 | 72.81 | 71.89 | 70.39 | 68.65 | 66.65 | 64.75 | 62.96 | 61.09 | 59.07 | 57.11 | 54.57 | 53.71 | 44.38 | 27.64 | 5.56 | -19.63
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | Steady Progression | Headroom (MW) | N/A | 73.73 | 73.44 | 73.39 | 73.3 | 73.36 | 73.21 | 72.92 | 72.55 | 72.18 | 71.57 | 71.14 | 70.69 | 70.1 | 69.54 | 68.87 | 67.64 | 64.92 | 61.04
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | System Transformation | Headroom (MW) | N/A | 73.73 | 73.37 | 73.2 | 72.98 | 72.61 | 72.1 | 71.43 | 70.36 | 69.01 | 67.81 | 66.47 | 65.05 | 63.72 | 62.94 | 57.37 | 52.74 | 43.5 | 33.35
Coventry 132kV | Nuneaton | Nuneaton | Bulk Supply Point | 33 | -1.4883 | 52.5116 | WPD Best View | Headroom (MW) | Thermal | 73.73 | 73.23 | 72.82 | 71.91 | 70.45 | 68.7 | 66.93 | 64.99 | 62.97 | 60.73 | 58.41 | 56.02 | 53.48 | 52.16 | 44.34 | 29.2 | 9.39 | -14.86
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Consumer Transformation | Headroom (MW) | Thermal | 42.69 | 42.23 | 41.87 | 41.44 | 40.43 | 39.55 | 38.67 | 36.01 | 33.01 | 29.66 | 25.37 | 20.52 | 15.31 | 10.45 | 4.52 | -9.55 | -27.67 | -48.26
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Leading the Way | Headroom (MW) | Thermal | 42.69 | 42.2 | 41.82 | 41.39 | 40.25 | 39.25 | 38.31 | 37.28 | 36.16 | 34.96 | 33.82 | 32.69 | 28.51 | 24.37 | 20.02 | 4.57 | -17.44 | -31.13
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | Steady Progression | Headroom (MW) | N/A | 42.69 | 42.4 | 42.25 | 42.1 | 41.92 | 41.74 | 41.7 | 41.22 | 40.69 | 39.87 | 38.98 | 37.87 | 35.35 | 32.9 | 29.61 | 25.53 | 20.49 | 14.54
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | System Transformation | Headroom (MW) | Thermal | 42.69 | 42.32 | 42.08 | 41.82 | 41.35 | 40.97 | 40.76 | 38.88 | 36.24 | 33.49 | 29.78 | 25.51 | 20.92 | 16.8 | 11.69 | 3.46 | -9.59 | -24.37
Grendon 132kV | Oakham | Oakham | Bulk Supply Point | 33 | -0.7096 | 52.6682 | WPD Best View | Headroom (MW) | Thermal | 42.69 | 42.32 | 42.05 | 41.77 | 41.25 | 40.8 | 40.31 | 38 | 35.2 | 32.22 | 28.28 | 23.8 | 19 | 14.62 | 9.21 | -0.86 | -15.7 | -32.37
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Consumer Transformation | Headroom (MW) | Thermal | 65.6 | 65.14 | 64.43 | 64.18 | 63.39 | 62.6 | 60.57 | 56.13 | 52.16 | 48.13 | 43.19 | 37.88 | 32.28 | 26.82 | 20.27 | -0.97 | -26.61 | -55.01
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Leading the Way | Headroom (MW) | Thermal | 65.6 | 65.13 | 64.44 | 64.2 | 63.38 | 62.6 | 60.44 | 58.6 | 57.07 | 55.08 | 53.12 | 51.22 | 46.79 | 42.31 | 37.48 | 17.22 | -8.48 | -29.44
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | Steady Progression | Headroom (MW) | N/A | 65.6 | 65.28 | 65.28 | 64.87 | 64.92 | 64.9 | 64.88 | 64.54 | 64.02 | 62.34 | 61.54 | 60.54 | 58.37 | 56.39 | 53.82 | 50.71 | 46.06 | 40.52
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | System Transformation | Headroom (MW) | N/A | 65.6 | 65.22 | 65.13 | 64.63 | 64.44 | 64.16 | 63.85 | 62.39 | 59.45 | 56.96 | 53.62 | 49.89 | 45.94 | 42.48 | 38.19 | 29.61 | 17.25 | 2.88
Coventry 132kV | Pailton | Pailton | Bulk Supply Point | 33 | -1.2763 | 52.4387 | WPD Best View | Headroom (MW) | Thermal | 65.6 | 65.14 | 64.47 | 64.25 | 63.52 | 62.8 | 62.14 | 60.48 | 58.37 | 55.02 | 52.08 | 48.68 | 44.68 | 41.06 | 36.61 | 25.02 | 12.1 | -2.9
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Consumer Transformation | Headroom (MW) | Thermal | 70.07 | 69.75 | 69.52 | 69.26 | 68.55 | 67.37 | 61.43 | 57.5 | 55.25 | 53.03 | 50.27 | 47.3 | 44.19 | 41.09 | 37.48 | 23.38 | 5.02 | -15.83
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Leading the Way | Headroom (MW) | Thermal | 70.07 | 69.72 | 69.47 | 69.17 | 63.93 | 61 | 59.31 | 57.68 | 56.16 | 54.66 | 53 | 50.38 | 47.5 | 44.56 | 41.34 | 25.31 | 5.66 | -16.06
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | Steady Progression | Headroom (MW) | N/A | 70.07 | 69.84 | 69.72 | 69.6 | 69.46 | 69.37 | 69.3 | 69.22 | 64.93 | 62.83 | 62.49 | 62.11 | 61.14 | 60.21 | 58.96 | 57.16 | 54.45 | 50.44
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | System Transformation | Headroom (MW) | N/A | 70.07 | 69.79 | 69.63 | 69.45 | 69.19 | 69.09 | 64.58 | 61.98 | 60.52 | 59.21 | 57.4 | 55.42 | 53.34 | 51.46 | 49.19 | 43.62 | 33.62 | 22.6
Coventry 132kV | Rugby | Rugby | Bulk Supply Point | 33 | -1.2617 | 52.3882 | WPD Best View | Headroom (MW) | N/A | 70.07 | 69.84 | 69.71 | 69.58 | 69.42 | 69.32 | 68.99 | 68.39 | 63.77 | 61.34 | 60.32 | 59.24 | 57.8 | 56.39 | 54.61 | 50.55 | 44.89 | 37.64
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Consumer Transformation | Headroom (MW) | Thermal | 52.96 | 51.95 | 51.03 | 50.18 | 47.93 | 45.9 | 42.49 | 38.36 | 33.9 | 29.05 | 23.54 | 17.43 | 10.93 | 4.79 | -2.81 | -25.52 | -50.54 | -80.2
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Leading the Way | Headroom (MW) | Thermal | 52.96 | 51.84 | 50.95 | 50.03 | 47.64 | 45.16 | 41.48 | 38.67 | 35.86 | 32.93 | 30.5 | 28.13 | 22.4 | 16.79 | 10.71 | -14.98 | -45.98 | -72.5
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | Steady Progression | Headroom (MW) | N/A | 52.96 | 52.25 | 51.92 | 51.61 | 51.21 | 50.77 | 50.34 | 49.42 | 48.55 | 47.54 | 46.35 | 45.04 | 42.31 | 39.66 | 36.17 | 31.38 | 25.22 | 17.21
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | System Transformation | Headroom (MW) | Thermal | 52.96 | 52.11 | 51.6 | 50.94 | 49.91 | 48.84 | 47.15 | 44.14 | 40.65 | 36.92 | 32.54 | 27.76 | 22.56 | 17.83 | 11.74 | 0.25 | -16.27 | -35.71
Bicker Fen 132kV | Skegness | Skegness | Bulk Supply Point | 33 | 0.2613 | 53.1409 | WPD Best View | Headroom (MW) | Thermal | 52.96 | 52.12 | 51.61 | 50.97 | 49.97 | 48.93 | 47.28 | 44.33 | 40.87 | 37.19 | 32.82 | 28.07 | 22.88 | 18.17 | 12.09 | 0.73 | -15.56 | -34.84
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Consumer Transformation | Headroom (MW) | Thermal | 58.91 | 58.19 | 57.59 | 56.86 | 55.22 | 53.76 | 51.67 | 47.59 | 43.37 | 38.88 | 33.76 | 28.15 | 22.2 | 16.44 | 9.5 | -10.51 | -34.28 | -61.28
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Leading the Way | Headroom (MW) | Thermal | 58.91 | 58.16 | 57.52 | 56.76 | 54.99 | 53.37 | 51.03 | 48.7 | 46.51 | 44.09 | 42.12 | 40.12 | 35.09 | 30.14 | 24.81 | 3.74 | -22.97 | -45
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | Steady Progression | Headroom (MW) | N/A | 58.91 | 58.47 | 58.23 | 58.04 | 57.78 | 57.53 | 57.25 | 56.57 | 55.81 | 54.56 | 53.47 | 52.2 | 49.54 | 47 | 43.65 | 39.22 | 33.74 | 26.89
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | System Transformation | Headroom (MW) | Thermal | 58.91 | 58.34 | 57.96 | 57.55 | 56.84 | 56.14 | 55.25 | 52.79 | 49.5 | 46.11 | 42.06 | 37.54 | 32.72 | 28.42 | 23.06 | 13.21 | -1.11 | -17.56
Bicker Fen 132kV | Sleaford | Sleaford | Bulk Supply Point | 33 | -0.4053 | 52.9917 | WPD Best View | Headroom (MW) | N/A | 58.91 | 58.43 | 58.13 | 57.85 | 57.39 | 56.98 | 56.5 | 55.59 | 54.64 | 53.19 | 51.93 | 50.51 | 47.71 | 45.01 | 41.49 | 35.96 | 28.95 | 20.9
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Consumer Transformation | Headroom (MW) | Thermal | 81.04 | 80.78 | 80.25 | 82.14 | 80.55 | 78.46 | 76.39 | 73.45 | 70.71 | 67.59 | 63.46 | 58.92 | 53.97 | 49.22 | 43.83 | 24.06 | -1.69 | -31.49
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Leading the Way | Headroom (MW) | Thermal | 81.04 | 80.77 | 80.22 | 82.76 | 81.1 | 78.67 | 76.11 | 73.56 | 71.61 | 69.35 | 66.7 | 64.04 | 59.39 | 54.73 | 51.88 | 26.37 | -3.8 | -34.93
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | Steady Progression | Headroom (MW) | N/A | 81.04 | 80.9 | 80.74 | 82.74 | 83.17 | 83.11 | 83.03 | 82.84 | 82.71 | 82.32 | 81.76 | 81.1 | 79.57 | 77.88 | 75.72 | 72.62 | 69.37 | 62.44
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | System Transformation | Headroom (MW) | N/A | 81.04 | 80.87 | 80.62 | 82.72 | 82.81 | 82.22 | 81.38 | 79.48 | 77.59 | 75.57 | 72.64 | 69.33 | 65.83 | 62.67 | 58.89 | 51.21 | 35.56 | 18.1
Willington 132kV | Spondon | Spondon | Bulk Supply Point | 33 | -1.3983 | 52.9065 | WPD Best View | Headroom (MW) | Thermal | 81.04 | 80.78 | 80.25 | 82.14 | 80.55 | 78.46 | 76.39 | 73.45 | 70.71 | 67.59 | 63.46 | 58.92 | 53.97 | 49.22 | 43.83 | 24.06 | -1.69 | -31.49
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Consumer Transformation | Headroom (MW) | Thermal | 53.86 | 53.05 | 52.27 | 50.58 | 48.23 | 46.46 | 42.73 | 33.12 | 26.68 | 20.15 | 13.16 | 5.6 | -2.26 | -10 | -19.07 | -50.71 | -88.81 | -130.87
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Leading the Way | Headroom (MW) | Thermal | 53.86 | 52.97 | 52.18 | 50.47 | 47.88 | 43.64 | 39.67 | 36.02 | 32.69 | 28.52 | 25.07 | 21.69 | 15.12 | 8.39 | 1.14 | -29.77 | -68.97 | -104.71
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | Steady Progression | Headroom (MW) | N/A | 53.86 | 53.43 | 53.19 | 52.96 | 52.63 | 52.39 | 52.25 | 51.66 | 50.71 | 45.55 | 44.32 | 42.88 | 40.02 | 37.45 | 34.16 | 29.91 | 23.62 | 15.6
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | System Transformation | Headroom (MW) | Thermal | 53.86 | 53.27 | 52.8 | 52.3 | 51.3 | 50.55 | 49.83 | 45.15 | 40.59 | 36.79 | 32.18 | 27.22 | 22.05 | 17.48 | 11.77 | -0.05 | -18.24 | -38.78
Walpole 132kV | Stamford | Stamford | Bulk Supply Point | 33 | -0.4714 | 52.6512 | WPD Best View | Headroom (MW) | Thermal | 53.86 | 53.1 | 52.36 | 50.78 | 48.69 | 47.13 | 44.69 | 37.32 | 31.64 | 26.23 | 20.23 | 13.74 | 6.9 | 0.39 | -7.37 | -32.12 | -63.08 | -97.71
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Consumer Transformation | Headroom (MW) | Thermal | 37.75 | 37 | 36.45 | 35.74 | 34.07 | 32.75 | 30.82 | 28.87 | 27.18 | 25.68 | 24.43 | 23.2 | 21.91 | 20.57 | 19.13 | 8.66 | 8.4 | -20.91
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Leading the Way | Headroom (MW) | Thermal | 37.75 | 36.94 | 36.36 | 35.62 | 33.73 | 32.33 | 30.72 | 29.25 | 27.94 | 26.59 | 25.24 | 23.88 | 22.37 | 20.79 | 30.81 | -2.55 | -17.38 | -36.49
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | Steady Progression | Headroom (MW) | N/A | 37.75 | 37.39 | 37.13 | 36.95 | 36.72 | 36.48 | 35.47 | 34.54 | 33.67 | 32.72 | 32 | 31.4 | 31.07 | 30.85 | 30.75 | 30.8 | 28.97 | 26.23
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | System Transformation | Headroom (MW) | N/A | 37.75 | 37.25 | 36.83 | 36.45 | 35.73 | 35.13 | 33.94 | 32.88 | 31.83 | 31.04 | 30.51 | 30.02 | 29.55 | 29.18 | 30.81 | 13.41 | 7.44 | 1.53
Willington 132kV | Stanton | Stanton | Bulk Supply Point | 33 | -1.3129 | 52.948 | WPD Best View | Headroom (MW) | Thermal | 37.75 | 37 | 36.45 | 35.74 | 34.07 | 32.75 | 30.82 | 28.87 | 27.18 | 25.67 | 24.42 | 23.19 | 21.9 | 20.56 | 19.12 | 8.64 | 8.36 | -20.98
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Consumer Transformation | Headroom (MW) | N/A | 51.38 | 51.07 | 50.78 | 50.41 | 49.51 | 48.82 | 48.24 | 47.37 | 46.48 | 45.6 | 44.76 | 43.9 | 42.88 | 41.86 | 40.72 | 35.22 | 28 | 19.87
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Leading the Way | Headroom (MW) | N/A | 51.38 | 51.05 | 50.73 | 50.33 | 49.33 | 48.6 | 48.01 | 47.35 | 46.71 | 46.12 | 45.51 | 44.96 | 43.97 | 42.89 | 41.73 | 35.21 | 26.8 | 16.72
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | Steady Progression | Headroom (MW) | N/A | 51.38 | 51.2 | 51.11 | 51.03 | 50.92 | 50.82 | 50.79 | 50.66 | 50.51 | 50.33 | 50.15 | 50.03 | 49.74 | 49.47 | 49.14 | 48.83 | 47.7 | 45.91
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | System Transformation | Headroom (MW) | N/A | 51.38 | 51.13 | 50.98 | 50.79 | 50.41 | 50.11 | 49.85 | 49.31 | 48.71 | 48.1 | 47.53 | 46.98 | 46.36 | 45.81 | 45.12 | 43.18 | 39.38 | 35.41
Chesterfield 132kV | Staveley | Staveley | Bulk Supply Point | 33 | -1.3861 | 53.2673 | WPD Best View | Headroom (MW) | N/A | 51.38 | 51.08 | 50.83 | 50.52 | 49.72 | 49.1 | 48.59 | 47.8 | 46.97 | 46.14 | 45.36 | 44.55 | 43.63 | 42.69 | 41.63 | 36.77 | 30.37 | 23.05
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Consumer Transformation | Headroom (MW) | Thermal | 67.55 | 67.32 | 64.49 | 64.18 | 62.91 | 61.56 | 59.4 | 56.15 | 53.27 | 50.43 | 47.29 | 44.08 | 40.82 | 37.48 | 33.67 | 15.18 | -5.6 | -30.06
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Leading the Way | Headroom (MW) | Thermal | 67.55 | 67.31 | 64.5 | 64.2 | 62.79 | 61.34 | 59.04 | 57.01 | 55.11 | 52.96 | 46.9 | 44.89 | 41.91 | 38.8 | 35.37 | 17.04 | -5.8 | -30.77
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | Steady Progression | Headroom (MW) | N/A | 67.55 | 67.49 | 64.92 | 64.97 | 65.07 | 64.94 | 64.8 | 64.54 | 64.11 | 62.96 | 62.41 | 61.76 | 60.67 | 59.68 | 58.48 | 56.34 | 53.24 | 50.46
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | System Transformation | Headroom (MW) | N/A | 67.55 | 67.43 | 64.77 | 64.71 | 64.51 | 64.1 | 63.42 | 62.33 | 60.43 | 58.86 | 56.99 | 55.04 | 53.08 | 51.39 | 49.44 | 42.77 | 34.18 | 23.36
Lea Marston 132kV | Tamworth | Tamworth | Bulk Supply Point | 33 | -1.6558 | 52.608 | WPD Best View | Headroom (MW) | N/A | 67.55 | 67.37 | 64.61 | 64.39 | 63.71 | 62.94 | 61.64 | 59.5 | 57.46 | 55.13 | 52.76 | 50.25 | 47.68 | 45.17 | 42.29 | 30.3 | 15.86 | 0.65
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Consumer Transformation | Headroom (MW) | N/A | 33.55 | 33.44 | 33.33 | 33.2 | 32.98 | 32.91 | 32.54 | 31.94 | 31.48 | 31.04 | 30.59 | 30.15 | 29.72 | 29.26 | 28.76 | 25.93 | 22.3 | 18.44
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Leading the Way | Headroom (MW) | N/A | 33.55 | 33.43 | 33.32 | 33.18 | 32.94 | 32.95 | 32.58 | 32.18 | 31.85 | 31.44 | 31.06 | 30.69 | 30.27 | 29.84 | 29.37 | 26.74 | 23.39 | 19.44
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | Steady Progression | Headroom (MW) | N/A | 33.55 | 33.46 | 33.42 | 33.38 | 33.38 | 33.46 | 33.46 | 33.43 | 33.36 | 33.12 | 33.06 | 32.99 | 32.91 | 32.86 | 32.81 | 32.68 | 32.31 | 31.76
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | System Transformation | Headroom (MW) | N/A | 33.55 | 33.45 | 33.39 | 33.31 | 33.25 | 33.29 | 33.24 | 33.14 | 32.88 | 32.72 | 32.54 | 32.38 | 32.23 | 32.11 | 31.99 | 31.32 | 30.04 | 28.71
Lea Marston 132kV | Tamworth Town 33 | Tamworth Town 33 | Bulk Supply Point | 33 | -1.6877 | 52.6323 | WPD Best View | Headroom (MW) | N/A | 33.55 | 33.46 | 33.42 | 33.38 | 33.38 | 33.46 | 33.46 | 33.43 | 33.36 | 33.12 | 33.06 | 32.99 | 32.91 | 32.86 | 32.81 | 32.68 | 32.31 | 31.76
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Consumer Transformation | Headroom (MW) | Thermal | 46.3 | 45.66 | 45.04 | 44.27 | 42.6 | 41.04 | 39.05 | 37.19 | 35.44 | 33.94 | 32.52 | 31.23 | 29.93 | 28.54 | 27.07 | 16.38 | 9.56 | -13.7
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Leading the Way | Headroom (MW) | Thermal | 46.3 | 45.6 | 44.94 | 44.1 | 42.28 | 40.64 | 38.96 | 37.41 | 35.88 | 34.57 | 33.12 | 31.68 | 30.13 | 28.41 | 34.11 | 10.58 | -5.99 | -27.97
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | Steady Progression | Headroom (MW) | N/A | 46.3 | 45.98 | 45.8 | 45.62 | 45.4 | 45.17 | 44.24 | 43.32 | 42.45 | 41.61 | 40.84 | 40.21 | 39.84 | 39.57 | 39.41 | 38.78 | 36.75 | 33.82
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | System Transformation | Headroom (MW) | N/A | 46.3 | 45.84 | 45.46 | 45.04 | 44.36 | 43.77 | 42.64 | 41.59 | 40.56 | 39.7 | 38.95 | 38.36 | 37.89 | 37.47 | 38.44 | 28.07 | 21.22 | 14.63
Ratcliffe 132kV | Toton | Toton | Bulk Supply Point | 33 | -1.2642 | 52.9167 | WPD Best View | Headroom (MW) | Thermal | 46.3 | 45.66 | 45.03 | 44.26 | 42.59 | 41.03 | 39.04 | 37.17 | 35.42 | 33.92 | 32.49 | 31.2 | 29.88 | 28.48 | 26.99 | 16.2 | 9.3 | -14.2
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Consumer Transformation | Headroom (MW) | Thermal | 27 | 26.67 | 26.36 | 26.01 | 25.21 | 24.72 | 23.31 | 19.75 | 16.18 | 12.3 | 7.81 | 2.91 | -2.27 | -7.19 | -13.28 | -28.82 | -47.66 | -67.26
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Leading the Way | Headroom (MW) | Thermal | 27 | 26.65 | 26.33 | 25.99 | 25.2 | 24.69 | 23.21 | 21.77 | 20.49 | 18.93 | 17.43 | 15.97 | 11.8 | 7.78 | 3.44 | -13.8 | -36.47 | -48.7
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | Steady Progression | Headroom (MW) | N/A | 27 | 26.78 | 26.63 | 26.52 | 26.41 | 26.36 | 26.18 | 25.6 | 24.94 | 23.68 | 22.75 | 21.66 | 19.32 | 17.09 | 14.16 | 10.17 | 5.76 | 0.8
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | System Transformation | Headroom (MW) | Thermal | 27 | 26.73 | 26.52 | 26.31 | 25.97 | 25.76 | 25.37 | 23.34 | 20.39 | 17.42 | 13.86 | 9.93 | 5.77 | 2.02 | -2.77 | -11.64 | -23.64 | -35.88
Willington 132kV | Uttoxeter | Uttoxeter | Bulk Supply Point | 33 | -1.8577 | 52.9087 | WPD Best View | Headroom (MW) | Thermal | 27 | 26.72 | 26.48 | 26.25 | 25.81 | 25.57 | 24.38 | 21.03 | 17.58 | 13.88 | 9.55 | 4.82 | -0.15 | -4.83 | -10.6 | -23.87 | -40.76 | -58.01
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Consumer Transformation | Headroom (MW) | Thermal | 96.4 | 95.49 | 94.86 | 94.03 | 92.17 | 90.22 | 88.18 | 85.11 | 81.85 | 78.52 | 74.71 | 70.49 | 66.07 | 61.76 | 56.57 | 36.45 | 12.01 | -15.29
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Leading the Way | Headroom (MW) | Thermal | 96.4 | 95.42 | 94.77 | 93.87 | 91.75 | 89.67 | 87.48 | 85.37 | 83.29 | 81.4 | 79.44 | 77.45 | 73.38 | 69.24 | 64.8 | 40.96 | 11.4 | -17.41
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | Steady Progression | Headroom (MW) | N/A | 96.4 | 95.83 | 95.67 | 95.42 | 95.15 | 94.86 | 94.57 | 94.09 | 93.6 | 93.05 | 92.39 | 91.67 | 89.93 | 88.19 | 85.93 | 83.01 | 77.8 | 70.91
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | System Transformation | Headroom (MW) | N/A | 96.4 | 95.68 | 95.31 | 94.83 | 94.03 | 93.33 | 92.58 | 90.79 | 88.41 | 85.86 | 82.82 | 79.46 | 75.97 | 72.84 | 69.06 | 59.57 | 44.88 | 29.44
Berkswell 132kV | Warwick 33 | Warwick 33 | Bulk Supply Point | 33 | -1.5667 | 52.2861 | WPD Best View | Headroom (MW) | N/A | 96.4 | 95.59 | 95.1 | 94.43 | 93.06 | 91.48 | 89.78 | 87.34 | 84.83 | 82.25 | 79.32 | 76.06 | 72.36 | 68.76 | 64.41 | 47.97 | 27.73 | 5.15
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Consumer Transformation | Headroom (MW) | N/A | 67.29 | 66.95 | 66.67 | 66.13 | 64.67 | 63.57 | 62.01 | 59.94 | 58.04 | 56.12 | 54.01 | 51.8 | 49.52 | 47.23 | 44.64 | 32.29 | 17.35 | 0.66
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Leading the Way | Headroom (MW) | N/A | 67.29 | 66.92 | 66.65 | 66.06 | 64.36 | 63.17 | 61.52 | 60.1 | 58.79 | 57.32 | 55.88 | 54.48 | 52.36 | 50.16 | 47.76 | 34.6 | 18.44 | 4.04
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | Steady Progression | Headroom (MW) | N/A | 67.29 | 67.1 | 67 | 66.82 | 66.56 | 66.35 | 66.14 | 65.89 | 65.59 | 64.91 | 64.48 | 64.02 | 63.26 | 62.57 | 61.74 | 60.13 | 57.89 | 54.64
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | System Transformation | Headroom (MW) | N/A | 67.29 | 67.04 | 66.88 | 66.59 | 65.96 | 65.47 | 64.89 | 64.09 | 62.91 | 61.8 | 60.47 | 59.07 | 57.64 | 56.36 | 54.9 | 50.43 | 43.01 | 35.07
Grendon 132kV | Wellingborough | Wellingborough | Bulk Supply Point | 33 | -0.6847 | 52.2921 | WPD Best View | Headroom (MW) | N/A | 67.29 | 67.04 | 66.84 | 66.5 | 65.68 | 65.05 | 64.22 | 63.46 | 62.57 | 61.67 | 60.68 | 59.74 | 58.3 | 56.95 | 55.54 | 49.04 | 39.72 | 30.99
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Consumer Transformation | Headroom (MW) | N/A | 67.79 | 67.75 | 67.95 | 68.02 | 68.07 | 68.09 | 67.5 | 66.57 | 65.66 | 64.92 | 64.17 | 63.43 | 62.46 | 61.35 | 60.11 | 50.02 | 35.13 | 17.7
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Leading the Way | Headroom (MW) | N/A | 67.79 | 67.78 | 67.97 | 68.1 | 68.06 | 68.18 | 67.52 | 66.71 | 65.83 | 65.07 | 64.25 | 63.45 | 62.2 | 60.74 | 59.04 | 47.26 | 36.39 | 14.26
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | Steady Progression | Headroom (MW) | N/A | 67.79 | 67.82 | 68.08 | 68.26 | 68.65 | 68.9 | 69.03 | 69.09 | 69.16 | 69.16 | 69.26 | 69.39 | 69.45 | 69.48 | 69.51 | 69.71 | 67.97 | 66.07
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | System Transformation | Headroom (MW) | N/A | 67.79 | 67.83 | 68.06 | 68.23 | 68.54 | 68.83 | 68.92 | 68.91 | 68.78 | 68.88 | 68.91 | 68.96 | 68.88 | 68.77 | 68.64 | 66.94 | 60.79 | 53.65
Coventry 132kV | Whitley | Whitley | Bulk Supply Point | 33 | -1.4827 | 52.3934 | WPD Best View | Headroom (MW) | N/A | 67.79 | 67.72 | 67.89 | 67.94 | 67.98 | 68.02 | 67.73 | 67.13 | 66.41 | 65.72 | 65.15 | 64.59 | 63.84 | 62.96 | 61.99 | 53.87 | 41.34 | 26.63
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Consumer Transformation | Headroom (MW) | Thermal | 36.34 | 36.12 | 36.04 | 29.52 | 28.23 | 27.17 | 24.46 | 21.13 | 18.39 | 15.86 | 13.54 | 11.44 | 9.51 | 7.45 | 5.22 | -11.28 | -26.34 | -42.96
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Leading the Way | Headroom (MW) | Thermal | 36.34 | 36.12 | 36.08 | 29.59 | 28.1 | 26.93 | 24.78 | 22.78 | 20.97 | 18.98 | 17.08 | 15.21 | 13.27 | 11.19 | 8.91 | -9.25 | -12.96 | -42.38
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | Steady Progression | Headroom (MW) | N/A | 36.34 | 36.31 | 36.47 | 30.33 | 30.11 | 29.92 | 28.32 | 26.71 | 25.05 | 22.8 | 21.31 | 19.98 | 19.12 | 18.49 | 18.04 | 17.28 | 15.33 | 12.72
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | System Transformation | Headroom (MW) | N/A | 36.34 | 36.24 | 36.35 | 30.08 | 29.51 | 29.01 | 27.5 | 26.01 | 24.1 | 22.74 | 21.62 | 20.76 | 20.07 | 19.49 | 18.86 | 13.05 | 16.42 | 1.98
Chesterfield 132kV | Whitwell | Whitwell | Bulk Supply Point | 33 | -1.2272 | 53.2773 | WPD Best View | Headroom (MW) | Thermal | 36.34 | 36.14 | 36.07 | 29.57 | 28.35 | 27.31 | 24.46 | 20.95 | 18.01 | 15.3 | 12.77 | 10.43 | 8.46 | 6.39 | 4.24 | -11.11 | -25.58 | -41.34
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Consumer Transformation | Headroom (MW) | Thermal | 46.03 | 45.33 | 44.71 | 43.94 | 42.1 | 40.6 | 39.16 | 37.64 | 36.17 | 34.82 | 33.21 | 31.51 | 29.74 | 27.94 | 25.91 | 14.69 | -0.37 | -16.81
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Leading the Way | Headroom (MW) | Thermal | 46.03 | 45.27 | 44.63 | 43.81 | 41.79 | 40.21 | 38.68 | 37.23 | 35.87 | 34.67 | 33.29 | 31.89 | 30.01 | 28.01 | 25.82 | 12.56 | -4.92 | -25.55
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | Steady Progression | Headroom (MW) | N/A | 46.03 | 39.55 | 39.4 | 39.26 | 31.31 | 31.1 | 30.04 | 29 | 28.02 | 27.09 | 26.18 | 25.38 | 24.71 | 24.14 | 23.58 | 22.65 | 20.26 | 16.66
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | System Transformation | Headroom (MW) | N/A | 46.03 | 45.52 | 45.18 | 44.8 | 44.07 | 43.43 | 42.69 | 41.84 | 40.99 | 40.22 | 39.25 | 38.25 | 37.26 | 36.38 | 35.35 | 31.37 | 23.54 | 15.81
Enderby 132kV | Wigston 33 | Wigston 33 | Bulk Supply Point | 33 | -1.1441 | 52.5775 | WPD Best View | Headroom (MW) | Thermal | 46.03 | 45.43 | 44.95 | 44.37 | 43.1 | 42.04 | 40.95 | 39.76 | 38.61 | 37.55 | 36.27 | 34.97 | 33.63 | 32.26 | 30.68 | 22.8 | 11.32 | -0.76
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Consumer Transformation | Headroom (MW) | Thermal | 66.58 | 65.3 | 65.01 | 64.88 | 62.75 | 61.28 | 59.26 | 54.1 | 48.46 | 42.36 | 34.49 | 25.54 | 15.95 | 6.88 | -4.01 | -35.01 | -72.63 | -115.33
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Leading the Way | Headroom (MW) | Thermal | 66.58 | 65.24 | 64.99 | 65.03 | 62.73 | 61.29 | 59.21 | 57.34 | 55.33 | 53.19 | 51.07 | 48.72 | 40.95 | 33.29 | 25.2 | -8.18 | -51.67 | -83.67
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | Steady Progression | Headroom (MW) | N/A | 66.58 | 66.36 | 66.58 | 66.4 | 66.41 | 66.58 | 66.7 | 66.25 | 65.59 | 64.24 | 62.96 | 61.32 | 57.16 | 53.1 | 47.64 | 41.47 | 31.87 | 20.67
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | System Transformation | Headroom (MW) | Thermal | 66.58 | 66.22 | 65.58 | 65.93 | 65.34 | 65.01 | 64.6 | 61.56 | 57.01 | 52.3 | 45.9 | 38.43 | 30.42 | 23.26 | 14.45 | -1.32 | -25.15 | -52.64
Ratcliffe 132kV | Willoughby | Willoughby | Bulk Supply Point | 33 | -1.0702 | 52.8263 | WPD Best View | Headroom (MW) | Thermal | 66.58 | 65.3 | 65.01 | 64.88 | 62.75 | 61.29 | 59.29 | 54.14 | 48.51 | 42.42 | 34.56 | 25.62 | 16.04 | 6.98 | -3.91 | -34.56 | -72.07 | -114.66
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Consumer Transformation | Headroom (MW) | Thermal | 38.6 | 37.93 | 37.3 | 36.59 | 34.82 | 33.53 | 31.23 | 27.1 | 23.18 | 19.15 | 14.44 | 9.4 | 4.14 | -1.02 | -7.13 | -36.04 | -62.71 | -90.21
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Leading the Way | Headroom (MW) | Thermal | 38.6 | 37.88 | 37.25 | 36.48 | 34.6 | 33.33 | 30.93 | 28.48 | 26.25 | 23.76 | 21.21 | 18.68 | 14.12 | 9.57 | 4.67 | -23.85 | -53.01 | -77.51
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | Steady Progression | Headroom (MW) | N/A | 38.6 | 38.21 | 37.97 | 37.76 | 37.58 | 37.49 | 37.25 | 36.69 | 36.05 | 34.78 | 33.91 | 32.95 | 31.03 | 29.29 | 27.03 | 23.88 | 17.14 | 11.36
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | System Transformation | Headroom (MW) | Thermal | 38.6 | 38.08 | 37.71 | 37.25 | 36.57 | 36.06 | 35.34 | 33.42 | 30.66 | 28.09 | 24.86 | 21.39 | 17.82 | 14.61 | 10.57 | -1.83 | -15.57 | -29.63
Willington 132kV | Winster | Winster | Bulk Supply Point | 33 | -1.6398 | 53.1264 | WPD Best View | Headroom (MW) | Thermal | 38.6 | 37.93 | 37.31 | 36.61 | 34.91 | 33.63 | 31.63 | 28 | 24.33 | 20.64 | 16.25 | 11.56 | 6.66 | 1.88 | -3.78 | -31.2 | -56.48 | -82.5
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Consumer Transformation | Headroom (MW) | N/A | 36.37 | 36.21 | 32.77 | 32.45 | 32.64 | 32.63 | 31.72 | 30.7 | 29.78 | 29.11 | 28.58 | 28.07 | 27.63 | 25.42 | 24.88 | 24.04 | 16.93 | 7.68
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Leading the Way | Headroom (MW) | N/A | 36.37 | 36.21 | 32.77 | 32.37 | 32.7 | 33.01 | 32.85 | 32.68 | 32.46 | 32.56 | 32.68 | 32.82 | 32.92 | 31.16 | 31.15 | 29.23 | 31.93 | 3.28
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | Steady Progression | Headroom (MW) | N/A | 36.37 | 36.32 | 33.02 | 32.93 | 33.72 | 34.2 | 33.35 | 32.49 | 31.66 | 30.89 | 30.27 | 29.86 | 29.99 | 30.22 | 30.62 | 33.84 | 33.22 | 30.47
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | System Transformation | Headroom (MW) | N/A | 36.37 | 36.29 | 32.94 | 32.75 | 33.49 | 33.89 | 33.32 | 32.62 | 32 | 31.63 | 31.38 | 31.19 | 31.1 | 30.22 | 30.17 | 32.92 | 40.21 | 22.67
Staythorpe 132kV | Worksop | Worksop | Bulk Supply Point | 33 | -1.1009 | 53.3062 | WPD Best View | Headroom (MW) | N/A | 36.37 | 36.21 | 32.77 | 32.45 | 32.64 | 32.63 | 31.72 | 30.7 | 29.78 | 29.11 | 28.58 | 28.07 | 27.63 | 25.42 | 24.88 | 24.04 | 16.93 | 7.68