## Metadata
Data Dictionary
Column Heading | Description
Associated GSP Group | Name of the upstream Grid Supply Point (GSP) group which supplies the substation. Note that multiple GSPs can run in parallel so are therefore reported as groups.
Bulk Supply Point | Name of the upstream Bulk Supply Point (BSP) which supplies the substation.
Substation | Name of the substation for which the generation and demand headroom figures have been calculated.
Supply Level | Identifier for whether the substation is a Primary or a Bulk Supply Point. The definition is supplied in the 'NDP Methodology Report'.
Voltage Level (kV) | Voltage of the lower voltage side of the transformation at the substation.
Latitude | Latitude and longitude of the location of the substation.
Longitude
Scenario | Identifier for one of the four Distribution Future Energy Scenarios (DFES) or WPD Best View scenario the headroom figures refer to
Units | The units used to define the headroom available at each substation under each scenario and all of the years reported on (see below)
Limiting constraint | For generation headroom worksheet only. Identifier for the limiting factor (either thermal or fault level) that triggers the constraint when the generation headroom falls below zero.
0 | Defines the year snapshot for the headroom calculation, where the year refers to the end of the calendar year
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2040
2045
2050

## Demand headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | 0 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Consumer Transformation | Thermal headroom (MW) | 6.13 | 6.17 | 6.13 | 6.05 | 5.95 | 5.73 | 5.49 | 5.25 | 5.02 | 4.77 | 4.47 | 4.09 | 3.51 | 2.93 | 2.36 | -0.42 | -1.56 | -2.04
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Leading the Way | Thermal headroom (MW) | 6.13 | 6.13 | 6.04 | 5.93 | 5.76 | 5.43 | 5.1 | 4.67 | 4.23 | 3.77 | 3.36 | 2.85 | 2.34 | 1.88 | 1.46 | -0.27 | -0.78 | -0.9
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Steady Progression | Thermal headroom (MW) | 6.13 | 6.23 | 6.25 | 6.26 | 6.27 | 6.16 | 6.04 | 5.91 | 5.78 | 5.61 | 5.39 | 5.16 | 4.92 | 4.65 | 4.38 | 1.99 | 0.87 | 0.59
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | System Transformation | Thermal headroom (MW) | 6.13 | 6.21 | 6.2 | 6.19 | 6.16 | 6.12 | 6.07 | 5.98 | 5.88 | 5.74 | 5.54 | 5.31 | 5.07 | 4.85 | 4.65 | 2.81 | 1.12 | 0.78
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | WPD Best View | Thermal headroom (MW) | 6.13 | 6.17 | 6.13 | 6.05 | 5.95 | 5.73 | 5.49 | 5.25 | 5.02 | 4.77 | 4.47 | 4.09 | 3.51 | 2.93 | 2.36 | -0.42 | -1.56 | -2.04
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Consumer Transformation | Thermal headroom (MW) | 4.36 | 4.26 | 4.04 | 3.78 | 3.31 | 2.56 | 1.84 | 1.13 | 0.13 | -1.07 | -3.07 | -5.04 | -7.03 | -8.93 | -10.75 | -17.98 | -22.09 | -24.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Leading the Way | Thermal headroom (MW) | 4.36 | 4.14 | 3.8 | 3.45 | 2.79 | 1.8 | 0.49 | -1.08 | -2.64 | -4.33 | -6.18 | -8.04 | -9.88 | -11.66 | -13.31 | -18.85 | -21.24 | -22.36
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Steady Progression | Thermal headroom (MW) | 4.36 | 4.41 | 4.36 | 4.31 | 4.15 | 3.84 | 3.51 | 3.14 | 2.72 | 2.28 | 1.49 | 0.73 | -0.11 | -0.95 | -1.86 | -8.2 | -11.68 | -13.31
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | System Transformation | Thermal headroom (MW) | 4.36 | 4.33 | 4.21 | 4.1 | 3.8 | 3.58 | 3.34 | 2.96 | 2.5 | 2.14 | 1.59 | 0.52 | -0.71 | -2 | -3.28 | -10.31 | -14.76 | -16.42
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | WPD Best View | Thermal headroom (MW) | 4.36 | 4.26 | 4.04 | 3.78 | 3.31 | 2.56 | 1.84 | 1.13 | 0.13 | -1.07 | -3.07 | -5.04 | -7.03 | -8.93 | -10.75 | -17.98 | -22.1 | -24.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Consumer Transformation | Thermal headroom (MW) | -0.1 | -0.05 | -0.06 | -0.1 | -0.19 | -0.45 | -0.7 | -0.95 | -1.19 | -1.46 | -1.81 | -2.3 | -2.82 | -3.35 | -3.87 | -5.56 | -6.31 | -6.67
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Leading the Way | Thermal headroom (MW) | -0.1 | -0.07 | -0.12 | -0.21 | -0.39 | -0.77 | -1.15 | -1.66 | -2.39 | -3.18 | -3.54 | -4.06 | -4.66 | -5.21 | -5.75 | -8 | -9.5 | -10.86
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Steady Progression | Thermal headroom (MW) | -0.1 | -0.02 | 0 | 0.02 | 0.01 | -0.15 | -0.31 | -0.47 | -0.68 | -1.06 | -1.58 | -1.87 | -2.2 | -2.59 | -2.92 | -5.53 | -6.24 | -6.53
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | System Transformation | Thermal headroom (MW) | -0.1 | -0.07 | -0.09 | -0.14 | -0.24 | -0.32 | -0.43 | -0.59 | -0.78 | -0.93 | -1.49 | -1.71 | -2.21 | -2.49 | -2.92 | -5.38 | -8.1 | -9.27
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | WPD Best View | Thermal headroom (MW) | -0.1 | -0.03 | -0.03 | -0.04 | -0.09 | -0.29 | -0.49 | -0.68 | -0.89 | -1.2 | -1.64 | -1.96 | -2.29 | -2.64 | -3.02 | -5.36 | -6.18 | -6.55
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Consumer Transformation | Thermal headroom (MW) | 0.45 | 0.5 | 0.47 | 0.37 | 0.24 | -0.34 | -0.91 | -1.5 | -2.06 | -2.9 | -4 | -5.08 | -6.2 | -7.28 | -8.34 | -12.49 | -14.95 | -16.93
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Leading the Way | Thermal headroom (MW) | 0.45 | 0.46 | 0.38 | 0.24 | 0.05 | -0.69 | -1.52 | -2.6 | -3.79 | -5.05 | -5.94 | -6.83 | -7.73 | -8.61 | -9.44 | -13.11 | -15.07 | -16.7
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Steady Progression | Thermal headroom (MW) | 0.45 | 0.53 | 0.54 | 0.51 | 0.48 | 0.21 | -0.08 | -0.44 | -0.79 | -1.18 | -1.78 | -2.39 | -3.04 | -3.69 | -4.42 | -8.64 | -9.97 | -10.51
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | System Transformation | Thermal headroom (MW) | 0.45 | 0.51 | 0.48 | 0.43 | 0.34 | 0.26 | 0.15 | -0.14 | -0.55 | -0.79 | -1.18 | -1.57 | -1.99 | -2.6 | -3.26 | -7.22 | -10.46 | -12.03
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | WPD Best View | Thermal headroom (MW) | 0.45 | 0.53 | 0.54 | 0.51 | 0.48 | 0.21 | -0.09 | -0.45 | -0.81 | -1.19 | -1.8 | -2.41 | -3.06 | -3.71 | -4.43 | -8.65 | -9.99 | -10.52
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Consumer Transformation | Thermal headroom (MW) | 1.46 | 1.51 | 1.49 | 1.41 | 1.22 | 0.75 | 0.3 | -0.14 | -0.61 | -1.35 | -2.48 | -3.65 | -4.83 | -6.01 | -7.08 | -11.46 | -13.74 | -14.72
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Leading the Way | Thermal headroom (MW) | 1.46 | 1.41 | 1.26 | 1.07 | 0.69 | 0.03 | -0.8 | -1.97 | -3.48 | -5.08 | -6.02 | -7.16 | -8.44 | -9.68 | -10.86 | -14.46 | -15.99 | -16.83
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Steady Progression | Thermal headroom (MW) | 1.46 | 1.59 | 1.64 | 1.67 | 1.66 | 1.43 | 1.2 | 0.9 | 0.56 | 0.19 | -0.39 | -1.02 | -1.69 | -2.42 | -3.12 | -7.84 | -9.76 | -10.46
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | System Transformation | Thermal headroom (MW) | 1.46 | 1.5 | 1.48 | 1.43 | 1.3 | 1.19 | 1.05 | 0.88 | 0.65 | 0.45 | -0.05 | -0.42 | -1.03 | -1.75 | -2.64 | -7.32 | -10.67 | -11.65
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | WPD Best View | Thermal headroom (MW) | 1.46 | 1.5 | 1.47 | 1.38 | 1.15 | 0.6 | 0.05 | -0.53 | -1.54 | -2.82 | -3.91 | -5.18 | -6.56 | -7.97 | -9.3 | -14.11 | -16.95 | -18.63
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Consumer Transformation | Thermal headroom (MW) | 0.75 | 0.75 | 0.58 | 0.54 | 0.44 | 0.15 | -0.12 | -0.38 | -0.66 | -1.07 | -1.82 | -2.55 | -3.28 | -3.99 | -4.69 | -7.72 | -9.26 | -9.88
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Leading the Way | Thermal headroom (MW) | 0.75 | 0.66 | 0.4 | 0.28 | 0.06 | -0.38 | -0.91 | -1.53 | -2.34 | -3.23 | -3.82 | -4.49 | -5.2 | -5.94 | -6.63 | -9.13 | -10.18 | -10.8
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Steady Progression | Thermal headroom (MW) | 0.75 | 0.81 | 0.73 | 0.74 | 0.74 | 0.61 | 0.45 | 0.25 | 0.04 | -0.25 | -0.67 | -1.02 | -1.43 | -1.87 | -2.32 | -5.27 | -6.3 | -6.7
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | System Transformation | Thermal headroom (MW) | 0.75 | 0.75 | 0.6 | 0.57 | 0.49 | 0.43 | 0.35 | 0.26 | 0.14 | 0.02 | -0.35 | -0.58 | -0.96 | -1.38 | -1.95 | -4.94 | -7.25 | -8.09
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | WPD Best View | Thermal headroom (MW) | 0.75 | 0.65 | 0.39 | 0.27 | 0.08 | -0.23 | -0.61 | -1.02 | -1.54 | -2.08 | -2.71 | -3.22 | -3.93 | -4.55 | -5.19 | -7.82 | -9.39 | -9.94
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Consumer Transformation | Thermal headroom (MW) | -0.35 | -0.78 | -1.38 | -2.08 | -3.19 | -4.15 | -5.05 | -5.92 | -6.8 | -7.9 | -10.22 | -12.51 | -14.8 | -17.06 | -19.18 | -28.66 | -33.92 | -36.33
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Leading the Way | Thermal headroom (MW) | -0.35 | -1 | -1.85 | -2.78 | -4.24 | -5.73 | -7.12 | -8.75 | -10.6 | -12.46 | -14.71 | -17.08 | -19.4 | -21.63 | -23.62 | -30.02 | -32.35 | -32.97
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Steady Progression | Thermal headroom (MW) | -0.35 | -0.47 | -0.76 | -1.05 | -1.58 | -1.97 | -2.38 | -2.8 | -3.27 | -3.74 | -4.37 | -4.98 | -5.64 | -6.39 | -7.29 | -14.02 | -17.95 | -19.58
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | System Transformation | Thermal headroom (MW) | -0.35 | -0.6 | -1.03 | -1.48 | -2.23 | -2.59 | -2.96 | -3.43 | -4.01 | -4.51 | -5.17 | -6.2 | -7.23 | -8.46 | -9.91 | -17.46 | -21.29 | -22.47
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | WPD Best View | Thermal headroom (MW) | -0.35 | -0.78 | -1.38 | -2.08 | -3.19 | -4.15 | -5.05 | -5.92 | -6.8 | -7.9 | -10.22 | -12.51 | -14.8 | -17.06 | -19.18 | -28.65 | -33.9 | -36.31
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Consumer Transformation | Thermal headroom (MW) | 23.63 | 23.23 | 22.83 | 22.33 | 21.56 | 20.37 | 19.24 | 18.09 | 16.49 | 14.55 | 11.41 | 8.38 | 5.58 | 2.86 | 0.27 | -11.24 | -17.29 | -20.04
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Leading the Way | Thermal headroom (MW) | 23.63 | 23.32 | 22.29 | 21.53 | 20.43 | 18.91 | 17.26 | 14.65 | 11.72 | 8.64 | 5.36 | 2.19 | -0.65 | -3.31 | -5.71 | -12.88 | -15.17 | -15.7
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Steady Progression | Thermal headroom (MW) | 23.63 | 23.85 | 23.81 | 23.75 | 23.63 | 23.21 | 22.8 | 22.34 | 21.83 | 21.3 | 20.43 | 19.6 | 18.78 | 17.35 | 15.77 | 7.25 | 2.29 | 0.13
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | System Transformation | Thermal headroom (MW) | 23.63 | 23.73 | 23.55 | 23.34 | 23 | 22.63 | 22.22 | 21.66 | 20.97 | 20.32 | 18.89 | 17.53 | 16.3 | 14.76 | 12.99 | 3.1 | -1.94 | -3.31
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | WPD Best View | Thermal headroom (MW) | 23.63 | 23.23 | 22.83 | 22.33 | 21.56 | 20.37 | 19.24 | 18.09 | 16.49 | 14.55 | 11.41 | 8.38 | 5.58 | 2.86 | 0.27 | -11.24 | -17.29 | -20.04
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Consumer Transformation | Thermal headroom (MW) | 0.97 | 1 | 0.99 | 0.96 | 0.88 | 0.62 | 0.37 | 0.11 | -0.14 | -0.46 | -0.99 | -1.54 | -2.1 | -2.67 | -3.16 | -5.28 | -6.1 | -6.46
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Leading the Way | Thermal headroom (MW) | 0.97 | 0.96 | 0.89 | 0.8 | 0.63 | 0.31 | -0.08 | -0.6 | -1.33 | -2.08 | -2.46 | -2.89 | -3.41 | -3.94 | -4.42 | -6.56 | -7.4 | -8.03
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Steady Progression | Thermal headroom (MW) | 0.97 | 1.03 | 1.05 | 1.06 | 1.05 | 0.91 | 0.74 | 0.56 | 0.37 | 0.11 | -0.3 | -0.64 | -1.06 | -1.51 | -1.92 | -4.73 | -5.81 | -6.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | System Transformation | Thermal headroom (MW) | 0.97 | 0.99 | 0.98 | 0.94 | 0.87 | 0.82 | 0.76 | 0.67 | 0.55 | 0.43 | 0.08 | -0.12 | -0.45 | -0.67 | -1.1 | -4.3 | -6.81 | -7.57
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | WPD Best View | Thermal headroom (MW) | 0.97 | 1 | 0.99 | 0.96 | 0.88 | 0.62 | 0.37 | 0.11 | -0.14 | -0.46 | -0.99 | -1.54 | -2.1 | -2.67 | -3.16 | -5.28 | -6.1 | -6.46
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Consumer Transformation | Thermal headroom (MW) | 4.18 | 4.13 | 4.07 | 4 | 3.89 | 3.66 | 3.47 | 3.29 | 3.07 | 2.82 | 2.46 | 2.03 | 1.64 | 1.26 | 0.89 | -1.15 | -2.13 | -2.47
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Leading the Way | Thermal headroom (MW) | 4.18 | 4.03 | 3.87 | 3.75 | 3.55 | 3.22 | 2.88 | 2.51 | 2.16 | 1.79 | 1.44 | 1.08 | 0.69 | 0.31 | -0.02 | -1.28 | -1.62 | -1.56
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Steady Progression | Thermal headroom (MW) | 4.18 | 4.21 | 4.21 | 4.22 | 4.21 | 4.14 | 4.07 | 4.01 | 3.9 | 3.74 | 3.54 | 3.36 | 3.2 | 3.03 | 2.82 | 1.4 | 0.74 | 0.52
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | System Transformation | Thermal headroom (MW) | 4.18 | 4.2 | 4.18 | 4.18 | 4.15 | 4.14 | 4.09 | 3.99 | 3.89 | 3.8 | 3.65 | 3.46 | 3.24 | 3.02 | 2.75 | 1.37 | 0.7 | 0.58
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | WPD Best View | Thermal headroom (MW) | 4.18 | 4.13 | 4.07 | 4 | 3.89 | 3.66 | 3.47 | 3.29 | 3.07 | 2.82 | 2.46 | 2.03 | 1.64 | 1.26 | 0.89 | -1.15 | -2.13 | -2.47
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Consumer Transformation | Thermal headroom (MW) | 5.26 | 5.22 | 5.08 | 4.83 | 4.37 | 3.23 | 2.51 | 1.78 | 0.9 | -0.32 | -2.28 | -4.3 | -6.32 | -8.3 | -10.27 | -17.8 | -21.72 | -23.75
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Leading the Way | Thermal headroom (MW) | 5.26 | 5.1 | 4.84 | 4.49 | 3.86 | 2.26 | 1.1 | -0.31 | -2.26 | -4.13 | -5.88 | -7.77 | -9.57 | -11.34 | -12.64 | -17.94 | -20.19 | -21.03
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Steady Progression | Thermal headroom (MW) | 5.26 | 5.36 | 5.37 | 5.33 | 5.24 | 4.62 | 4.26 | 3.89 | 3.35 | 2.81 | 2.12 | 1.42 | 0.54 | -0.41 | -1.4 | -8.2 | -11.52 | -12.85
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | System Transformation | Thermal headroom (MW) | 5.26 | 5.29 | 5.22 | 5.1 | 4.86 | 4.26 | 4.01 | 3.65 | 3.04 | 2.57 | 1.99 | 1.36 | 0.3 | -1.05 | -2.43 | -9.26 | -13.43 | -14.5
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | WPD Best View | Thermal headroom (MW) | 5.26 | 5.36 | 5.36 | 5.32 | 5.2 | 4.56 | 4.17 | 3.78 | 3.26 | 2.72 | 2.01 | 1.33 | 0.43 | -0.56 | -1.57 | -8.18 | -11.57 | -12.97
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Consumer Transformation | Thermal headroom (MW) | 3.38 | 3.4 | 3.36 | 3.28 | 3.17 | 2.85 | 2.53 | 2.21 | 1.91 | 1.53 | 0.47 | -0.61 | -1.67 | -2.67 | -3.66 | -6.44 | -7.66 | -8.02
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Leading the Way | Thermal headroom (MW) | 3.38 | 3.37 | 3.28 | 3.16 | 2.98 | 2.55 | 2.09 | 1.5 | 0.66 | -0.23 | -1.08 | -2 | -2.97 | -3.95 | -4.85 | -7.75 | -9.13 | -9.8
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Steady Progression | Thermal headroom (MW) | 3.38 | 3.43 | 3.42 | 3.41 | 3.38 | 3.2 | 3.01 | 2.77 | 2.51 | 2.17 | 1.68 | 1.31 | 0.83 | 0.31 | -0.21 | -4.32 | -6.26 | -7.35
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | System Transformation | Thermal headroom (MW) | 3.38 | 3.39 | 3.35 | 3.28 | 3.19 | 3.1 | 2.99 | 2.85 | 2.68 | 2.52 | 2.09 | 1.46 | 0.71 | 0.05 | -0.71 | -5.44 | -9.03 | -10.25
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | WPD Best View | Thermal headroom (MW) | 3.38 | 3.4 | 3.36 | 3.28 | 3.17 | 2.85 | 2.53 | 2.21 | 1.91 | 1.53 | 0.47 | -0.61 | -1.67 | -2.67 | -3.66 | -6.44 | -7.66 | -8.02
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Consumer Transformation | Thermal headroom (MW) | 9.66 | 9.7 | 9.72 | 9.7 | 9.63 | 9.29 | 8.91 | 8.54 | 8.14 | 7.72 | 6.83 | 5.91 | 5.03 | 4.14 | 3.22 | 0.75 | -0.23 | -0.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Leading the Way | Thermal headroom (MW) | 9.66 | 9.66 | 9.62 | 9.57 | 9.44 | 8.93 | 8.4 | 7.79 | 7.2 | 6.57 | 5.84 | 5.07 | 4.3 | 3.53 | 3.19 | 1.43 | 0.77 | 0.94
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Steady Progression | Thermal headroom (MW) | 9.66 | 9.71 | 9.7 | 9.69 | 9.67 | 9.48 | 9.31 | 9.14 | 8.91 | 8.67 | 8.28 | 7.93 | 7.58 | 7.24 | 6.89 | 3.81 | 2.33 | 1.74
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | System Transformation | Thermal headroom (MW) | 9.66 | 9.71 | 9.71 | 9.7 | 9.67 | 9.66 | 9.59 | 9.49 | 9.34 | 9.19 | 8.94 | 8.64 | 8 | 7.32 | 6.62 | 3.47 | 1.35 | 1.05
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | WPD Best View | Thermal headroom (MW) | 9.66 | 9.7 | 9.72 | 9.7 | 9.63 | 9.29 | 8.91 | 8.54 | 8.14 | 7.72 | 6.83 | 5.91 | 5.03 | 4.14 | 3.22 | 0.75 | -0.23 | -0.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Consumer Transformation | Thermal headroom (MW) | 1.61 | 1.69 | 1.68 | 1.69 | 1.62 | 1.46 | 1.33 | 1.19 | 1.06 | 0.93 | 0.7 | 0.38 | -0.11 | -0.63 | -1.13 | -3.38 | -4.49 | -4.86
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Leading the Way | Thermal headroom (MW) | 1.61 | 1.64 | 1.57 | 1.52 | 1.37 | 1.13 | 0.91 | 0.61 | 0.3 | -0.04 | -0.4 | -0.8 | -1.2 | -1.59 | -2.01 | -3.45 | -3.79 | -3.69
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Steady Progression | Thermal headroom (MW) | 1.61 | 1.75 | 1.8 | 1.87 | 1.9 | 1.86 | 1.81 | 1.76 | 1.7 | 1.63 | 1.5 | 1.38 | 1.23 | 1.04 | 0.84 | -0.94 | -1.71 | -1.94
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | System Transformation | Thermal headroom (MW) | 1.61 | 1.72 | 1.75 | 1.78 | 1.77 | 1.78 | 1.79 | 1.78 | 1.76 | 1.73 | 1.61 | 1.46 | 1.31 | 1.17 | 1.05 | -0.52 | -1.59 | -1.77
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | WPD Best View | Thermal headroom (MW) | 1.61 | 1.65 | 1.6 | 1.56 | 1.44 | 1.24 | 1.06 | 0.89 | 0.67 | 0.4 | 0.06 | -0.39 | -0.85 | -1.29 | -1.77 | -3.47 | -4.04 | -4.1
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Consumer Transformation | Thermal headroom (MW) | 1.82 | 1.73 | 1.41 | 0.94 | 0.23 | -0.9 | -1.91 | -2.92 | -4.01 | -5.29 | -8.07 | -10.89 | -13.72 | -16.39 | -19 | -29.87 | -36.03 | -39.17
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Leading the Way | Thermal headroom (MW) | 1.82 | 1.5 | 0.91 | 0.21 | -0.77 | -2.29 | -4 | -6.12 | -8.55 | -11.04 | -13.6 | -16.3 | -18.94 | -21.46 | -23.74 | -31.41 | -34.22 | -35.47
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Steady Progression | Thermal headroom (MW) | 1.82 | 1.99 | 1.95 | 1.89 | 1.75 | 1.26 | 0.76 | 0.23 | -0.36 | -0.97 | -1.88 | -2.82 | -4.04 | -5.3 | -6.62 | -15.57 | -20.06 | -22.07
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | System Transformation | Thermal headroom (MW) | 1.82 | 1.86 | 1.7 | 1.48 | 1.13 | 0.81 | 0.49 | 0.02 | -0.64 | -1.18 | -1.98 | -3.22 | -4.44 | -5.72 | -7.41 | -16.64 | -22.26 | -24.43
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | WPD Best View | Thermal headroom (MW) | 1.82 | 1.73 | 1.41 | 0.94 | 0.23 | -0.9 | -1.91 | -2.92 | -4.01 | -5.29 | -8.07 | -10.89 | -13.72 | -16.39 | -19 | -29.87 | -36.03 | -39.17
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Consumer Transformation | Thermal headroom (MW) | -0.32 | -0.27 | -0.24 | -0.23 | -0.27 | -0.81 | -1.36 | -1.93 | -2.5 | -3.06 | -3.8 | -4.53 | -5.3 | -6.08 | -6.84 | -10.01 | -11.7 | -13.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Leading the Way | Thermal headroom (MW) | -0.32 | -0.27 | -0.31 | -0.36 | -0.45 | -1.28 | -2.12 | -2.95 | -3.8 | -4.71 | -5.22 | -5.74 | -6.27 | -6.85 | -7.38 | -10.34 | -11.79 | -13.02
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Steady Progression | Thermal headroom (MW) | -0.32 | -0.31 | -0.36 | -0.41 | -0.47 | -0.78 | -1.07 | -1.36 | -1.65 | -1.94 | -2.43 | -2.89 | -3.39 | -3.89 | -4.39 | -7.76 | -8.94 | -9.72
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | System Transformation | Thermal headroom (MW) | -0.32 | -0.29 | -0.33 | -0.37 | -0.42 | -0.47 | -0.5 | -0.7 | -0.97 | -1.12 | -1.5 | -1.87 | -2.27 | -2.68 | -3.1 | -6.54 | -9.39 | -10.6
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | WPD Best View | Thermal headroom (MW) | -0.32 | -0.27 | -0.24 | -0.23 | -0.27 | -0.81 | -1.36 | -1.93 | -2.5 | -3.06 | -3.8 | -4.53 | -5.3 | -6.08 | -6.84 | -10.01 | -11.7 | -13.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Consumer Transformation | Thermal headroom (MW) | 8.18 | 8.23 | 8.21 | 8.18 | 8.07 | 7.75 | 7.43 | 7.08 | 6.78 | 6.47 | 5.86 | 5.15 | 4.44 | 3.68 | 2.94 | -0.18 | -1.3 | -1.77
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Leading the Way | Thermal headroom (MW) | 8.18 | 8.16 | 8.07 | 7.98 | 7.78 | 7.4 | 6.97 | 6.38 | 5.72 | 4.93 | 4.45 | 3.88 | 3.32 | 2.8 | 2.24 | -0.06 | -0.52 | -0.56
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Steady Progression | Thermal headroom (MW) | 8.18 | 8.27 | 8.29 | 8.31 | 8.32 | 8.16 | 8 | 7.81 | 7.61 | 7.36 | 6.99 | 6.63 | 6.26 | 5.83 | 5.36 | 1.42 | -0.37 | -1.15
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | System Transformation | Thermal headroom (MW) | 8.18 | 8.25 | 8.25 | 8.25 | 8.2 | 8.16 | 8.11 | 8.01 | 7.9 | 7.77 | 7.54 | 7.27 | 7 | 6.75 | 6.51 | 2.46 | -0.33 | -0.81
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | WPD Best View | Thermal headroom (MW) | 8.18 | 8.23 | 8.21 | 8.18 | 8.08 | 7.77 | 7.45 | 7.11 | 6.82 | 6.52 | 6.02 | 5.37 | 4.72 | 4.02 | 3.31 | 0.08 | -1.47 | -1.94
Bishops Wood 132kV | Kidderminster 132 11 (GT1A) | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Consumer Transformation | Thermal headroom (MW) | 37.85 | 37.2 | 36.32 | 35.03 | 33.25 | 30.62 | 27.7 | 24.87 | 21.78 | 18.53 | 11.67 | 4.87 | -2.04 | -8.79 | -15.28 | -46.75 | -65.54 | -73.84
Bishops Wood 132kV | Kidderminster 132 11 (GT1A) | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Leading the Way | Thermal headroom (MW) | 37.85 | 36.86 | 34.84 | 32.85 | 30.04 | 25.78 | 21.29 | 15.68 | 9.79 | 3.35 | -3.92 | -11.19 | -18.44 | -25.42 | -31.85 | -51.17 | -58.17 | -59.96
Bishops Wood 132kV | Kidderminster 132 11 (GT1A) | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Steady Progression | Thermal headroom (MW) | 37.85 | 38.42 | 38.48 | 38.36 | 38.12 | 37.27 | 36.23 | 35.21 | 34.03 | 32.61 | 30.67 | 28.69 | 26.56 | 23.95 | 21.35 | 5.36 | -6.3 | -11.46
Bishops Wood 132kV | Kidderminster 132 11 (GT1A) | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | System Transformation | Thermal headroom (MW) | 37.85 | 38.13 | 37.83 | 37.35 | 36.59 | 35.73 | 34.48 | 33.05 | 31.4 | 29.55 | 26.74 | 23.86 | 20.92 | 18.05 | 15.43 | -2.54 | -10.46 | -13.22
Bishops Wood 132kV | Kidderminster 132 11 (GT1A) | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | WPD Best View | Thermal headroom (MW) | 37.85 | 38.42 | 38.48 | 38.36 | 38.12 | 37.27 | 36.23 | 35.21 | 34.03 | 32.61 | 30.67 | 28.69 | 26.56 | 23.95 | 21.35 | 5.37 | -6.29 | -11.44
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Consumer Transformation | Thermal headroom (MW) | 0.64 | 0.69 | 0.64 | 0.59 | 0.49 | 0.01 | -0.47 | -0.91 | -1.35 | -1.85 | -2.49 | -3.11 | -3.78 | -4.41 | -5.07 | -7.19 | -8.01 | -8.33
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Leading the Way | Thermal headroom (MW) | 0.64 | 0.6 | 0.49 | 0.37 | 0.15 | -0.54 | -1.24 | -1.95 | -2.78 | -3.63 | -4.1 | -4.61 | -5.2 | -5.8 | -6.4 | -8.53 | -9.35 | -9.89
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Steady Progression | Thermal headroom (MW) | 0.64 | 0.69 | 0.63 | 0.59 | 0.53 | 0.28 | 0 | -0.28 | -0.57 | -0.94 | -1.49 | -1.9 | -2.35 | -2.81 | -3.3 | -6.24 | -7.08 | -7.32
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | System Transformation | Thermal headroom (MW) | 0.64 | 0.68 | 0.61 | 0.55 | 0.44 | 0.31 | 0.2 | 0.08 | -0.1 | -0.26 | -0.75 | -1.11 | -1.63 | -2.03 | -2.57 | -5.5 | -7.77 | -8.48
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | WPD Best View | Thermal headroom (MW) | 0.64 | 0.68 | 0.61 | 0.55 | 0.44 | 0.31 | 0.19 | 0.07 | -0.12 | -0.27 | -0.76 | -1.12 | -1.64 | -2.05 | -2.58 | -5.51 | -7.77 | -8.46
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Consumer Transformation | Thermal headroom (MW) | 1.94 | 1.97 | 1.95 | 1.9 | 1.78 | 1.21 | 0.67 | 0.1 | -0.44 | -1.01 | -2.48 | -3.93 | -5.38 | -6.8 | -8.3 | -12.37 | -18.91 | -24.1
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Leading the Way | Thermal headroom (MW) | 1.94 | 1.89 | 1.75 | 1.58 | 0.98 | -0.16 | -1.32 | -2.85 | -6.32 | -10.02 | -10.99 | -12.85 | -15.53 | -18.42 | -21.11 | -31.53 | -43.89 | -56.87
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Steady Progression | Thermal headroom (MW) | 1.94 | 1.95 | 1.91 | 1.87 | 1.77 | 1.44 | 1.13 | 0.76 | 0.39 | -1.52 | -3.95 | -4.43 | -4.97 | -5.97 | -6.49 | -9.8 | -10.81 | -11.18
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | System Transformation | Thermal headroom (MW) | 1.94 | 1.87 | 1.77 | 1.64 | 1.43 | 1.25 | 0.99 | 0.65 | 0.21 | -0.09 | -1.47 | -1.84 | -3.04 | -3.67 | -4.83 | -9.9 | -15.79 | -18.98
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | WPD Best View | Thermal headroom (MW) | 1.94 | 1.94 | 1.89 | 1.82 | 1.69 | 1.56 | 1.39 | 1.19 | 0.92 | -0.78 | -3.13 | -3.51 | -4.12 | -5.08 | -5.62 | -8.87 | -11.42 | -12.3
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Consumer Transformation | Thermal headroom (MW) | 0.71 | 0.69 | 0.57 | 0.43 | -0.01 | -0.94 | -1.84 | -2.75 | -3.7 | -4.8 | -6.53 | -8.23 | -9.96 | -11.6 | -13.17 | -18.9 | -21.29 | -22.06
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Leading the Way | Thermal headroom (MW) | 0.71 | 0.59 | 0.26 | -0.02 | -0.7 | -2.06 | -3.38 | -4.78 | -6.3 | -8.01 | -9.44 | -11.01 | -12.6 | -14.15 | -15.24 | -19.24 | -20.77 | -21.15
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Steady Progression | Thermal headroom (MW) | 0.71 | 0.73 | 0.66 | 0.61 | 0.35 | -0.18 | -0.67 | -1.18 | -1.74 | -2.44 | -3.32 | -4.03 | -4.86 | -5.7 | -6.54 | -12.82 | -15.66 | -16.55
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | System Transformation | Thermal headroom (MW) | 0.71 | 0.7 | 0.61 | 0.47 | 0.1 | -0.21 | -0.5 | -0.9 | -1.32 | -1.78 | -2.56 | -3.25 | -4.5 | -5.7 | -6.99 | -13.45 | -17.87 | -18.73
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | WPD Best View | Thermal headroom (MW) | 0.71 | 0.72 | 0.64 | 0.51 | 0.16 | -0.23 | -0.59 | -1.02 | -1.47 | -2 | -2.73 | -3.5 | -4.71 | -5.9 | -7.1 | -13.14 | -16.5 | -17.02
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Consumer Transformation | Thermal headroom (MW) | 6.59 | 6.21 | 5.72 | 5.18 | 4.4 | 3.17 | 1.99 | 0.83 | -0.4 | -1.7 | -4.1 | -6.45 | -8.85 | -11.18 | -13.37 | -22.39 | -27.32 | -29.35
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Leading the Way | Thermal headroom (MW) | 6.59 | 5.85 | 4.93 | 4.05 | 2.85 | 1.05 | -0.64 | -2.45 | -4.26 | -6.28 | -8.5 | -10.81 | -13.15 | -15.37 | -17.01 | -22.79 | -24.54 | -24.74
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Steady Progression | Thermal headroom (MW) | 6.59 | 6.46 | 6.22 | 6 | 5.67 | 5.09 | 4.5 | 3.86 | 3.24 | 2.55 | 1.58 | 0.64 | -0.36 | -1.43 | -2.44 | -9.59 | -13.2 | -14.53
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | System Transformation | Thermal headroom (MW) | 6.59 | 6.33 | 5.99 | 5.66 | 5.12 | 4.68 | 4.29 | 3.84 | 3.35 | 2.76 | 1.88 | 0.87 | -0.56 | -2.05 | -3.5 | -10.79 | -14.64 | -15.35
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | WPD Best View | Thermal headroom (MW) | 6.59 | 6.33 | 5.99 | 5.66 | 5.12 | 4.67 | 4.27 | 3.81 | 3.32 | 2.72 | 1.83 | 0.8 | -0.64 | -2.14 | -3.59 | -10.87 | -14.69 | -15.37
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Consumer Transformation | Thermal headroom (MW) | 0.65 | 0.66 | 0.63 | 0.57 | 0.45 | 0.01 | -0.43 | -0.84 | -1.23 | -1.63 | -2.13 | -2.68 | -3.49 | -4.27 | -5 | -7.99 | -9.45 | -10.52
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Leading the Way | Thermal headroom (MW) | 0.65 | 0.63 | 0.56 | 0.47 | 0.3 | -0.28 | -0.86 | -1.57 | -2.37 | -3.2 | -3.67 | -4.26 | -4.94 | -5.66 | -6.26 | -9.02 | -10.69 | -12.19
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Steady Progression | Thermal headroom (MW) | 0.65 | 0.69 | 0.69 | 0.68 | 0.65 | 0.42 | 0.19 | -0.09 | -0.37 | -0.74 | -1.26 | -1.64 | -2.04 | -2.47 | -2.89 | -6.34 | -7.45 | -7.83
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | System Transformation | Thermal headroom (MW) | 0.65 | 0.66 | 0.63 | 0.58 | 0.48 | 0.37 | 0.25 | 0.04 | -0.24 | -0.44 | -0.87 | -1.18 | -1.6 | -1.93 | -2.32 | -5.12 | -8.38 | -9.76
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | WPD Best View | Thermal headroom (MW) | 0.65 | 0.69 | 0.69 | 0.68 | 0.65 | 0.42 | 0.19 | -0.09 | -0.37 | -0.74 | -1.26 | -1.64 | -2.04 | -2.47 | -2.89 | -6.33 | -7.46 | -7.84
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Consumer Transformation | Thermal headroom (MW) | 11.25 | 11.29 | 11.27 | 11.21 | 11.06 | 10.7 | 10.29 | 9.91 | 9.56 | 9.19 | 8.55 | 7.62 | 6.67 | 5.77 | 4.89 | 0.66 | -1.34 | -2.25
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Leading the Way | Thermal headroom (MW) | 11.25 | 11.19 | 11.08 | 10.93 | 10.67 | 10.14 | 9.49 | 8.75 | 8.09 | 7.11 | 6.33 | 5.53 | 4.74 | 3.96 | 3.27 | 0.57 | -0.19 | -0.38
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Steady Progression | Thermal headroom (MW) | 11.25 | 11.38 | 11.43 | 11.47 | 11.48 | 11.3 | 11.11 | 10.91 | 10.7 | 10.47 | 10.08 | 9.72 | 9.31 | 8.88 | 8.42 | 4.5 | 2.89 | 2.45
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | System Transformation | Thermal headroom (MW) | 11.25 | 11.34 | 11.34 | 11.34 | 11.27 | 11.19 | 11.08 | 10.94 | 10.79 | 10.63 | 10.33 | 9.98 | 9.63 | 9.3 | 9 | 5.67 | 3.32 | 2.8
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | WPD Best View | Thermal headroom (MW) | 11.25 | 11.36 | 11.4 | 11.43 | 11.4 | 11.25 | 11.07 | 10.89 | 10.7 | 10.5 | 10.16 | 9.82 | 9.43 | 9 | 8.53 | 4.87 | 3.03 | 2.57
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Consumer Transformation | Thermal headroom (MW) | 12.01 | 11.8 | 11.34 | 10.46 | 9.16 | 7.46 | 5.61 | 3.68 | 1.75 | -0.03 | -3.24 | -7.62 | -12.1 | -16.36 | -20.51 | -42.83 | -55.64 | -61.12
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Leading the Way | Thermal headroom (MW) | 12.01 | 11.31 | 10.3 | 8.92 | 6.95 | 3.91 | 0.83 | -2.78 | -6.77 | -10.85 | -15.43 | -20.24 | -24.98 | -29.52 | -33.67 | -46.51 | -50.92 | -51.97
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Steady Progression | Thermal headroom (MW) | 12.01 | 12.41 | 12.52 | 12.45 | 12.26 | 11.64 | 10.91 | 10.07 | 9.03 | 7.93 | 6.55 | 5.15 | 3.66 | 2.11 | 0.53 | -9.68 | -16.41 | -19.15
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | System Transformation | Thermal headroom (MW) | 12.01 | 12.23 | 12.13 | 11.82 | 11.29 | 10.72 | 9.89 | 8.82 | 7.61 | 6.34 | 4.92 | 3.03 | 1.1 | -0.78 | -2.49 | -14.08 | -19.59 | -21.57
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | WPD Best View | Thermal headroom (MW) | 12.01 | 12.39 | 12.48 | 12.38 | 12.15 | 11.48 | 10.72 | 9.81 | 8.74 | 7.62 | 6.23 | 4.83 | 3.35 | 1.82 | 0.27 | -10.74 | -17.63 | -20.45
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Consumer Transformation | Thermal headroom (MW) | 7.546 | 7.5695 | 7.226 | 6.7303 | 5.9885 | 4.7821 | 3.5526 | 2.3204 | 1.0272 | -0.50082 | -3.1829 | -5.7648 | -8.6522 | -11.7677 | -14.7698 | -30.9017 | -41.0347 | -46.2088
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Leading the Way | Thermal headroom (MW) | 7.546 | 7.2806 | 6.4733 | 5.5961 | 4.3563 | 2.3409 | 0.33129 | -2.0017 | -4.5596 | -7.4246 | -10.152 | -13.283 | -16.5156 | -19.6628 | -22.5887 | -32.8119 | -36.8372 | -38.6027
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Steady Progression | Thermal headroom (MW) | 7.546 | 8.0685 | 8.1839 | 8.2633 | 8.2666 | 7.8548 | 7.4044 | 6.8915 | 6.3146 | 5.6465 | 4.6762 | 3.6774 | 2.6052 | 1.4175 | 0.1206 | -7.8543 | -13.0478 | -15.0902
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | System Transformation | Thermal headroom (MW) | 7.546 | 7.9327 | 7.881 | 7.7724 | 7.499 | 7.1642 | 6.7396 | 6.1948 | 5.537 | 4.7699 | 3.5662 | 2.2319 | 0.83895 | -0.55217 | -1.8596 | -9.9942 | -14.7576 | -15.942
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | WPD Best View | Thermal headroom (MW) | 7.546 | 7.9411 | 7.9356 | 7.8872 | 7.7023 | 7.0973 | 6.4778 | 5.7991 | 5.0631 | 4.1794 | 3.0128 | 1.7861 | 0.48674 | -0.86033 | -2.2514 | -10.1669 | -15.6147 | -17.6867
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Consumer Transformation | Thermal headroom (MW) | 0.73 | 0.84 | 0.8 | 0.74 | 0.55 | 0.2 | -0.08 | -0.33 | -0.59 | -0.94 | -1.64 | -2.33 | -3.03 | -3.73 | -4.36 | -8.58 | -10.89 | -11.85
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Leading the Way | Thermal headroom (MW) | 0.73 | 0.61 | 0.37 | 0.12 | -0.29 | -0.98 | -1.55 | -2.13 | -2.7 | -3.39 | -4.1 | -4.87 | -5.64 | -6.33 | -6.95 | -9.37 | -10.21 | -10.51
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Steady Progression | Thermal headroom (MW) | 0.73 | 0.94 | 1.02 | 1.08 | 1.11 | 1.02 | 0.95 | 0.82 | 0.7 | 0.58 | 0.36 | 0.15 | -0.07 | -0.34 | -0.66 | -2.55 | -3.34 | -3.47
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | System Transformation | Thermal headroom (MW) | 0.73 | 0.92 | 0.97 | 1 | 0.98 | 0.87 | 0.78 | 0.71 | 0.63 | 0.52 | 0.32 | 0.06 | -0.24 | -0.54 | -0.84 | -2.69 | -3.46 | -3.66
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | WPD Best View | Thermal headroom (MW) | 0.73 | 0.67 | 0.5 | 0.31 | -0.03 | -0.62 | -1.09 | -1.61 | -2.1 | -2.71 | -3.37 | -4.07 | -4.78 | -5.41 | -5.97 | -8.37 | -9.21 | -9.42
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Consumer Transformation | Thermal headroom (MW) | 1.15 | 1.4 | 1.46 | 1.47 | 1.42 | 1.24 | 1.06 | 0.88 | 0.69 | 0.48 | 0.15 | -0.12 | -0.49 | -0.89 | -1.4 | -5.2 | -6.96 | -7.59
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Leading the Way | Thermal headroom (MW) | 1.15 | 1.33 | 1.32 | 1.27 | 1.12 | 0.79 | 0.46 | 0.1 | -0.27 | -0.75 | -1.11 | -1.47 | -1.85 | -2.47 | -2.99 | -5.08 | -5.59 | -5.56
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Steady Progression | Thermal headroom (MW) | 1.15 | 1.47 | 1.6 | 1.72 | 1.81 | 1.8 | 1.78 | 1.74 | 1.67 | 1.57 | 1.38 | 1.19 | 0.98 | 0.77 | 0.55 | -1.15 | -1.94 | -2.11
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | System Transformation | Thermal headroom (MW) | 1.15 | 1.45 | 1.55 | 1.63 | 1.67 | 1.72 | 1.71 | 1.69 | 1.63 | 1.54 | 1.35 | 1.14 | 0.91 | 0.69 | 0.51 | -0.54 | -1.87 | -2.02
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | WPD Best View | Thermal headroom (MW) | 1.15 | 1.45 | 1.55 | 1.63 | 1.67 | 1.71 | 1.71 | 1.68 | 1.61 | 1.53 | 1.33 | 1.12 | 0.9 | 0.68 | 0.5 | -0.57 | -1.86 | -2
Bishops Wood 132kV | Stourport 132 33 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Consumer Transformation | Thermal headroom (MW) | 7.57 | 7.19 | 6.73 | 6.1 | 5.08 | 3.4 | 1.78 | 0.06 | -1.7 | -4.35 | -9.05 | -13.87 | -18.67 | -23.41 | -28.08 | -48.92 | -68.04 | -80.75
Bishops Wood 132kV | Stourport 132 33 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Leading the Way | Thermal headroom (MW) | 7.57 | 6.99 | 5.98 | 4.81 | 2.99 | 0.18 | -2.55 | -5.64 | -9.83 | -14.55 | -18.38 | -22.76 | -27.53 | -32.14 | -36.48 | -50.82 | -59.54 | -65.49
Bishops Wood 132kV | Stourport 132 33 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Steady Progression | Thermal headroom (MW) | 7.57 | 8 | 8.05 | 8.07 | 8 | 7.34 | 6.69 | 5.97 | 5.24 | 4.46 | 3.33 | 2.16 | 0.88 | -0.44 | -2.27 | -14.24 | -21.99 | -24.55
Bishops Wood 132kV | Stourport 132 33 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | System Transformation | Thermal headroom (MW) | 7.57 | 7.78 | 7.66 | 7.43 | 6.92 | 6.47 | 5.99 | 5.33 | 4.48 | 3.61 | 1.95 | -0.01 | -2.09 | -4.33 | -6.64 | -19.81 | -26.34 | -27.83
Bishops Wood 132kV | Stourport 132 33 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | WPD Best View | Thermal headroom (MW) | 7.57 | 8 | 8.05 | 8.07 | 8 | 7.34 | 6.69 | 5.98 | 5.25 | 4.47 | 3.35 | 2.19 | 0.91 | -0.39 | -2.22 | -14.17 | -21.96 | -24.53
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Consumer Transformation | Thermal headroom (MW) | 8.01 | 8.07 | 7.85 | 7.58 | 7.26 | 6.76 | 6.23 | 5.68 | 5.11 | 4.52 | 3.74 | 3.07 | 2.05 | 0.7 | -0.57 | -7.9 | -11.85 | -13.72
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Leading the Way | Thermal headroom (MW) | 8.01 | 7.95 | 7.59 | 7.19 | 6.73 | 5.95 | 5.13 | 4.18 | 3.21 | 2.17 | 1.22 | -0.12 | -1.51 | -2.8 | -4.04 | -8.85 | -10.4 | -11.01
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Steady Progression | Thermal headroom (MW) | 8.01 | 8.25 | 8.28 | 8.31 | 8.31 | 8.11 | 7.88 | 7.62 | 7.32 | 6.96 | 6.46 | 5.93 | 5.37 | 4.78 | 4.18 | 0.81 | -1.59 | -2.71
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | System Transformation | Thermal headroom (MW) | 8.01 | 8.19 | 8.12 | 8.05 | 7.93 | 7.77 | 7.58 | 7.3 | 6.96 | 6.56 | 6.01 | 5.4 | 4.78 | 4.19 | 3.66 | 0.37 | -2.16 | -2.76
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | WPD Best View | Thermal headroom (MW) | 8.01 | 8.25 | 8.27 | 8.3 | 8.3 | 8.11 | 7.89 | 7.63 | 7.33 | 6.96 | 6.46 | 5.93 | 5.36 | 4.77 | 4.18 | 0.88 | -1.58 | -2.71
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Consumer Transformation | Thermal headroom (MW) | -8.736 | -9.4123 | -10.4356 | -11.9073 | -14.3505 | -18.5343 | -22.6584 | -26.8667 | -31.5006 | -37.858 | -48.3187 | -58.8625 | -69.4545 | -79.7814 | -89.8667 | -133.9457 | -167.4742 | -188.1947
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Leading the Way | Thermal headroom (MW) | -8.736 | -10.1195 | -12.4158 | -14.9147 | -18.769 | -25.2001 | -31.8862 | -39.6762 | -48.5356 | -58.6384 | -67.6572 | -77.3636 | -87.2763 | -96.8164 | -105.4498 | -134.1836 | -147.305 | -154.0453
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Steady Progression | Thermal headroom (MW) | -8.736 | -8.0481 | -8.0324 | -8.1264 | -8.6462 | -10.3828 | -12.0351 | -13.8447 | -15.765 | -18.4081 | -21.8914 | -24.9662 | -28.5473 | -32.687 | -37.202 | -65.9098 | -82.2965 | -87.862
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | System Transformation | Thermal headroom (MW) | -8.736 | -8.4259 | -8.81 | -9.3625 | -10.6418 | -11.9991 | -13.2979 | -15.1222 | -17.4975 | -19.8631 | -23.2279 | -26.9644 | -31.7017 | -37.0019 | -42.691 | -72.7758 | -88.075 | -92.5371
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | WPD Best View | Thermal headroom (MW) | -8.736 | -8.1749 | -8.2897 | -8.5182 | -9.2524 | -10.9973 | -12.699 | -14.5833 | -16.6447 | -19.4463 | -23.0177 | -26.2506 | -30.4377 | -34.9812 | -39.8928 | -68.8003 | -83.0928 | -87.5003
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Consumer Transformation | Thermal headroom (MW) | 11.4 | 11.05 | 10.75 | 10.21 | 9.33 | 7.1 | 4.97 | 2.84 | 0.47 | -2.24 | -7.87 | -13.59 | -19.29 | -24.93 | -30.67 | -53.54 | -79.06 | -96.71
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Leading the Way | Thermal headroom (MW) | 11.4 | 10.71 | 9.36 | 8.15 | 6.47 | 2.97 | -0.26 | -3.64 | -7.86 | -12.56 | -16.43 | -20.77 | -25.31 | -29.8 | -33.97 | -47.6 | -54.6 | -58.97
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Steady Progression | Thermal headroom (MW) | 11.4 | 11.81 | 11.92 | 11.98 | 11.89 | 10.91 | 10.24 | 9.56 | 8.76 | 7.02 | 4.83 | 3.67 | 2 | -0.01 | -1.86 | -12.96 | -19.74 | -22.4
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | System Transformation | Thermal headroom (MW) | 11.4 | 11.7 | 11.63 | 11.46 | 11.09 | 10.16 | 9.64 | 8.96 | 7.91 | 6.9 | 5.27 | 3.46 | 1.51 | -0.58 | -3.13 | -15.54 | -21.64 | -23.69
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | WPD Best View | Thermal headroom (MW) | 11.4 | 11.81 | 11.92 | 11.98 | 11.89 | 10.91 | 10.24 | 9.56 | 8.76 | 7.02 | 4.83 | 3.67 | 2 | -0.01 | -1.86 | -12.96 | -19.74 | -22.4
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Consumer Transformation | Thermal headroom (MW) | 27.07 | 26.79 | 26.29 | 25.71 | 24.07 | 22.48 | 21.01 | 19.33 | 17.54 | 15.45 | 12.19 | 8.9 | 5.55 | 2.31 | -0.69 | -15.11 | -21.93 | -24.51
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Leading the Way | Thermal headroom (MW) | 27.07 | 26.3 | 25.27 | 24.2 | 21.7 | 19.21 | 17.12 | 14.59 | 11.97 | 8.98 | 5.58 | 2.01 | -1.52 | -4.84 | -7.8 | -15.69 | -17.48 | -16.65
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Steady Progression | Thermal headroom (MW) | 27.07 | 27.32 | 27.27 | 27.24 | 26.49 | 25.79 | 25.23 | 24.61 | 23.95 | 23.18 | 22.2 | 21.13 | 19.93 | 18.63 | 17.28 | 7.69 | 1.28 | -0.33
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | System Transformation | Thermal headroom (MW) | 27.07 | 27.14 | 26.94 | 26.74 | 25.61 | 24.83 | 24.23 | 23.51 | 22.72 | 21.7 | 20.42 | 18.94 | 17.23 | 15.4 | 13.52 | 3.56 | -0.19 | -0.14
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | WPD Best View | Thermal headroom (MW) | 27.07 | 27.31 | 27.25 | 27.2 | 26.37 | 25.61 | 25.06 | 24.43 | 23.74 | 22.89 | 21.79 | 20.53 | 19.08 | 17.55 | 15.97 | 6.22 | 0.58 | -0.51
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Consumer Transformation | Thermal headroom (MW) | 14.22 | 13.64 | 12.75 | 11.63 | 10.04 | 8 | 5.87 | 3.82 | 1.23 | -2.67 | -8.53 | -14.41 | -20.28 | -25.9 | -31.27 | -56.6 | -70.11 | -75.86
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Leading the Way | Thermal headroom (MW) | 14.22 | 13.17 | 11.74 | 10.16 | 8.01 | 4.82 | 0.8 | -3.93 | -8.61 | -14.37 | -20.27 | -26.44 | -32.5 | -38.21 | -43.06 | -58.49 | -63.24 | -63.15
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Steady Progression | Thermal headroom (MW) | 14.22 | 14.42 | 14.31 | 14.14 | 13.85 | 13.12 | 12.25 | 11.33 | 10.36 | 9.02 | 7.46 | 5.89 | 4.1 | 1.62 | -1 | -18.34 | -29.1 | -32.67
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | System Transformation | Thermal headroom (MW) | 14.22 | 14.16 | 13.79 | 13.35 | 12.65 | 11.99 | 11.05 | 9.97 | 8.67 | 7.08 | 5.4 | 3.6 | 0.33 | -3.21 | -6.85 | -24.97 | -32.28 | -33.7
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | WPD Best View | Thermal headroom (MW) | 14.22 | 14.18 | 13.83 | 13.41 | 12.76 | 12.06 | 11.09 | 10.05 | 8.83 | 7.23 | 5.57 | 3.81 | 1.01 | -2.11 | -5.35 | -22.99 | -30.18 | -31.86
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Consumer Transformation | Thermal headroom (MW) | 18.51 | 18.19 | 17.13 | 16.34 | 15.33 | 13.82 | 12.09 | 10.16 | 8.28 | 6.22 | 3.78 | 0.42 | -3.14 | -6.69 | -9.84 | -27.42 | -37.29 | -41.7
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Leading the Way | Thermal headroom (MW) | 18.51 | 17.83 | 16.27 | 15.11 | 13.56 | 11.18 | 8.7 | 5.66 | 2.56 | -1.17 | -4.85 | -8.61 | -12.36 | -16.01 | -19.07 | -29.62 | -33.44 | -34.6
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Steady Progression | Thermal headroom (MW) | 18.51 | 18.68 | 18.22 | 18.07 | 17.9 | 17.32 | 16.67 | 15.82 | 14.85 | 13.79 | 12.52 | 11.2 | 9.79 | 8.3 | 6.89 | -0.39 | -6.02 | -8.52
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | System Transformation | Thermal headroom (MW) | 18.51 | 18.54 | 17.82 | 17.49 | 17.07 | 16.54 | 15.79 | 14.73 | 13.58 | 12.25 | 10.87 | 9.42 | 7.94 | 6.48 | 5.35 | -2.6 | -7.28 | -8.89
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | WPD Best View | Thermal headroom (MW) | 18.51 | 18.68 | 18.22 | 18.07 | 17.9 | 17.32 | 16.67 | 15.82 | 14.85 | 13.79 | 12.52 | 11.2 | 9.79 | 8.3 | 6.89 | -0.39 | -6.02 | -8.52
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Consumer Transformation | Thermal headroom (MW) | 41.71 | 41.1 | 40.43 | 39.49 | 37.69 | 35.16 | 33.12 | 30.76 | 27.46 | 24.26 | 18.98 | 13.68 | 8.24 | 2.83 | -2.48 | -29.57 | -46.43 | -53.35
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Leading the Way | Thermal headroom (MW) | 41.71 | 40.75 | 38.95 | 37.26 | 33.89 | 29.32 | 26.06 | 21.69 | 15.97 | 10.49 | 4.64 | -1 | -6.58 | -12.05 | -17.27 | -34.76 | -41.37 | -42.89
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Steady Progression | Thermal headroom (MW) | 41.71 | 42.2 | 42.25 | 42.15 | 41.5 | 40.34 | 39.55 | 38.54 | 37.12 | 35.55 | 33.71 | 31.91 | 30.02 | 27.75 | 25.46 | 11.32 | 2.2 | -2.13
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | System Transformation | Thermal headroom (MW) | 41.71 | 41.93 | 41.7 | 41.29 | 40.16 | 38.97 | 38.21 | 37.01 | 35.15 | 33.32 | 30.94 | 28.66 | 26.35 | 24.1 | 22.06 | 6.86 | 0.2 | -2.06
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | WPD Best View | Thermal headroom (MW) | 41.71 | 42.2 | 42.25 | 42.15 | 41.5 | 40.34 | 39.55 | 38.54 | 37.12 | 35.55 | 33.71 | 31.91 | 30.02 | 27.75 | 25.46 | 11.32 | 2.2 | -2.13
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Consumer Transformation | Thermal headroom (MW) | 48.47 | 48.33 | 47.89 | 47.17 | 45.98 | 44.13 | 41.86 | 39.63 | 37.17 | 33.71 | 24.74 | 15.75 | 6.7 | -2.11 | -11.02 | -37.9 | -71.29 | -94.84
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Leading the Way | Thermal headroom (MW) | 48.47 | 47.88 | 46.91 | 45.69 | 43.45 | 40.19 | 36.22 | 31.55 | 24.64 | 17.59 | 11.89 | 5.18 | -2.2 | -9.46 | -15.84 | -29.66 | -35.57 | -38.46
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Steady Progression | Thermal headroom (MW) | 48.47 | 48.98 | 49.19 | 49.31 | 49.17 | 48.55 | 47.85 | 47.13 | 46.22 | 43.34 | 39.69 | 38.34 | 36.79 | 34.59 | 32.68 | 19.39 | 11.47 | 9.07
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | System Transformation | Thermal headroom (MW) | 48.47 | 48.49 | 48.29 | 47.87 | 47.1 | 46.3 | 45.19 | 43.89 | 42.18 | 40.77 | 37.43 | 35.47 | 31.83 | 28.63 | 24.42 | 7.89 | -1.28 | -5.57
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | WPD Best View | Thermal headroom (MW) | 48.47 | 48.98 | 49.19 | 49.31 | 49.17 | 48.55 | 47.85 | 47.13 | 46.22 | 43.34 | 39.69 | 38.34 | 36.79 | 34.59 | 32.68 | 19.39 | 11.47 | 9.07
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Consumer Transformation | Thermal headroom (MW) | 24.2 | 23.97 | 23.34 | 22.46 | 21.18 | 18.54 | 16.24 | 13.74 | 11.09 | 7.88 | 2.07 | -4.76 | -11.61 | -17.95 | -24.17 | -58.17 | -77.82 | -85.7
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Leading the Way | Thermal headroom (MW) | 24.2 | 23.54 | 22.05 | 20.38 | 18.09 | 12.96 | 8.9 | 4.41 | -1.56 | -8.07 | -15.5 | -22.91 | -30.18 | -36.77 | -43.02 | -64.53 | -72.12 | -74.33
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Steady Progression | Thermal headroom (MW) | 24.2 | 25.12 | 25.37 | 25.47 | 25.44 | 24.32 | 23.51 | 22.56 | 21.45 | 20.19 | 18.14 | 16.09 | 13.87 | 11.71 | 9.2 | -5.57 | -15.66 | -19.82
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | System Transformation | Thermal headroom (MW) | 24.2 | 24.87 | 24.82 | 24.59 | 24.11 | 22.86 | 21.94 | 20.75 | 19.12 | 17.22 | 14.18 | 11.13 | 8.07 | 5.28 | 2.74 | -13.24 | -20.58 | -23.16
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | WPD Best View | Thermal headroom (MW) | 24.2 | 23.84 | 23.08 | 22.04 | 20.58 | 17.36 | 14.79 | 11.7 | 8.39 | 4.45 | -2.83 | -9.9 | -16.85 | -23.18 | -29.3 | -60.01 | -77.29 | -84.01
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Consumer Transformation | Thermal headroom (MW) | 8.08 | 1.98 | 1.29 | 0.46 | -0.71 | -2.72 | -4.64 | -6.82 | -8.81 | -10.95 | -13.94 | -16.92 | -19.92 | -22.75 | -25.44 | -39.63 | -46.06 | -48.28
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Leading the Way | Thermal headroom (MW) | 8.08 | 0.83 | -0.28 | -1.46 | -2.64 | -5.92 | -9.28 | -12.8 | -15.84 | -19.12 | -22.1 | -25.17 | -28.11 | -30.86 | -33.02 | -41.06 | -43.31 | -43.6
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Steady Progression | Thermal headroom (MW) | 8.08 | 3.06 | 2.73 | 2.3 | 1.67 | 0.35 | -0.93 | -2.59 | -3.73 | -4.93 | -6.21 | -7.43 | -8.7 | -10.1 | -11.48 | -19.99 | -23.39 | -24.62
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | System Transformation | Thermal headroom (MW) | 8.08 | 2.21 | 1.74 | 1.2 | 0.39 | -0.95 | -2.13 | -3.59 | -4.83 | -6.16 | -7.48 | -8.84 | -10.57 | -12.3 | -14.06 | -23.13 | -26.58 | -26.86
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | WPD Best View | Thermal headroom (MW) | 8.08 | 1.84 | 0.9 | -0.1 | -1.47 | -4.47 | -7.43 | -10.5 | -13.1 | -15.88 | -18.51 | -21.18 | -23.75 | -26.19 | -28.13 | -36.19 | -38.89 | -39.25
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Consumer Transformation | Thermal headroom (MW) | 9.28 | 9.29 | 9.1 | 8.82 | 8.24 | 7.57 | 6.71 | 5.83 | 4.9 | 3.88 | 1.5 | -1.27 | -4.11 | -6.78 | -9.52 | -22.06 | -30.1 | -34.44
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Leading the Way | Thermal headroom (MW) | 9.28 | 9.14 | 8.8 | 8.39 | 7.55 | 6.55 | 5.13 | 3.55 | 1.39 | -1.14 | -3.74 | -6.63 | -9.65 | -12.47 | -14.82 | -24.09 | -27.7 | -29.3
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Steady Progression | Thermal headroom (MW) | 9.28 | 9.49 | 9.51 | 9.49 | 9.41 | 9.16 | 8.79 | 8.38 | 7.89 | 7.34 | 6.64 | 5.91 | 5.06 | 4.18 | 3.29 | -4.51 | -8.05 | -9.2
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | System Transformation | Thermal headroom (MW) | 9.28 | 9.42 | 9.36 | 9.27 | 9.01 | 8.76 | 8.29 | 7.74 | 7.12 | 6.41 | 5.57 | 4.65 | 3.35 | 2.12 | 0.56 | -7.85 | -10.8 | -11.07
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | WPD Best View | Thermal headroom (MW) | 9.28 | 9.14 | 8.8 | 8.39 | 7.55 | 6.55 | 5.13 | 3.55 | 1.39 | -1.14 | -3.74 | -6.63 | -9.65 | -12.47 | -14.82 | -24.09 | -27.7 | -29.3
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Consumer Transformation | Thermal headroom (MW) | 58.68 | 59.03 | 59.17 | 59.29 | 59.39 | 59.42 | 59.44 | 59.46 | 59.48 | 59.48 | 59.34 | 59.23 | 59.17 | 59.14 | 59.12 | 58.21 | 57.89 | 57.97
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Leading the Way | Thermal headroom (MW) | 58.68 | 58.98 | 59.07 | 59.14 | 59.19 | 59.15 | 59.1 | 59.04 | 59 | 58.95 | 58.89 | 58.85 | 58.85 | 58.78 | 58.67 | 58.55 | 58.75 | 59.2
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Steady Progression | Thermal headroom (MW) | 58.68 | 59.09 | 59.29 | 59.48 | 59.66 | 59.79 | 59.92 | 60.04 | 60.14 | 60.23 | 60.29 | 60.34 | 60.39 | 60.43 | 60.45 | 60.01 | 60.07 | 60.51
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | System Transformation | Thermal headroom (MW) | 58.68 | 59.07 | 59.25 | 59.42 | 59.57 | 59.71 | 59.83 | 59.93 | 60.02 | 60.09 | 60.14 | 60.16 | 60.16 | 60.14 | 60.13 | 60.01 | 60.15 | 60.81
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | WPD Best View | Thermal headroom (MW) | 58.68 | 59.03 | 59.17 | 59.29 | 59.39 | 59.41 | 59.42 | 59.43 | 59.44 | 59.42 | 59.27 | 59.16 | 59.09 | 59.06 | 59.04 | 58.14 | 57.82 | 57.91
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Consumer Transformation | Thermal headroom (MW) | 45.68 | 44.05 | 43.02 | 41.68 | 38.92 | 34.71 | 29.76 | 24.86 | 20.36 | 15.44 | 6.36 | -2.78 | -11.92 | -20.88 | -30 | -59.99 | -97.72 | -124.59
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Leading the Way | Thermal headroom (MW) | 45.68 | 43.57 | 41.32 | 39.23 | 35.06 | 28.9 | 22.05 | 14.49 | 5.1 | -4.95 | -10.93 | -18.44 | -26.91 | -35.15 | -42.74 | -67.97 | -88.16 | -105.69
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Steady Progression | Thermal headroom (MW) | 45.68 | 45.18 | 44.87 | 44.51 | 43.43 | 41.5 | 39.5 | 37.52 | 35.8 | 31.58 | 26.44 | 24.36 | 21.63 | 18.03 | 15.18 | -1.51 | -11.16 | -14.43
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | System Transformation | Thermal headroom (MW) | 45.68 | 44.76 | 44.14 | 43.37 | 41.62 | 39.35 | 36.65 | 33.93 | 31.53 | 29.19 | 24.88 | 21.96 | 17.58 | 13.97 | 8.98 | -12.28 | -24.74 | -29.68
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | WPD Best View | Thermal headroom (MW) | 45.68 | 45.18 | 44.87 | 44.51 | 43.43 | 41.5 | 39.5 | 37.52 | 35.8 | 31.58 | 26.44 | 24.36 | 21.63 | 18.03 | 15.18 | -1.5 | -11.16 | -14.44
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Consumer Transformation | Thermal headroom (MW) | 43.38 | 42.86 | 42.12 | 41.32 | 40.17 | 38.24 | 35.97 | 33.68 | 30.99 | 28.18 | 24.5 | 19.83 | 14.68 | 9.65 | 4.69 | -22.39 | -38.39 | -45.64
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Leading the Way | Thermal headroom (MW) | 43.38 | 42.65 | 40.89 | 39.52 | 37.64 | 34.29 | 30.5 | 26.1 | 21.32 | 15.79 | 10.47 | 4.97 | -0.58 | -5.94 | -11.09 | -28.21 | -35.49 | -38.76
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Steady Progression | Thermal headroom (MW) | 43.38 | 43.9 | 43.9 | 43.93 | 43.87 | 43.25 | 42.36 | 41.32 | 40.04 | 38.52 | 36.72 | 34.98 | 33.12 | 30.8 | 28.5 | 16.28 | 7.64 | 3.74
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | System Transformation | Thermal headroom (MW) | 43.38 | 43.68 | 43.41 | 43.15 | 42.71 | 42.16 | 41.08 | 39.67 | 38.01 | 36.29 | 33.92 | 31.55 | 29.03 | 26.7 | 24.5 | 10.59 | 2.37 | -0.68
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | WPD Best View | Thermal headroom (MW) | 43.38 | 43.85 | 43.79 | 43.76 | 43.61 | 42.86 | 41.84 | 40.62 | 39.17 | 37.57 | 35.67 | 33.95 | 32.01 | 29.76 | 27.43 | 14.31 | 5.59 | 1.63
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Consumer Transformation | Thermal headroom (MW) | 33.3 | 32.82 | 31.96 | 31 | 29.68 | 27.44 | 25.24 | 22.64 | 19.83 | 16.34 | 10.58 | 3.62 | -3.75 | -10.96 | -18.15 | -52.66 | -73.77 | -82.82
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Leading the Way | Thermal headroom (MW) | 33.3 | 32.36 | 30.56 | 28.81 | 26.22 | 22.18 | 18.57 | 14.3 | 9.14 | 2.73 | -4.71 | -12.51 | -20.41 | -28.04 | -35.33 | -58.41 | -67.43 | -70.24
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Steady Progression | Thermal headroom (MW) | 33.3 | 34.03 | 34.14 | 34.25 | 34.25 | 33.6 | 32.96 | 32.1 | 31 | 29.58 | 27.63 | 25.59 | 23.39 | 21.03 | 18.27 | 4.31 | -8.02 | -13.79
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | System Transformation | Thermal headroom (MW) | 33.3 | 33.75 | 33.51 | 33.29 | 32.82 | 32.12 | 31.47 | 30.23 | 28.63 | 26.7 | 23.71 | 20.16 | 16.53 | 12.96 | 9.65 | -6.49 | -15.33 | -18.47
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | WPD Best View | Thermal headroom (MW) | 33.3 | 33.51 | 32.99 | 32.41 | 31.6 | 30.1 | 28.57 | 26.41 | 24.06 | 21.4 | 17.34 | 12.93 | 7.88 | 2.6 | -3.07 | -29.35 | -46.1 | -53.6
Bustleholm 132kV | Bentley 132 11 (GT2A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Consumer Transformation | Thermal headroom (MW) | 27.08 | 26.98 | 26.72 | 26.3 | 25.28 | 23.52 | 21.51 | 19.27 | 16.85 | 13.55 | 5.67 | -2.62 | -11.01 | -18.83 | -26.78 | -57.72 | -89.35 | -109.21
Bustleholm 132kV | Bentley 132 11 (GT2A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Leading the Way | Thermal headroom (MW) | 27.08 | 26.67 | 25.36 | 24.33 | 22.41 | 19.98 | 16.46 | 12.07 | 5.87 | -0.09 | -5.88 | -12.62 | -19.67 | -26.22 | -32.37 | -49.95 | -57.23 | -59.29
Bustleholm 132kV | Bentley 132 11 (GT2A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Steady Progression | Thermal headroom (MW) | 27.08 | 27.98 | 28.34 | 28.67 | 28.78 | 28.59 | 28.13 | 27.49 | 26.75 | 25.13 | 22.98 | 21.67 | 20.12 | 18.18 | 16.32 | 0.36 | -11.39 | -15.95
Bustleholm 132kV | Bentley 132 11 (GT2A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | System Transformation | Thermal headroom (MW) | 27.08 | 27.72 | 27.84 | 27.89 | 27.58 | 27.38 | 26.77 | 25.84 | 24.79 | 23.61 | 21.86 | 19.9 | 17.89 | 15.34 | 11.92 | -5.23 | -11.69 | -12.69
Bustleholm 132kV | Bentley 132 11 (GT2A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | WPD Best View | Thermal headroom (MW) | 27.08 | 27.97 | 28.33 | 28.65 | 28.76 | 28.57 | 28.12 | 27.49 | 26.74 | 25.13 | 22.98 | 21.68 | 20.12 | 18.16 | 16.14 | 0.12 | -11.43 | -15.89
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Consumer Transformation | Thermal headroom (MW) | 41.81 | 41.18 | 40.49 | 39.57 | 38.16 | 35.76 | 33.38 | 30.88 | 28.34 | 25.34 | 20.86 | 14.74 | 8.6 | 2.62 | -3.31 | -33.92 | -54.42 | -64.38
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Leading the Way | Thermal headroom (MW) | 41.81 | 40.8 | 39.26 | 37.43 | 34.77 | 30.9 | 27.22 | 23.21 | 18.83 | 13.47 | 7.27 | 0.85 | -5.63 | -12 | -17.98 | -38.61 | -48.26 | -52.52
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Steady Progression | Thermal headroom (MW) | 41.81 | 42.4 | 42.58 | 42.67 | 42.64 | 42.02 | 41.34 | 40.39 | 39.25 | 37.94 | 36.13 | 34.27 | 32.29 | 30.19 | 27.73 | 14.83 | 3.85 | -1.33
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | System Transformation | Thermal headroom (MW) | 41.81 | 42.14 | 42.01 | 41.77 | 41.33 | 40.8 | 39.93 | 38.67 | 37.14 | 35.55 | 32.96 | 30.19 | 27.37 | 24.67 | 21.85 | 7.86 | -0.85 | -4.93
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | WPD Best View | Thermal headroom (MW) | 41.81 | 42.23 | 42.22 | 42.09 | 41.82 | 41.25 | 40.47 | 39.27 | 37.81 | 36.29 | 33.8 | 31.17 | 28.48 | 25.83 | 23.31 | 9.03 | -0.89 | -5.61
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Consumer Transformation | Thermal headroom (MW) | 29.53 | 29.29 | 28.43 | 27.23 | 25.21 | 22.24 | 19.23 | 16.12 | 12.99 | 9.65 | 4.17 | -3.58 | -11.37 | -19.13 | -26.66 | -65.63 | -91.21 | -103.03
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Leading the Way | Thermal headroom (MW) | 29.53 | 28.38 | 26.44 | 24.08 | 20.62 | 15.78 | 11.14 | 6.11 | 0.95 | -5.48 | -13.38 | -21.57 | -30.02 | -38.2 | -45.84 | -72.69 | -84.13 | -88.53
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Steady Progression | Thermal headroom (MW) | 29.53 | 30.45 | 30.72 | 30.88 | 30.86 | 30.07 | 29.07 | 27.69 | 26.06 | 24.2 | 21.7 | 19.06 | 16.24 | 13.29 | 10.28 | -7.39 | -20.38 | -27.3
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | System Transformation | Thermal headroom (MW) | 29.53 | 30.11 | 29.99 | 29.72 | 29.16 | 28.33 | 27.06 | 25.46 | 23.58 | 21.33 | 18.38 | 14.86 | 11.26 | 7.66 | 3.86 | -13.83 | -24.43 | -28.78
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | WPD Best View | Thermal headroom (MW) | 29.53 | 29.01 | 27.77 | 26.35 | 24.38 | 20.82 | 17.38 | 13.66 | 9.98 | 6.07 | -0.21 | -6.67 | -13.19 | -19.72 | -26.09 | -51.17 | -63.07 | -67.98
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Consumer Transformation | Thermal headroom (MW) | 41.07 | 40.64 | 39.73 | 38.58 | 37.87 | 37.19 | 36.48 | 35.59 | 34.6 | 31.94 | 28.5 | 24.9 | 21.32 | 17.98 | 14.86 | 5.85 | 3 | 1.93
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Leading the Way | Thermal headroom (MW) | 41.07 | 40.57 | 39.48 | 38.23 | 37.61 | 37.06 | 36.37 | 35.27 | 32.66 | 29.49 | 26.31 | 22.88 | 19.55 | 16.57 | 14.04 | 10.3 | 12.81 | 18.16
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Steady Progression | Thermal headroom (MW) | 41.07 | 41.44 | 41.44 | 41.43 | 41.72 | 41.91 | 42.02 | 42.06 | 41.97 | 41.6 | 41.08 | 40.28 | 38.64 | 36.74 | 34.59 | 20.27 | 9.57 | 7.09
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | System Transformation | Thermal headroom (MW) | 41.07 | 41.12 | 40.78 | 40.4 | 40.37 | 40.78 | 41.13 | 41.37 | 41.34 | 41.08 | 39.88 | 37.91 | 35.59 | 32.85 | 29.87 | 15.9 | 12.93 | 14.43
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | WPD Best View | Thermal headroom (MW) | 41.07 | 40.57 | 39.48 | 38.23 | 37.61 | 37.06 | 36.37 | 35.27 | 32.66 | 29.49 | 26.31 | 22.88 | 19.55 | 16.57 | 14.04 | 10.3 | 12.81 | 18.16
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Consumer Transformation | Thermal headroom (MW) | 22.65 | 21.88 | 20.77 | 19.37 | 17.67 | 15.02 | 12.2 | 9.33 | 6.03 | 3 | -2.39 | -8.93 | -16.26 | -23.42 | -30.38 | -65.85 | -89.2 | -100.12
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Leading the Way | Thermal headroom (MW) | 22.65 | 21.24 | 18.7 | 16.32 | 13.57 | 8.95 | 4.59 | -0.5 | -5.58 | -11.54 | -18.84 | -26.48 | -34.05 | -41.44 | -48.34 | -70.45 | -79.38 | -82.41
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Steady Progression | Thermal headroom (MW) | 22.65 | 23.3 | 23.33 | 23.28 | 23.18 | 22.42 | 21.6 | 20.68 | 19.62 | 18.34 | 16.42 | 14.47 | 12.4 | 9.86 | 7.32 | -5.4 | -17.96 | -24.01
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | System Transformation | Thermal headroom (MW) | 22.65 | 22.9 | 22.45 | 21.9 | 21.22 | 20.44 | 19.56 | 18.28 | 16.56 | 14.94 | 12.17 | 9.23 | 6.25 | 3.36 | 0.75 | -12.61 | -20.86 | -24.07
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | WPD Best View | Thermal headroom (MW) | 22.65 | 21.25 | 18.71 | 16.34 | 13.62 | 9.01 | 4.67 | -0.39 | -5.4 | -11.32 | -18.6 | -26.19 | -33.72 | -41.07 | -47.96 | -70.14 | -79.08 | -82.1
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Consumer Transformation | Thermal headroom (MW) | 40.99 | 39.63 | 38.1 | 35.81 | 32.62 | 27.94 | 23.27 | 18.65 | 13.4 | 7.69 | -5.45 | -18.69 | -32.02 | -45.07 | -58.09 | -107.9 | -160.36 | -194.35
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Leading the Way | Thermal headroom (MW) | 40.99 | 37.65 | 33.73 | 29.58 | 24.08 | 17.22 | 10.37 | 2.92 | -6.5 | -16.35 | -26.41 | -37.5 | -49.13 | -60.59 | -71.02 | -100.02 | -113.11 | -118.97
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Steady Progression | Thermal headroom (MW) | 40.99 | 41.56 | 41.54 | 41.4 | 40.97 | 39.57 | 38.08 | 36.49 | 34.63 | 31.39 | 26.61 | 23.4 | 19.9 | 15.68 | 11.7 | -14.38 | -33.04 | -40.15
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | System Transformation | Thermal headroom (MW) | 40.99 | 41.05 | 40.5 | 39.81 | 38.63 | 37.25 | 35.65 | 33.57 | 31.02 | 28.38 | 24.86 | 20.51 | 15.7 | 10.44 | 5 | -22.91 | -33.27 | -36.12
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | WPD Best View | Thermal headroom (MW) | 40.99 | 41.56 | 41.54 | 41.4 | 40.97 | 39.57 | 38.08 | 36.49 | 34.63 | 31.39 | 26.61 | 23.4 | 19.9 | 15.68 | 11.7 | -14.37 | -33.04 | -40.14
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Consumer Transformation | Thermal headroom (MW) | 46.71 | 46.35 | 45.83 | 45.1 | 43.38 | 41.64 | 39.8 | 37.72 | 35.53 | 32.95 | 27.95 | 22.85 | 17.71 | 12.78 | 7.96 | -10.66 | -22.43 | -27.93
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Leading the Way | Thermal headroom (MW) | 46.71 | 45.73 | 44.56 | 43.26 | 40.53 | 38.22 | 35.74 | 32.77 | 29.54 | 25.87 | 21.06 | 15.88 | 10.68 | 5.76 | 1.6 | -9.51 | -13.33 | -12.66
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Steady Progression | Thermal headroom (MW) | 46.71 | 47.04 | 47.1 | 47.07 | 46.54 | 46.09 | 45.51 | 44.88 | 44.22 | 43.38 | 42.26 | 41.15 | 39.84 | 38.4 | 36.83 | 24.22 | 13.69 | 9.24
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | System Transformation | Thermal headroom (MW) | 46.71 | 46.77 | 46.59 | 46.29 | 45.27 | 44.63 | 43.89 | 43 | 42.04 | 40.91 | 39.44 | 37.38 | 34.73 | 31.9 | 28.94 | 15.07 | 9.72 | 9.65
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | WPD Best View | Thermal headroom (MW) | 46.71 | 46.49 | 46.04 | 45.46 | 44.11 | 43.1 | 42.02 | 40.75 | 39.36 | 37.72 | 35.24 | 32.19 | 28.93 | 25.53 | 22.48 | 9.25 | 4.54 | 4.82
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Consumer Transformation | Thermal headroom (MW) | 45.67 | 43.88 | 42.1 | 40.01 | 37.41 | 33.85 | 30.43 | 26.8 | 22.76 | 17.98 | 11.1 | 4.13 | -2.88 | -9.54 | -15.95 | -40.04 | -50.06 | -54.14
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Leading the Way | Thermal headroom (MW) | 45.67 | 43.14 | 40.23 | 37.07 | 33.39 | 29.26 | 25.27 | 20.51 | 14.99 | 9.19 | 2.23 | -4.98 | -12.06 | -18.66 | -24.53 | -37.51 | -38.16 | -33.9
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Steady Progression | Thermal headroom (MW) | 45.67 | 45.41 | 44.78 | 44.16 | 43.54 | 42.41 | 41.18 | 39.86 | 38.33 | 36.67 | 34.6 | 32.42 | 29.91 | 27.14 | 23.76 | 2.25 | -14.53 | -20.76
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | System Transformation | Thermal headroom (MW) | 45.67 | 44.94 | 43.84 | 42.67 | 41.37 | 40.06 | 38.67 | 37.02 | 35.11 | 33 | 30.04 | 26.64 | 22.75 | 18.51 | 14.01 | -7.52 | -14.19 | -14.13
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | WPD Best View | Thermal headroom (MW) | 45.67 | 43.17 | 40.32 | 37.26 | 33.75 | 29.82 | 25.94 | 21.35 | 16.08 | 10.53 | 3.75 | -3.32 | -10.29 | -16.78 | -22.57 | -35.73 | -36.52 | -32.41
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Consumer Transformation | Thermal headroom (MW) | 12.11 | 12.09 | 11.27 | 10.55 | 9.31 | 6.92 | 4.2 | 1.47 | -1.19 | -4.09 | -8.96 | -14.53 | -20.11 | -25.57 | -30.8 | -54.38 | -67.87 | -73.74
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Leading the Way | Thermal headroom (MW) | 12.11 | 11.51 | 10 | 8.73 | 6.85 | 3.6 | -0.16 | -4.1 | -8.77 | -14.76 | -20.78 | -26.56 | -32.3 | -37.73 | -42.66 | -57.43 | -62.09 | -62.74
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Steady Progression | Thermal headroom (MW) | 12.11 | 12.77 | 12.66 | 12.78 | 12.72 | 11.89 | 10.99 | 10.1 | 9.09 | 7.88 | 6.4 | 4.91 | 3.36 | 1.73 | 0.13 | -11.61 | -21.05 | -24.93
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | System Transformation | Thermal headroom (MW) | 12.11 | 12.53 | 12.12 | 11.96 | 11.52 | 10.5 | 9.26 | 8.06 | 6.61 | 4.66 | 2.69 | 0.41 | -1.89 | -4.13 | -6.19 | -20.18 | -25.68 | -26.73
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | WPD Best View | Thermal headroom (MW) | 12.11 | 11.78 | 10.57 | 9.6 | 8.07 | 5.41 | 2.62 | -0.75 | -4.47 | -9.82 | -15.2 | -20.29 | -25.33 | -30.06 | -34.37 | -47.61 | -52.11 | -52.78
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Consumer Transformation | Thermal headroom (MW) | 36.52 | 35.54 | 34.58 | 29.97 | 28.08 | 24.65 | 20.98 | 16.56 | 12.06 | 7.1 | -2.33 | -11.83 | -21.39 | -30.65 | -39.98 | -75.02 | -111.32 | -134.64
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Leading the Way | Thermal headroom (MW) | 36.52 | 34.65 | 32.1 | 26.36 | 22.99 | 18.14 | 13.18 | 6.72 | -0.83 | -8.67 | -15.99 | -24.09 | -32.5 | -40.66 | -48.18 | -69.6 | -79.39 | -83.69
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Steady Progression | Thermal headroom (MW) | 36.52 | 36.96 | 36.99 | 36.93 | 36.65 | 35.43 | 34.31 | 32.84 | 31.27 | 28.84 | 25.72 | 23.56 | 20.82 | 17.68 | 14.67 | -4.5 | -18.61 | -24.13
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | System Transformation | Thermal headroom (MW) | 36.52 | 36.61 | 36.26 | 35.8 | 35 | 30.32 | 28.99 | 27.03 | 24.93 | 22.79 | 19.82 | 16.54 | 12.98 | 9.13 | 4.74 | -16.16 | -23.4 | -24.41
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | WPD Best View | Thermal headroom (MW) | 36.52 | 34.8 | 32.37 | 26.79 | 23.61 | 18.93 | 14.12 | 7.88 | 0.6 | -7.01 | -14.1 | -21.98 | -30.14 | -38.1 | -45.44 | -66.77 | -76.9 | -81.44
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Consumer Transformation | Thermal headroom (MW) | 5.09 | 5.14 | 5.08 | 4.94 | 4.78 | 3.21 | 1.7 | 0.51 | -0.67 | -2.23 | -14.36 | -26.47 | -38.56 | -50.64 | -64.18 | -99.34 | -209.39 | -302.7
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Leading the Way | Thermal headroom (MW) | 5.09 | 5.09 | 4.85 | 4.51 | 3 | -0.18 | -3.36 | -7.46 | -20.57 | -34.75 | -37.34 | -44.04 | -54.41 | -65.78 | -76.79 | -115.92 | -169.01 | -226.13
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Steady Progression | Thermal headroom (MW) | 5.09 | 5.14 | 5.12 | 5.09 | 5.06 | 4.45 | 3.96 | 3.58 | 3.2 | 2.66 | 1.97 | 1.51 | 1.05 | 0.51 | 0.03 | -3.29 | -4.37 | -4.46
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | System Transformation | Thermal headroom (MW) | 5.09 | 5.1 | 5.07 | 5.01 | 4.92 | 4.27 | 3.68 | 3.42 | 3.14 | 2.86 | 2.14 | 1.73 | 1.03 | 0.52 | -0.15 | -3.59 | -6.25 | -7.11
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | WPD Best View | Thermal headroom (MW) | 5.09 | 5.12 | 5.09 | 5.05 | 4.99 | 4.26 | 3.6 | 3.2 | 2.8 | 2.34 | 1.6 | 1.15 | 0.58 | 0.05 | -0.54 | -4.01 | -5.61 | -6.08
Cellarhead 132kV | Forsbrook 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Consumer Transformation | Thermal headroom (MW) | 16.11 | 15.86 | 15.52 | 15.12 | 14.51 | 13.74 | 13 | 12.25 | 11.47 | 10.6 | 9.15 | 7.65 | 6.14 | 4.69 | 3.33 | -4.82 | -9.01 | -10.82
Cellarhead 132kV | Forsbrook 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Leading the Way | Thermal headroom (MW) | 16.11 | 15.57 | 14.91 | 14.21 | 13.26 | 11.98 | 10.78 | 9.5 | 8.23 | 6.77 | 5.3 | 3.74 | 2.21 | 0.73 | -0.62 | -5.37 | -6.99 | -7.35
Cellarhead 132kV | Forsbrook 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Steady Progression | Thermal headroom (MW) | 16.11 | 16.06 | 15.91 | 15.74 | 15.53 | 15.16 | 14.84 | 14.46 | 14.01 | 13.57 | 12.97 | 12.37 | 11.72 | 11.05 | 10.35 | 5.63 | 3.02 | 2.15
Cellarhead 132kV | Forsbrook 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | System Transformation | Thermal headroom (MW) | 16.11 | 16.02 | 15.82 | 15.6 | 15.29 | 14.96 | 14.62 | 14.27 | 13.87 | 13.43 | 12.79 | 12.05 | 11.29 | 10.48 | 9.63 | 4.78 | 2.38 | 1.71
Cellarhead 132kV | Forsbrook 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | WPD Best View | Thermal headroom (MW) | 16.11 | 16.04 | 15.85 | 15.66 | 15.42 | 15 | 14.63 | 14.21 | 13.72 | 13.24 | 12.6 | 11.96 | 11.27 | 10.55 | 9.8 | 4.92 | 2.2 | 1.27
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Consumer Transformation | Thermal headroom (MW) | -7.33 | -7.05 | -6.91 | -6.77 | -6.63 | -6.49 | -6.36 | -6.22 | -6.09 | -5.96 | -5.83 | -5.7 | -5.58 | -5.45 | -5.33 | -4.74 | -4.19 | -3.66
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Leading the Way | Thermal headroom (MW) | -7.33 | -7.05 | -6.91 | -6.77 | -6.63 | -6.5 | -6.36 | -6.23 | -6.1 | -5.97 | -5.84 | -5.72 | -5.59 | -5.46 | -5.34 | -4.75 | -4.19 | -3.66
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Steady Progression | Thermal headroom (MW) | -7.33 | -7.05 | -6.91 | -6.77 | -6.63 | -6.49 | -6.36 | -6.22 | -6.09 | -5.96 | -5.83 | -5.7 | -5.58 | -5.45 | -5.33 | -4.74 | -4.18 | -3.65
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | System Transformation | Thermal headroom (MW) | -7.33 | -7.05 | -6.91 | -6.77 | -6.63 | -6.49 | -6.36 | -6.22 | -6.09 | -5.96 | -5.83 | -5.7 | -5.58 | -5.45 | -5.33 | -4.74 | -4.18 | -3.65
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | WPD Best View | Thermal headroom (MW) | -7.33 | -7.05 | -6.91 | -6.77 | -6.63 | -6.49 | -6.36 | -6.22 | -6.09 | -5.96 | -5.83 | -5.7 | -5.58 | -5.45 | -5.33 | -4.74 | -4.18 | -3.65
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Consumer Transformation | Thermal headroom (MW) | 4.34 | 4.34 | 4.25 | 4.07 | 3.62 | 3.26 | 2.92 | 2.56 | 2.18 | 1.79 | 1.1 | 0.47 | -0.38 | -1.22 | -2.02 | -7.06 | -9.72 | -10.83
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Leading the Way | Thermal headroom (MW) | 4.34 | 4.25 | 4.06 | 3.78 | 3.08 | 2.39 | 1.75 | 1.09 | 0.39 | -0.47 | -1.28 | -2.14 | -2.98 | -3.76 | -4.52 | -7.36 | -8.4 | -8.72
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Steady Progression | Thermal headroom (MW) | 4.34 | 4.44 | 4.44 | 4.43 | 4.21 | 4.04 | 3.87 | 3.68 | 3.48 | 3.25 | 2.96 | 2.65 | 2.33 | 2.01 | 1.69 | -0.55 | -1.97 | -2.49
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | System Transformation | Thermal headroom (MW) | 4.34 | 4.4 | 4.38 | 4.32 | 4 | 3.86 | 3.69 | 3.48 | 3.25 | 3 | 2.65 | 2.29 | 1.95 | 1.62 | 1.33 | -0.76 | -2.26 | -2.72
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | WPD Best View | Thermal headroom (MW) | 4.34 | 4.44 | 4.44 | 4.43 | 4.21 | 4.04 | 3.87 | 3.68 | 3.48 | 3.25 | 2.96 | 2.65 | 2.33 | 2.01 | 1.69 | -0.55 | -1.97 | -2.49
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Consumer Transformation | Thermal headroom (MW) | 4.47 | 4.04 | 3.41 | 2.74 | 1.9 | 1.01 | 0.16 | -0.72 | -1.64 | -2.58 | -4.29 | -6.07 | -7.9 | -9.5 | -11.06 | -20.28 | -25.09 | -27.22
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Leading the Way | Thermal headroom (MW) | 4.47 | 3.87 | 3 | 1.98 | 0.75 | -0.72 | -2.02 | -3.49 | -5.12 | -6.85 | -8.72 | -10.72 | -12.71 | -14.4 | -15.93 | -21.61 | -23.68 | -24.49
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Steady Progression | Thermal headroom (MW) | 4.47 | 4.32 | 3.99 | 3.67 | 3.3 | 2.84 | 2.41 | 1.96 | 1.45 | 0.9 | 0.16 | -0.58 | -1.44 | -2.21 | -2.99 | -8.16 | -10.77 | -11.53
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | System Transformation | Thermal headroom (MW) | 4.47 | 4.22 | 3.77 | 3.33 | 2.78 | 2.32 | 1.88 | 1.4 | 0.75 | 0.04 | -0.85 | -1.78 | -2.72 | -3.54 | -4.33 | -9.9 | -12.21 | -12.65
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | WPD Best View | Thermal headroom (MW) | 4.47 | 4.22 | 3.78 | 3.34 | 2.83 | 2.18 | 1.51 | 0.8 | 0.08 | -0.66 | -1.61 | -2.75 | -3.97 | -5.03 | -6.07 | -11.81 | -14.37 | -15.15
Cellarhead 132kV | Forsbrook 132 33 | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Consumer Transformation | Thermal headroom (MW) | -51.76 | -52.55 | -53.66 | -54.78 | -56.78 | -60.26 | -64.35 | -69.51 | -75.61 | -82.11 | -93.64 | -105.17 | -116.76 | -127.5 | -138.13 | -181.19 | -217.12 | -238.04
Cellarhead 132kV | Forsbrook 132 33 | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Leading the Way | Thermal headroom (MW) | -51.76 | -53.2 | -55.73 | -57.78 | -61.29 | -66.91 | -74.32 | -82.69 | -92.01 | -101.7 | -111.97 | -122.79 | -133.65 | -143.2 | -151.88 | -176.12 | -184.94 | -187.11
Cellarhead 132kV | Forsbrook 132 33 | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Steady Progression | Thermal headroom (MW) | -51.76 | -51.23 | -51.36 | -51.3 | -51.53 | -52.71 | -53.98 | -55.33 | -56.78 | -59.05 | -62.22 | -64.62 | -67.55 | -71.5 | -75.4 | -99.26 | -115.84 | -122.05
Cellarhead 132kV | Forsbrook 132 33 | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | System Transformation | Thermal headroom (MW) | -51.76 | -51.62 | -52.16 | -52.5 | -53.34 | -54.75 | -56.44 | -58.27 | -60.34 | -62.69 | -66.26 | -70.01 | -74.48 | -79.36 | -84.72 | -110.48 | -119.66 | -121.61
Cellarhead 132kV | Forsbrook 132 33 | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | WPD Best View | Thermal headroom (MW) | -51.76 | -53.09 | -55.49 | -57.38 | -60.56 | -65.92 | -72.95 | -80.98 | -89.99 | -99.37 | -109.37 | -119.87 | -130.4 | -139.72 | -148.15 | -172.14 | -181.08 | -183.02
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Consumer Transformation | Thermal headroom (MW) | 30.42 | 29.82 | 28.98 | 27.9 | 26.14 | 23.29 | 19.91 | 16.64 | 13.22 | 8.41 | -1.06 | -10.53 | -20.1 | -29.38 | -38.68 | -77.94 | -114.8 | -136.37
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Leading the Way | Thermal headroom (MW) | 30.42 | 29.28 | 27.12 | 25.1 | 21.55 | 16.78 | 11.61 | 5.43 | -1.5 | -9.15 | -17 | -25.41 | -34.05 | -42.37 | -50.08 | -75.34 | -86.84 | -91.54
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Steady Progression | Thermal headroom (MW) | 30.42 | 31.04 | 31.05 | 31.02 | 30.83 | 29.95 | 29.03 | 28.08 | 27 | 24.79 | 21.83 | 19.83 | 17.33 | 14.49 | 11.92 | -7.18 | -21.1 | -27.31
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | System Transformation | Thermal headroom (MW) | 30.42 | 30.74 | 30.43 | 30.01 | 29.31 | 28.46 | 27.48 | 26.29 | 24.75 | 22.95 | 20.04 | 16.98 | 13.86 | 10.87 | 7.78 | -13.11 | -22.39 | -25.84
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | WPD Best View | Thermal headroom (MW) | 30.42 | 29.34 | 27.24 | 25.38 | 21.92 | 17.32 | 12.49 | 6.53 | -0.25 | -7.71 | -15.43 | -23.69 | -32.17 | -40.34 | -47.9 | -73.32 | -84.97 | -89.75
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Consumer Transformation | Thermal headroom (MW) | 3.05 | 3.12 | 3.14 | 3.14 | 3.13 | 2.85 | 2.58 | 2.33 | 2.09 | 1.81 | 0.38 | -1.09 | -2.53 | -3.99 | -5.61 | -9.34 | -18.85 | -26.79
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Leading the Way | Thermal headroom (MW) | 3.05 | 3.1 | 3.03 | 2.93 | 2.32 | 1.35 | 0.34 | -1.14 | -5.64 | -10.47 | -11.32 | -13.56 | -17.05 | -20.9 | -24.59 | -38.68 | -57.47 | -77.68
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Steady Progression | Thermal headroom (MW) | 3.05 | 3.08 | 3.06 | 3.04 | 2.98 | 2.78 | 2.59 | 2.39 | 2.19 | -0.4 | -3.59 | -3.78 | -4.09 | -5.11 | -5.32 | -6.75 | -7 | -7.07
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | System Transformation | Thermal headroom (MW) | 3.05 | 2.98 | 2.9 | 2.78 | 2.62 | 2.42 | 2.19 | 1.89 | 1.51 | 1.32 | -0.1 | -0.22 | -1.37 | -1.72 | -2.83 | -6.91 | -12.86 | -16.62
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | WPD Best View | Thermal headroom (MW) | 3.05 | 2.97 | 2.89 | 2.77 | 2.6 | 2.38 | 2.11 | 1.78 | 1.37 | 1.15 | -0.3 | -0.45 | -1.62 | -1.99 | -3.11 | -7.22 | -13.03 | -16.77
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Consumer Transformation | Thermal headroom (MW) | 9.73 | 9.79 | 9.81 | 9.79 | 9.72 | 9.59 | 9.45 | 9.33 | 9.19 | 9.03 | 8.82 | 8.37 | 7.93 | 7.49 | 7.06 | 4.87 | 4.07 | 3.77
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Leading the Way | Thermal headroom (MW) | 9.73 | 9.77 | 9.75 | 9.71 | 9.59 | 9.39 | 9.18 | 8.9 | 8.62 | 8.21 | 7.84 | 7.48 | 7.07 | 6.68 | 6.34 | 5.07 | 4.75 | 4.83
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Steady Progression | Thermal headroom (MW) | 9.73 | 9.83 | 9.87 | 9.91 | 9.92 | 9.86 | 9.8 | 9.72 | 9.63 | 9.54 | 9.39 | 9.25 | 9.09 | 8.92 | 8.73 | 6.59 | 5.49 | 5.22
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | System Transformation | Thermal headroom (MW) | 9.73 | 9.82 | 9.85 | 9.87 | 9.85 | 9.84 | 9.81 | 9.77 | 9.71 | 9.64 | 9.52 | 9.39 | 9.25 | 9.12 | 9 | 6.99 | 5.66 | 5.46
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | WPD Best View | Thermal headroom (MW) | 9.73 | 9.83 | 9.87 | 9.91 | 9.92 | 9.86 | 9.8 | 9.72 | 9.63 | 9.54 | 9.39 | 9.25 | 9.09 | 8.92 | 8.73 | 6.59 | 5.49 | 5.22
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Consumer Transformation | Thermal headroom (MW) | 0.31 | 0.31 | 0.27 | 0.21 | 0.09 | -0.14 | -0.39 | -0.56 | -0.74 | -0.93 | -1.3 | -1.79 | -2.28 | -2.76 | -3.23 | -5.68 | -6.9 | -7.43
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Leading the Way | Thermal headroom (MW) | 0.31 | 0.26 | 0.18 | 0.08 | -0.11 | -0.46 | -0.91 | -1.25 | -1.64 | -2.11 | -2.57 | -3.03 | -3.48 | -3.92 | -4.3 | -5.79 | -6.28 | -6.39
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Steady Progression | Thermal headroom (MW) | 0.31 | 0.37 | 0.4 | 0.42 | 0.41 | 0.29 | 0.16 | 0.06 | -0.07 | -0.2 | -0.38 | -0.55 | -0.74 | -0.92 | -1.12 | -2.72 | -3.52 | -3.8
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | System Transformation | Thermal headroom (MW) | 0.31 | 0.35 | 0.36 | 0.36 | 0.31 | 0.2 | 0.05 | -0.05 | -0.16 | -0.29 | -0.47 | -0.65 | -0.84 | -1.02 | -1.19 | -2.83 | -3.62 | -3.78
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | WPD Best View | Thermal headroom (MW) | 0.31 | 0.37 | 0.4 | 0.42 | 0.41 | 0.29 | 0.16 | 0.06 | -0.07 | -0.2 | -0.38 | -0.55 | -0.74 | -0.92 | -1.12 | -2.72 | -3.52 | -3.8
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Consumer Transformation | Thermal headroom (MW) | 0.85 | 0.86 | 0.8 | 0.72 | 0.57 | 0.33 | 0.09 | -0.15 | -0.4 | -0.67 | -1.4 | -2.23 | -3.18 | -4.11 | -5.04 | -8.92 | -10.95 | -11.7
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Leading the Way | Thermal headroom (MW) | 0.85 | 0.82 | 0.7 | 0.56 | 0.36 | -0.06 | -0.54 | -1.03 | -1.49 | -2.03 | -2.92 | -3.83 | -4.74 | -5.63 | -6.15 | -8.58 | -9.69 | -9.96
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Steady Progression | Thermal headroom (MW) | 0.85 | 0.93 | 0.95 | 0.96 | 0.94 | 0.81 | 0.68 | 0.53 | 0.37 | 0.18 | -0.08 | -0.33 | -0.61 | -0.9 | -1.19 | -3.82 | -5.27 | -5.99
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | System Transformation | Thermal headroom (MW) | 0.85 | 0.92 | 0.91 | 0.89 | 0.85 | 0.78 | 0.7 | 0.58 | 0.44 | 0.28 | 0.04 | -0.21 | -0.83 | -1.44 | -2.01 | -4.59 | -6.49 | -6.88
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | WPD Best View | Thermal headroom (MW) | 0.85 | 0.93 | 0.95 | 0.96 | 0.94 | 0.81 | 0.68 | 0.53 | 0.36 | 0.17 | -0.09 | -0.34 | -0.62 | -0.9 | -1.18 | -3.8 | -5.26 | -5.97
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Consumer Transformation | Thermal headroom (MW) | 2.8 | 2.83 | 2.84 | 2.84 | 2.82 | 2.65 | 2.48 | 2.32 | 2.13 | 1.91 | 1.62 | 1.29 | 0.97 | 0.64 | 0.32 | -0.95 | -1.32 | -1.51
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Leading the Way | Thermal headroom (MW) | 2.8 | 2.82 | 2.82 | 2.81 | 2.77 | 2.44 | 2.12 | 1.76 | 1.3 | 0.8 | 0.61 | 0.38 | 0.05 | -0.29 | -0.61 | -1.82 | -2.58 | -3.27
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Steady Progression | Thermal headroom (MW) | 2.8 | 2.8 | 2.79 | 2.76 | 2.74 | 2.59 | 2.44 | 2.3 | 2.15 | 1.93 | 1.62 | 1.45 | 1.26 | 1.05 | 0.82 | -0.98 | -1.69 | -1.84
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | System Transformation | Thermal headroom (MW) | 2.8 | 2.79 | 2.76 | 2.73 | 2.68 | 2.63 | 2.59 | 2.53 | 2.46 | 2.41 | 2.09 | 1.91 | 1.6 | 1.4 | 1.08 | -0.76 | -2.54 | -3.16
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | WPD Best View | Thermal headroom (MW) | 2.8 | 2.8 | 2.79 | 2.76 | 2.74 | 2.59 | 2.44 | 2.3 | 2.15 | 1.93 | 1.62 | 1.45 | 1.26 | 1.05 | 0.82 | -0.98 | -1.69 | -1.84
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Consumer Transformation | Thermal headroom (MW) | 0.21 | 0.19 | 0.11 | 0.02 | -0.05 | -0.16 | -0.26 | -0.37 | -0.48 | -0.61 | -0.84 | -1.07 | -1.29 | -1.51 | -1.72 | -2.84 | -3.36 | -3.62
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Leading the Way | Thermal headroom (MW) | 0.21 | 0.16 | 0.03 | -0.08 | -0.16 | -0.36 | -0.55 | -0.78 | -1.01 | -1.25 | -1.4 | -1.61 | -1.81 | -2 | -2.19 | -2.93 | -3.23 | -3.32
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Steady Progression | Thermal headroom (MW) | 0.21 | 0.21 | 0.18 | 0.16 | 0.14 | 0.07 | 0.01 | -0.06 | -0.13 | -0.19 | -0.28 | -0.36 | -0.46 | -0.56 | -0.65 | -1.39 | -1.67 | -1.8
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | System Transformation | Thermal headroom (MW) | 0.21 | 0.21 | 0.16 | 0.12 | 0.1 | 0.07 | 0.04 | 0 | -0.07 | -0.14 | -0.22 | -0.31 | -0.39 | -0.48 | -0.57 | -1.32 | -1.78 | -1.94
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | WPD Best View | Thermal headroom (MW) | 0.21 | 0.21 | 0.18 | 0.16 | 0.14 | 0.07 | 0.01 | -0.06 | -0.13 | -0.19 | -0.28 | -0.36 | -0.46 | -0.56 | -0.65 | -1.39 | -1.67 | -1.8
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Consumer Transformation | Thermal headroom (MW) | 2.53 | 2.57 | 2.59 | 2.54 | 2.45 | 2.26 | 2.1 | 1.94 | 1.8 | 1.65 | 1.41 | 1.14 | 0.76 | 0.38 | 0.01 | -1.24 | -1.71 | -1.88
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Leading the Way | Thermal headroom (MW) | 2.53 | 2.56 | 2.56 | 2.52 | 2.38 | 2.09 | 1.84 | 1.5 | 1.05 | 0.58 | 0.4 | 0.11 | -0.26 | -0.59 | -0.91 | -2.35 | -3.16 | -3.76
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Steady Progression | Thermal headroom (MW) | 2.53 | 2.58 | 2.6 | 2.6 | 2.58 | 2.47 | 2.35 | 2.24 | 2.1 | 1.86 | 1.56 | 1.34 | 1.12 | 0.87 | 0.62 | -1.25 | -1.72 | -1.95
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | System Transformation | Thermal headroom (MW) | 2.53 | 2.55 | 2.55 | 2.51 | 2.44 | 2.38 | 2.33 | 2.26 | 2.17 | 2.08 | 1.8 | 1.67 | 1.41 | 1.25 | 1.02 | -0.51 | -2.21 | -2.88
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | WPD Best View | Thermal headroom (MW) | 2.53 | 2.55 | 2.55 | 2.51 | 2.44 | 2.38 | 2.33 | 2.26 | 2.17 | 2.08 | 1.79 | 1.66 | 1.4 | 1.24 | 1 | -0.54 | -2.22 | -2.88
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Consumer Transformation | Thermal headroom (MW) | 4.18 | 4.14 | 4.09 | 4 | 3.86 | 3.54 | 3.25 | 2.97 | 2.65 | 2.28 | 1.72 | 1.17 | 0.66 | 0.18 | -0.28 | -3.12 | -4.3 | -4.85
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Leading the Way | Thermal headroom (MW) | 4.18 | 4.09 | 3.93 | 3.76 | 3.58 | 3.07 | 2.57 | 2.07 | 1.58 | 0.97 | 0.5 | -0.02 | -0.48 | -0.89 | -1.25 | -3.4 | -4 | -4.21
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Steady Progression | Thermal headroom (MW) | 4.18 | 4.18 | 4.14 | 4.09 | 4.04 | 3.86 | 3.7 | 3.54 | 3.37 | 3.2 | 2.9 | 2.61 | 2.31 | 1.97 | 1.64 | -0.74 | -1.79 | -2.42
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | System Transformation | Thermal headroom (MW) | 4.18 | 4.18 | 4.13 | 4.07 | 4 | 3.94 | 3.89 | 3.84 | 3.74 | 3.6 | 3.37 | 3.09 | 2.84 | 2.6 | 2.3 | -0.29 | -1.86 | -2.26
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | WPD Best View | Thermal headroom (MW) | 4.18 | 4.18 | 4.14 | 4.09 | 4.04 | 3.86 | 3.7 | 3.54 | 3.37 | 3.2 | 2.9 | 2.61 | 2.31 | 1.97 | 1.64 | -0.73 | -1.79 | -2.43
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Consumer Transformation | Thermal headroom (MW) | 14.22 | 14.3 | 14.18 | 13.96 | 13.26 | 12.5 | 11.78 | 11.03 | 10.3 | 9.4 | 7.08 | 4.39 | 1.93 | -0.42 | -2.71 | -12.72 | -17.77 | -19.55
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Leading the Way | Thermal headroom (MW) | 14.22 | 14.11 | 13.79 | 13.41 | 12.39 | 11.29 | 10.12 | 8.75 | 7.12 | 4.8 | 2.06 | -0.8 | -3.21 | -5.52 | -7.64 | -14.47 | -16.37 | -16.34
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Steady Progression | Thermal headroom (MW) | 14.22 | 14.52 | 14.6 | 14.68 | 14.48 | 14.19 | 13.9 | 13.55 | 13.17 | 12.65 | 11.96 | 11.23 | 10.56 | 9.87 | 8.81 | 1.14 | -2.95 | -4.57
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | System Transformation | Thermal headroom (MW) | 14.22 | 14.43 | 14.41 | 14.38 | 13.99 | 13.73 | 13.43 | 13.05 | 12.63 | 12.01 | 11.16 | 9.89 | 8.8 | 7.71 | 6.21 | -2.09 | -5.81 | -6.53
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | WPD Best View | Thermal headroom (MW) | 14.22 | 14.43 | 14.41 | 14.38 | 13.99 | 13.72 | 13.42 | 13.02 | 12.6 | 11.96 | 11.11 | 9.84 | 8.75 | 7.65 | 6.08 | -2.25 | -5.9 | -6.6
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Consumer Transformation | Thermal headroom (MW) | 24.28 | 23.85 | 22.94 | 21.98 | 20.77 | 18.99 | 17.18 | 15.29 | 13.54 | 11.48 | 3.15 | -6.14 | -15.45 | -24.32 | -33.92 | -60.28 | -108.1 | -145.48
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Leading the Way | Thermal headroom (MW) | 24.28 | 23.96 | 22.27 | 20.9 | 18.66 | 16.14 | 13.5 | 10.31 | 4.46 | -1.98 | -5.48 | -10.57 | -16.74 | -22.68 | -28.38 | -41.55 | -50.85 | -58.16
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Steady Progression | Thermal headroom (MW) | 24.28 | 24.57 | 24.11 | 23.71 | 23.18 | 22.67 | 22.16 | 21.57 | 20.99 | 17.45 | 13.13 | 11.98 | 10.67 | 8.5 | 7.31 | -0.74 | -6.96 | -9.56
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | System Transformation | Thermal headroom (MW) | 24.28 | 24.19 | 23.35 | 22.5 | 21.42 | 20.7 | 19.91 | 18.82 | 17.54 | 16.21 | 13.15 | 11.92 | 9.18 | 7.27 | 4.44 | -8.49 | -17.97 | -22.58
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | WPD Best View | Thermal headroom (MW) | 24.28 | 24.55 | 24 | 23.48 | 22.39 | 21.54 | 20.65 | 19.37 | 16.34 | 11.99 | 9.62 | 7.22 | 4 | 0.28 | -3.04 | -13.46 | -22.67 | -28.47
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Consumer Transformation | Thermal headroom (MW) | 16.62 | 16.54 | 16.48 | 16.36 | 16.09 | 15.74 | 15.41 | 15.05 | 14.69 | 14.29 | 13.83 | 13.12 | 12.3 | 11.53 | 10.78 | 6.81 | 5.04 | 4.19
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Leading the Way | Thermal headroom (MW) | 16.62 | 16.47 | 16.38 | 16.2 | 15.84 | 15.38 | 14.87 | 14.27 | 13.67 | 12.84 | 12.08 | 11.22 | 10.35 | 9.67 | 9.06 | 6.7 | 5.83 | 5.66
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Steady Progression | Thermal headroom (MW) | 16.62 | 16.62 | 16.65 | 16.65 | 16.59 | 16.45 | 16.3 | 16.14 | 15.96 | 15.76 | 15.49 | 15.21 | 14.9 | 14.59 | 14.29 | 11.7 | 10.1 | 9.62
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | System Transformation | Thermal headroom (MW) | 16.62 | 16.59 | 16.59 | 16.55 | 16.42 | 16.31 | 16.17 | 16 | 15.81 | 15.58 | 15.28 | 14.94 | 14.58 | 14.28 | 14.02 | 11.41 | 9.73 | 9.38
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | WPD Best View | Thermal headroom (MW) | 16.62 | 16.61 | 16.63 | 16.62 | 16.55 | 16.44 | 16.32 | 16.18 | 16.02 | 15.84 | 15.57 | 15.3 | 15.01 | 14.71 | 14.42 | 12.1 | 10.24 | 9.73
Cellarhead 132kV | Newcastle 132 11 (GT3A) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Consumer Transformation | Thermal headroom (MW) | 58.94 | 58.04 | 56.83 | 55.24 | 52.82 | 49.19 | 45.23 | 40.94 | 36.66 | 31.09 | 22.31 | 13.66 | 5.2 | -2.97 | -10.94 | -45.7 | -71.01 | -84.4
Cellarhead 132kV | Newcastle 132 11 (GT3A) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Leading the Way | Thermal headroom (MW) | 58.94 | 57.04 | 54.35 | 51.39 | 47.45 | 42.08 | 36.18 | 29.32 | 21.79 | 13.11 | 4.54 | -4.26 | -12.96 | -21.26 | -28.82 | -51.26 | -60.33 | -64.01
Cellarhead 132kV | Newcastle 132 11 (GT3A) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Steady Progression | Thermal headroom (MW) | 58.94 | 59.56 | 59.55 | 59.48 | 59.09 | 57.86 | 56.44 | 54.79 | 53.16 | 51.14 | 48.59 | 46.13 | 43.49 | 40.63 | 37.31 | 17.03 | 3.92 | -0.34
Cellarhead 132kV | Newcastle 132 11 (GT3A) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | System Transformation | Thermal headroom (MW) | 58.94 | 59.2 | 58.81 | 58.28 | 57.27 | 55.94 | 54.1 | 51.89 | 49.81 | 47.15 | 43.69 | 40.05 | 36.21 | 32.07 | 27.77 | 6.21 | -0.56 | -1.66
Cellarhead 132kV | Newcastle 132 11 (GT3A) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | WPD Best View | Thermal headroom (MW) | 58.94 | 59.38 | 59.12 | 58.81 | 58.19 | 56.53 | 54.82 | 52.62 | 50.6 | 47.96 | 44.98 | 42.01 | 38.89 | 35.68 | 32.1 | 12.25 | 0.24 | -3.31
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Consumer Transformation | Thermal headroom (MW) | 10.29 | 10.2228 | 9.8795 | 9.4349 | 8.7514 | 7.7055 | 6.6991 | 5.7339 | 4.7165 | 3.6153 | 1.2076 | -1.4236 | -4.2365 | -6.935 | -9.5732 | -24.1778 | -34.477 | -40.3133
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Leading the Way | Thermal headroom (MW) | 10.29 | 9.9993 | 9.3701 | 8.681 | 7.5819 | 5.6294 | 3.8553 | 1.7915 | -0.66995 | -3.2999 | -5.9237 | -8.8165 | -11.7318 | -14.5243 | -17.1182 | -26.2668 | -30.4419 | -32.8469
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Steady Progression | Thermal headroom (MW) | 10.29 | 10.5305 | 10.5316 | 10.5144 | 10.3799 | 9.9536 | 9.5881 | 9.199 | 8.7299 | 8.1746 | 7.3917 | 6.5767 | 5.6996 | 4.7922 | 3.8712 | -2.7508 | -7.2826 | -8.9938
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | System Transformation | Thermal headroom (MW) | 10.29 | 10.4424 | 10.3375 | 10.1828 | 9.875 | 9.3769 | 8.9403 | 8.4183 | 7.7658 | 7.0379 | 6.0497 | 4.9973 | 3.922 | 2.8839 | 1.9385 | -5.6834 | -9.2313 | -10.1134
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | WPD Best View | Thermal headroom (MW) | 10.29 | 10.5305 | 10.5316 | 10.5144 | 10.3799 | 9.9536 | 9.5881 | 9.199 | 8.7299 | 8.1746 | 7.3917 | 6.5767 | 5.6996 | 4.7922 | 3.8712 | -2.7508 | -7.2826 | -8.9938
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Consumer Transformation | Thermal headroom (MW) | 1.64 | 1.6 | 1.41 | 1.12 | 0.77 | 0.24 | -0.29 | -0.83 | -1.33 | -1.84 | -2.84 | -4.13 | -5.59 | -7.01 | -8.4 | -15.51 | -22.14 | -26.53
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Leading the Way | Thermal headroom (MW) | 1.64 | 1.51 | 1.18 | 0.78 | 0.25 | -0.64 | -1.52 | -2.5 | -3.79 | -5.16 | -6.36 | -7.73 | -9.2 | -10.6 | -11.91 | -16.82 | -19.62 | -21.81
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Steady Progression | Thermal headroom (MW) | 1.64 | 1.73 | 1.72 | 1.68 | 1.61 | 1.39 | 1.17 | 0.94 | 0.69 | 0.42 | 0.04 | -0.35 | -0.78 | -1.23 | -1.67 | -4.31 | -6.35 | -7.37
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | System Transformation | Thermal headroom (MW) | 1.64 | 1.69 | 1.63 | 1.5 | 1.34 | 1.1 | 0.84 | 0.55 | 0.23 | -0.12 | -0.58 | -1.06 | -1.56 | -2.03 | -2.46 | -5.59 | -7.32 | -7.78
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | WPD Best View | Thermal headroom (MW) | 1.64 | 1.73 | 1.72 | 1.68 | 1.61 | 1.39 | 1.17 | 0.94 | 0.69 | 0.42 | 0.04 | -0.35 | -0.78 | -1.23 | -1.67 | -4.31 | -6.35 | -7.37
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Consumer Transformation | Thermal headroom (MW) | 12.28 | 12.24 | 12.07 | 11.86 | 11.48 | 10.89 | 10.34 | 9.83 | 9.24 | 8.58 | 7.02 | 5.5 | 3.92 | 2.44 | 0.99 | -7.54 | -12.2 | -14.3
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Leading the Way | Thermal headroom (MW) | 12.28 | 12.1 | 11.75 | 11.41 | 10.75 | 9.57 | 8.55 | 7.32 | 5.95 | 4.5 | 2.9 | 1.18 | -0.48 | -2.08 | -3.56 | -8.52 | -10.31 | -10.86
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Steady Progression | Thermal headroom (MW) | 12.28 | 12.44 | 12.45 | 12.47 | 12.4 | 12.15 | 11.97 | 11.78 | 11.53 | 11.2 | 10.74 | 10.27 | 9.76 | 9.23 | 8.69 | 4.33 | 1.54 | 0.7
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | System Transformation | Thermal headroom (MW) | 12.28 | 12.39 | 12.34 | 12.29 | 12.12 | 11.83 | 11.61 | 11.34 | 10.96 | 10.53 | 9.93 | 9.3 | 8.65 | 8.01 | 7.43 | 2.49 | 0.42 | -0.07
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | WPD Best View | Thermal headroom (MW) | 12.28 | 12.44 | 12.45 | 12.47 | 12.4 | 12.15 | 11.97 | 11.78 | 11.53 | 11.2 | 10.74 | 10.27 | 9.76 | 9.23 | 8.69 | 4.33 | 1.54 | 0.7
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Consumer Transformation | Thermal headroom (MW) | 2.57 | 2.51 | 2.37 | 2.21 | 1.98 | 1.76 | 1.5 | 1.23 | 0.96 | 0.65 | 0.23 | -0.41 | -1.11 | -1.76 | -2.39 | -6.49 | -8.41 | -9.18
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Leading the Way | Thermal headroom (MW) | 2.57 | 2.44 | 2.22 | 1.99 | 1.66 | 1.24 | 0.77 | 0.27 | -0.37 | -1.05 | -1.74 | -2.49 | -3.23 | -3.89 | -4.52 | -7.25 | -7.99 | -8.13
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Steady Progression | Thermal headroom (MW) | 2.57 | 2.62 | 2.58 | 2.53 | 2.46 | 2.35 | 2.25 | 2.14 | 2.01 | 1.85 | 1.61 | 1.34 | 1.05 | 0.79 | 0.52 | -1.62 | -2.91 | -3.53
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | System Transformation | Thermal headroom (MW) | 2.57 | 2.59 | 2.51 | 2.42 | 2.29 | 2.2 | 2.11 | 1.98 | 1.8 | 1.57 | 1.3 | 1 | 0.68 | 0.42 | 0.17 | -2.45 | -3.66 | -3.85
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | WPD Best View | Thermal headroom (MW) | 2.57 | 2.62 | 2.58 | 2.53 | 2.46 | 2.35 | 2.25 | 2.14 | 2.01 | 1.85 | 1.61 | 1.34 | 1.05 | 0.79 | 0.52 | -1.62 | -2.91 | -3.53
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Consumer Transformation | Thermal headroom (MW) | 16.55 | 16.14 | 15.53 | 14.8 | 13.76 | 12.78 | 11.77 | 10.46 | 8.82 | 6.48 | 2.49 | -1.6 | -5.74 | -9.67 | -13.43 | -32.03 | -42.19 | -46.43
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Leading the Way | Thermal headroom (MW) | 16.55 | 15.8 | 14.86 | 13.83 | 12.36 | 10.57 | 8.48 | 5.35 | 2.04 | -1.32 | -5.44 | -9.79 | -14.14 | -18.32 | -21.75 | -33 | -36.74 | -36.72
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Steady Progression | Thermal headroom (MW) | 16.55 | 16.69 | 16.63 | 16.53 | 16.36 | 16.06 | 15.71 | 15.17 | 14.51 | 13.78 | 12.84 | 11.86 | 10.81 | 9.32 | 7.61 | -4.06 | -12.04 | -15.01
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | System Transformation | Thermal headroom (MW) | 16.55 | 16.52 | 16.29 | 16 | 15.54 | 15.21 | 14.83 | 14.06 | 13.07 | 12.19 | 11.09 | 9.91 | 7.62 | 5.04 | 2.37 | -10.38 | -15.21 | -15.84
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | WPD Best View | Thermal headroom (MW) | 16.55 | 16.69 | 16.63 | 16.53 | 16.36 | 16.06 | 15.71 | 15.17 | 14.51 | 13.78 | 12.84 | 11.86 | 10.81 | 9.32 | 7.61 | -4.06 | -12.04 | -15.01
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Consumer Transformation | Thermal headroom (MW) | 14.11 | 14.06 | 13.9 | 13.66 | 13.24 | 12.73 | 12.16 | 11.5 | 10.81 | 10.15 | 9.22 | 8.04 | 6.66 | 5.32 | 4.02 | -4 | -8.65 | -10.95
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Leading the Way | Thermal headroom (MW) | 14.11 | 13.96 | 13.65 | 13.25 | 12.64 | 11.64 | 10.64 | 9.49 | 8.35 | 7.04 | 5.65 | 4.2 | 2.72 | 1.31 | 0 | -5.08 | -7.27 | -8.29
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Steady Progression | Thermal headroom (MW) | 14.11 | 14.25 | 14.28 | 14.27 | 14.23 | 14.04 | 13.81 | 13.49 | 13.13 | 12.74 | 12.2 | 11.64 | 11.03 | 10.4 | 9.77 | 6.49 | 4.45 | 3.47
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | System Transformation | Thermal headroom (MW) | 14.11 | 14.21 | 14.17 | 14.1 | 13.97 | 13.79 | 13.52 | 13.15 | 12.72 | 12.26 | 11.58 | 10.89 | 10.19 | 9.51 | 8.78 | 5.54 | 3.46 | 2.69
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | WPD Best View | Thermal headroom (MW) | 14.11 | 14.08 | 13.91 | 13.71 | 13.4 | 12.76 | 12.08 | 11.25 | 10.44 | 9.69 | 8.67 | 7.57 | 6.46 | 5.37 | 4.29 | -0.49 | -2.62 | -3.6
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Consumer Transformation | Thermal headroom (MW) | 1.11 | 1.07 | 0.96 | 0.8 | 0.57 | 0.23 | -0.11 | -0.5 | -0.9 | -1.31 | -1.94 | -2.84 | -3.77 | -4.7 | -5.62 | -11.22 | -14.68 | -16.35
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Leading the Way | Thermal headroom (MW) | 1.11 | 0.97 | 0.73 | 0.4 | -0.01 | -0.66 | -1.27 | -1.98 | -2.74 | -3.57 | -4.53 | -5.55 | -6.6 | -7.61 | -8.55 | -12.11 | -13.71 | -14.47
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Steady Progression | Thermal headroom (MW) | 1.11 | 1.21 | 1.24 | 1.25 | 1.24 | 1.15 | 1.03 | 0.85 | 0.65 | 0.42 | 0.09 | -0.24 | -0.59 | -0.98 | -1.36 | -3.4 | -4.82 | -5.53
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | System Transformation | Thermal headroom (MW) | 1.11 | 1.17 | 1.15 | 1.12 | 1.05 | 0.96 | 0.8 | 0.59 | 0.34 | 0.06 | -0.35 | -0.81 | -1.28 | -1.74 | -2.22 | -4.43 | -5.73 | -6.26
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | WPD Best View | Thermal headroom (MW) | 1.11 | 1.2 | 1.21 | 1.2 | 1.18 | 1.06 | 0.9 | 0.7 | 0.47 | 0.22 | -0.12 | -0.46 | -0.81 | -1.18 | -1.54 | -3.88 | -5.38 | -6.1
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Consumer Transformation | Thermal headroom (MW) | 11.94 | 11.4 | 11.11 | 10.73 | 10.08 | 9.11 | 8.12 | 7.11 | 6.08 | 4.41 | 1.77 | -0.88 | -3.6 | -6.17 | -8.64 | -21.21 | -28.13 | -31.01
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Leading the Way | Thermal headroom (MW) | 11.94 | 11.55 | 10.99 | 10.18 | 9.09 | 7.34 | 5.45 | 3.4 | 1.05 | -1.51 | -4.1 | -6.83 | -9.65 | -12.17 | -14.5 | -22.71 | -25.94 | -27.02
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Steady Progression | Thermal headroom (MW) | 11.94 | 12 | 11.91 | 11.81 | 11.64 | 11.21 | 10.79 | 10.24 | 9.65 | 9.04 | 8.2 | 7.36 | 6.44 | 5.45 | 4.08 | -3.58 | -8.32 | -10.5
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | System Transformation | Thermal headroom (MW) | 11.94 | 11.92 | 11.75 | 11.56 | 11.23 | 10.85 | 10.37 | 9.8 | 9.18 | 8.47 | 7.16 | 5.79 | 4.36 | 3.06 | 1.74 | -6.5 | -10.67 | -12.29
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | WPD Best View | Thermal headroom (MW) | 11.94 | 12 | 11.91 | 11.81 | 11.64 | 11.21 | 10.79 | 10.24 | 9.65 | 9.04 | 8.2 | 7.36 | 6.44 | 5.45 | 4.08 | -3.58 | -8.32 | -10.5
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Consumer Transformation | Thermal headroom (MW) | 0.84 | 0.63 | 0.24 | -0.32 | -1.36 | -2.51 | -3.69 | -4.91 | -6.21 | -8.18 | -11.85 | -15.54 | -19.22 | -22.78 | -26.28 | -40.03 | -50.34 | -55.8
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Leading the Way | Thermal headroom (MW) | 0.84 | 0.34 | -0.4 | -1.06 | -2.39 | -4.22 | -5.98 | -8.35 | -11.26 | -14.42 | -17.85 | -21.5 | -25.23 | -28.8 | -32.02 | -41.54 | -45.44 | -46.85
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Steady Progression | Thermal headroom (MW) | 0.84 | 0.95 | 0.85 | 0.71 | 0.36 | -0.19 | -0.77 | -1.24 | -1.78 | -2.38 | -3.18 | -4.01 | -4.88 | -5.81 | -7.06 | -16.28 | -22.54 | -25.12
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | System Transformation | Thermal headroom (MW) | 0.84 | 0.83 | 0.58 | 0.26 | -0.34 | -0.72 | -1.21 | -1.81 | -2.5 | -3.28 | -4.27 | -5.65 | -7.08 | -8.63 | -10.63 | -20.6 | -24.77 | -25.64
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | WPD Best View | Thermal headroom (MW) | 0.84 | 0.95 | 0.85 | 0.71 | 0.36 | -0.19 | -0.77 | -1.24 | -1.78 | -2.38 | -3.18 | -4.01 | -4.88 | -5.81 | -7.06 | -16.28 | -22.54 | -25.12
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Consumer Transformation | Thermal headroom (MW) | 12.9 | 12.83 | 12.66 | 12.44 | 12.05 | 11.28 | 10.49 | 9.75 | 8.99 | 8.17 | 6.49 | 4.69 | 2.88 | 1.13 | -0.62 | -11.19 | -17.87 | -20.76
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Leading the Way | Thermal headroom (MW) | 12.9 | 12.6 | 12.17 | 11.48 | 10.64 | 9.26 | 8 | 6.49 | 4.99 | 3.36 | 1.48 | -0.45 | -2.37 | -4.23 | -5.98 | -12.94 | -15.87 | -17.01
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Steady Progression | Thermal headroom (MW) | 12.9 | 13.06 | 13.11 | 13.14 | 13.12 | 12.86 | 12.59 | 12.29 | 11.92 | 11.53 | 10.96 | 10.39 | 9.78 | 9.15 | 8.5 | 4.34 | 1.26 | -0.45
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | System Transformation | Thermal headroom (MW) | 12.9 | 12.99 | 12.97 | 12.92 | 12.79 | 12.52 | 12.22 | 11.84 | 11.4 | 10.91 | 10.16 | 9.4 | 8.63 | 7.89 | 7.18 | 2.26 | -0.26 | -1.31
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | WPD Best View | Thermal headroom (MW) | 12.9 | 12.6 | 12.17 | 11.48 | 10.64 | 9.26 | 8 | 6.49 | 4.99 | 3.36 | 1.48 | -0.45 | -2.36 | -4.22 | -5.97 | -12.92 | -15.86 | -17
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Consumer Transformation | Thermal headroom (MW) | 91.74 | 90.43 | 89.28 | 87.86 | 85.04 | 80.28 | 75.5 | 71.21 | 66.61 | 61.22 | 54.46 | 47.89 | 41.34 | 35 | 28.96 | 2.3 | -11 | -15.47
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Leading the Way | Thermal headroom (MW) | 91.74 | 89.49 | 86.8 | 84.28 | 80.09 | 73.28 | 66.46 | 59.64 | 52.95 | 45.21 | 38.49 | 31.68 | 25.1 | 18.82 | 13.05 | -2.96 | -6.2 | -5.09
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Steady Progression | Thermal headroom (MW) | 91.74 | 91.83 | 91.79 | 91.69 | 90.75 | 88.52 | 86.33 | 84.28 | 82.17 | 79.6 | 76.82 | 74.34 | 71.66 | 68.5 | 65.26 | 46.32 | 36.52 | 33.96
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | System Transformation | Thermal headroom (MW) | 91.74 | 91.44 | 91.05 | 90.58 | 88.94 | 86.42 | 83.6 | 81.04 | 78.46 | 75.33 | 71.95 | 68.7 | 65.08 | 61.38 | 57.45 | 37.88 | 31.68 | 31.35
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | WPD Best View | Thermal headroom (MW) | 91.74 | 89.5 | 86.84 | 84.34 | 80.18 | 73.43 | 66.68 | 59.93 | 53.42 | 45.79 | 38.97 | 32.22 | 25.74 | 19.55 | 13.9 | -1.87 | -4.65 | -2.97
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Consumer Transformation | Thermal headroom (MW) | 9.27 | 9.17 | 8.92 | 8.51 | 7.95 | 6.99 | 6.05 | 5.09 | 4.16 | 3.19 | 1.46 | -0.52 | -2.56 | -4.53 | -6.45 | -16.72 | -22.46 | -25.78
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Leading the Way | Thermal headroom (MW) | 9.27 | 9.01 | 8.57 | 8.02 | 7.24 | 5.94 | 4.41 | 2.81 | 0.92 | -1.09 | -2.87 | -4.84 | -6.83 | -8.67 | -10.34 | -17.47 | -20.57 | -22.26
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Steady Progression | Thermal headroom (MW) | 9.27 | 9.38 | 9.35 | 9.28 | 9.14 | 8.72 | 8.29 | 7.81 | 7.3 | 6.74 | 6.04 | 5.31 | 4.55 | 3.72 | 2.64 | -4.72 | -8.65 | -10.42
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | System Transformation | Thermal headroom (MW) | 9.27 | 9.3 | 9.19 | 9 | 8.71 | 8.41 | 8.08 | 7.55 | 6.92 | 6.38 | 5.66 | 4.88 | 4.1 | 3.34 | 2.54 | -5.12 | -10.08 | -11.82
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | WPD Best View | Thermal headroom (MW) | 9.27 | 9.38 | 9.35 | 9.28 | 9.14 | 8.72 | 8.29 | 7.81 | 7.3 | 6.74 | 6.04 | 5.31 | 4.55 | 3.72 | 2.64 | -4.72 | -8.65 | -10.42
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Consumer Transformation | Thermal headroom (MW) | 7.13 | 6.74 | 6.33 | 5.76 | 4.95 | 3.81 | 2.71 | 1.58 | 0.44 | -0.88 | -3.95 | -6.99 | -10.07 | -13.11 | -16.23 | -26.48 | -39.71 | -49.25
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Leading the Way | Thermal headroom (MW) | 7.13 | 6.49 | 5.69 | 4.83 | 3.28 | 1.11 | -1.04 | -3.78 | -9.52 | -15.78 | -18.26 | -22.17 | -27.25 | -32.64 | -37.39 | -55.06 | -75.23 | -95.39
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Steady Progression | Thermal headroom (MW) | 7.13 | 6.93 | 6.75 | 6.51 | 6.18 | 5.61 | 5.05 | 4.49 | 3.85 | 0.83 | -2.81 | -3.5 | -4.33 | -5.91 | -6.7 | -12.21 | -15.27 | -16.61
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | System Transformation | Thermal headroom (MW) | 7.13 | 6.78 | 6.42 | 5.99 | 5.47 | 4.83 | 4.11 | 3.33 | 2.46 | 1.71 | -0.17 | -0.95 | -3.06 | -4.49 | -6.55 | -14.91 | -22.5 | -26.46
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | WPD Best View | Thermal headroom (MW) | 7.13 | 6.49 | 5.69 | 4.83 | 3.28 | 1.12 | -1.03 | -3.77 | -9.51 | -15.77 | -18.25 | -22.16 | -27.23 | -32.63 | -37.38 | -55.05 | -75.23 | -95.43
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Consumer Transformation | Thermal headroom (MW) | 3.88 | 3.84 | 3.69 | 3.37 | 2.8 | 2.16 | 1.41 | 0.78 | 0.08 | -0.67 | -2.37 | -4.07 | -5.83 | -7.57 | -9.17 | -17.96 | -22.53 | -24.52
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Leading the Way | Thermal headroom (MW) | 3.88 | 3.67 | 3.34 | 2.85 | 2.03 | 0.97 | -0.28 | -1.65 | -3.32 | -5.06 | -6.71 | -8.48 | -10.23 | -11.86 | -13.36 | -18.86 | -20.44 | -20.64
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Steady Progression | Thermal headroom (MW) | 3.88 | 4.04 | 4.08 | 4.06 | 3.94 | 3.65 | 3.33 | 3.01 | 2.64 | 2.25 | 1.69 | 1.12 | 0.52 | -0.15 | -1.06 | -6.98 | -10.21 | -11.68
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | System Transformation | Thermal headroom (MW) | 3.88 | 3.96 | 3.93 | 3.82 | 3.55 | 3.32 | 2.99 | 2.67 | 2.28 | 1.83 | 1.27 | 0.65 | 0.02 | -0.58 | -1.51 | -7.81 | -10.84 | -11.62
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | WPD Best View | Thermal headroom (MW) | 3.88 | 4.04 | 4.08 | 4.06 | 3.94 | 3.65 | 3.33 | 3.01 | 2.64 | 2.25 | 1.69 | 1.12 | 0.52 | -0.15 | -1.06 | -6.98 | -10.21 | -11.68
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Consumer Transformation | Thermal headroom (MW) | -1.21 | -1.15 | -1.2 | -1.3 | -1.47 | -1.87 | -2.33 | -2.78 | -3.23 | -3.77 | -4.66 | -5.71 | -6.82 | -7.86 | -8.83 | -13.11 | -14.9 | -15.64
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Leading the Way | Thermal headroom (MW) | -1.21 | -1.22 | -1.36 | -1.53 | -1.79 | -2.36 | -3.01 | -3.83 | -4.78 | -6.07 | -6.95 | -7.88 | -8.84 | -9.71 | -10.49 | -13.22 | -13.79 | -13.8
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Steady Progression | Thermal headroom (MW) | -1.21 | -1.07 | -1.03 | -1.01 | -1.02 | -1.22 | -1.46 | -1.72 | -2 | -2.34 | -2.79 | -3.24 | -3.72 | -4.32 | -5.01 | -9.44 | -11.13 | -11.52
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | System Transformation | Thermal headroom (MW) | -1.21 | -1.1 | -1.12 | -1.15 | -1.24 | -1.33 | -1.49 | -1.68 | -1.9 | -2.22 | -2.58 | -2.98 | -3.39 | -3.79 | -4.19 | -8.29 | -10.74 | -11.14
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | WPD Best View | Thermal headroom (MW) | -1.21 | -1.07 | -1.03 | -1.01 | -1.02 | -1.22 | -1.46 | -1.72 | -2 | -2.34 | -2.79 | -3.24 | -3.72 | -4.32 | -5.01 | -9.44 | -11.13 | -11.52
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Consumer Transformation | Thermal headroom (MW) | -6.29 | -6.16 | -6.21 | -6.3 | -6.51 | -7.17 | -7.83 | -8.53 | -9.18 | -10.07 | -11.15 | -12.98 | -14.83 | -16.61 | -18.37 | -24.32 | -26.85 | -28.03
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Leading the Way | Thermal headroom (MW) | -6.29 | -6.23 | -6.38 | -6.55 | -6.87 | -7.69 | -8.53 | -9.5 | -10.63 | -12.31 | -13.65 | -15.09 | -16.53 | -18 | -18.98 | -23.36 | -24.97 | -25.43
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Steady Progression | Thermal headroom (MW) | -6.29 | -6.06 | -6.03 | -5.98 | -5.96 | -6.27 | -6.59 | -6.96 | -7.33 | -7.88 | -8.58 | -9.27 | -9.98 | -10.73 | -11.56 | -18.81 | -21.62 | -22.51
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | System Transformation | Thermal headroom (MW) | -6.29 | -6.11 | -6.13 | -6.14 | -6.24 | -6.3 | -6.39 | -6.64 | -6.93 | -7.4 | -7.84 | -8.32 | -9.16 | -9.99 | -10.78 | -17.26 | -22.3 | -23.34
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | WPD Best View | Thermal headroom (MW) | -6.29 | -6.14 | -6.19 | -6.25 | -6.42 | -7.06 | -7.72 | -8.47 | -9.22 | -10.55 | -11.2 | -12.13 | -13.18 | -14.25 | -15.27 | -21.03 | -23.37 | -24.46
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Consumer Transformation | Thermal headroom (MW) | 6.6 | 6.24 | 5.91 | 5.19 | 3.96 | 1.69 | -0.55 | -2.76 | -5.01 | -9.13 | -16.98 | -25.33 | -33.24 | -40.6 | -48.08 | -77.63 | -108.17 | -128.37
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Leading the Way | Thermal headroom (MW) | 6.6 | 6.12 | 4.89 | 3.68 | 1.73 | -1.91 | -5.43 | -9.91 | -15.21 | -21.88 | -28.16 | -35.39 | -42.04 | -48.17 | -53.86 | -71.81 | -79.56 | -83.46
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Steady Progression | Thermal headroom (MW) | 6.6 | 7.13 | 7.31 | 7.33 | 7.17 | 6.52 | 5.96 | 5.34 | 4.64 | 2.64 | -0.04 | -2.01 | -4.28 | -7.17 | -9.83 | -25.93 | -35.89 | -39.64
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | System Transformation | Thermal headroom (MW) | 6.6 | 6.95 | 6.93 | 6.73 | 6.22 | 5.61 | 5.07 | 4.34 | 3.26 | 1.48 | -0.77 | -3.17 | -5.86 | -9.28 | -12.83 | -30.52 | -38.42 | -40.73
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | WPD Best View | Thermal headroom (MW) | 6.6 | 7.13 | 7.31 | 7.33 | 7.17 | 6.52 | 5.96 | 5.34 | 4.64 | 2.64 | -0.04 | -2.01 | -4.28 | -7.17 | -9.83 | -25.93 | -35.89 | -39.64
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Consumer Transformation | Thermal headroom (MW) | 13.97 | 13.96 | 13.95 | 13.93 | 13.89 | 13.85 | 13.8 | 13.75 | 13.7 | 13.64 | 13.58 | 13.52 | 13.39 | 13.24 | 13.09 | 12.42 | 12.06 | 11.89
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Leading the Way | Thermal headroom (MW) | 13.97 | 13.96 | 13.94 | 13.91 | 13.86 | 13.79 | 13.72 | 13.65 | 13.56 | 13.47 | 13.39 | 13.24 | 13.09 | 12.94 | 12.8 | 12.38 | 12.2 | 12.16
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Steady Progression | Thermal headroom (MW) | 13.97 | 13.98 | 13.99 | 13.99 | 13.99 | 13.97 | 13.95 | 13.93 | 13.9 | 13.87 | 13.83 | 13.78 | 13.74 | 13.69 | 13.64 | 13.33 | 13.05 | 12.94
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | System Transformation | Thermal headroom (MW) | 13.97 | 13.98 | 13.97 | 13.97 | 13.95 | 13.93 | 13.91 | 13.88 | 13.85 | 13.81 | 13.77 | 13.73 | 13.68 | 13.63 | 13.58 | 13.25 | 12.99 | 12.92
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | WPD Best View | Thermal headroom (MW) | 13.97 | 13.98 | 13.99 | 13.99 | 13.99 | 13.97 | 13.95 | 13.93 | 13.9 | 13.87 | 13.83 | 13.78 | 13.74 | 13.69 | 13.64 | 13.33 | 13.05 | 12.94
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Consumer Transformation | Thermal headroom (MW) | 1.12 | 1.07 | 0.93 | 0.67 | 0.24 | -0.34 | -0.96 | -1.61 | -2.45 | -3.57 | -5.37 | -7.12 | -8.92 | -10.66 | -12.32 | -20.68 | -25.14 | -27.02
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Leading the Way | Thermal headroom (MW) | 1.12 | 0.87 | 0.53 | 0.08 | -0.61 | -1.62 | -2.79 | -4.34 | -5.91 | -7.58 | -9.35 | -11.23 | -13.11 | -14.83 | -16.42 | -21.54 | -22.83 | -22.61
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Steady Progression | Thermal headroom (MW) | 1.12 | 1.25 | 1.27 | 1.25 | 1.2 | 0.99 | 0.74 | 0.47 | 0.17 | -0.18 | -0.66 | -1.14 | -1.83 | -2.62 | -3.46 | -9.34 | -13.23 | -15.01
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | System Transformation | Thermal headroom (MW) | 1.12 | 1.17 | 1.1 | 0.99 | 0.79 | 0.57 | 0.3 | -0.03 | -0.38 | -0.79 | -1.3 | -1.88 | -2.8 | -3.81 | -4.88 | -11.24 | -14.01 | -14.46
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | WPD Best View | Thermal headroom (MW) | 1.12 | 1.25 | 1.27 | 1.25 | 1.2 | 0.99 | 0.74 | 0.47 | 0.17 | -0.18 | -0.66 | -1.14 | -1.83 | -2.62 | -3.46 | -9.34 | -13.23 | -15.01
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Consumer Transformation | Thermal headroom (MW) | 42.67 | 41.49 | 40.8 | 39.99 | 37.53 | 36.42 | 35.42 | 34.31 | 33.1 | 31.67 | 29.24 | 26.8 | 24.37 | 21.99 | 19.71 | 8.35 | 2.47 | 0.34
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Leading the Way | Thermal headroom (MW) | 42.67 | 40.88 | 39.7 | 38.41 | 35.02 | 33.42 | 31.93 | 30.34 | 28.71 | 26.76 | 24.41 | 21.94 | 19.47 | 17.08 | 14.9 | 8.51 | 6.87 | 7.84
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Steady Progression | Thermal headroom (MW) | 42.67 | 41.98 | 41.73 | 41.42 | 39.94 | 39.51 | 39.15 | 38.68 | 38.31 | 37.89 | 37.24 | 36.55 | 35.82 | 35.03 | 34.18 | 27.05 | 21.49 | 19.99
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | System Transformation | Thermal headroom (MW) | 42.67 | 41.72 | 41.28 | 40.8 | 38.83 | 38.4 | 38.1 | 37.69 | 37.17 | 36.6 | 35.77 | 34.85 | 33.77 | 32.58 | 31.27 | 23.77 | 20.96 | 21.5
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | WPD Best View | Thermal headroom (MW) | 42.67 | 41.98 | 41.73 | 41.42 | 39.77 | 39.34 | 38.97 | 38.5 | 38.13 | 37.71 | 37.06 | 36.45 | 35.79 | 35 | 34.16 | 27.01 | 21.49 | 20.02
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Consumer Transformation | Thermal headroom (MW) | 0.22 | 0.1 | -0.17 | -0.44 | -0.85 | -1.72 | -2.58 | -3.41 | -4.29 | -5.17 | -6.32 | -7.5 | -8.66 | -9.73 | -10.78 | -16.69 | -19.15 | -20.13
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Leading the Way | Thermal headroom (MW) | 0.22 | -0.13 | -0.69 | -1.19 | -1.78 | -2.88 | -4.02 | -5.28 | -6.54 | -7.82 | -8.91 | -10.07 | -11.19 | -12.18 | -13.08 | -16.83 | -17.55 | -17.54
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Steady Progression | Thermal headroom (MW) | 0.22 | 0.23 | 0.12 | 0.03 | -0.09 | -0.44 | -0.79 | -1.13 | -1.47 | -1.84 | -2.45 | -3.02 | -3.59 | -4.16 | -4.76 | -9.29 | -11.2 | -11.88
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | System Transformation | Thermal headroom (MW) | 0.22 | 0.19 | 0.02 | -0.11 | -0.32 | -0.45 | -0.6 | -0.81 | -1.09 | -1.38 | -1.88 | -2.41 | -2.94 | -3.51 | -4.11 | -8.77 | -11.8 | -12.42
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | WPD Best View | Thermal headroom (MW) | 0.22 | 0.23 | 0.12 | 0.03 | -0.09 | -0.44 | -0.79 | -1.13 | -1.47 | -1.84 | -2.45 | -3.02 | -3.59 | -4.16 | -4.76 | -9.29 | -11.2 | -11.88
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Consumer Transformation | Thermal headroom (MW) | 1.22 | 1.17 | 1.04 | 0.73 | 0.34 | -0.33 | -0.95 | -1.51 | -2.07 | -2.86 | -4.5 | -6.15 | -7.82 | -9.45 | -11.07 | -18.95 | -23.98 | -26.79
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Leading the Way | Thermal headroom (MW) | 1.22 | 1 | 0.68 | 0.2 | -0.41 | -1.3 | -2.31 | -3.39 | -4.96 | -6.71 | -8.14 | -9.67 | -11.29 | -12.81 | -14.18 | -19.02 | -20.71 | -21.46
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Steady Progression | Thermal headroom (MW) | 1.22 | 1.34 | 1.36 | 1.27 | 1.22 | 0.96 | 0.7 | 0.44 | 0.16 | -0.17 | -0.66 | -1.19 | -1.77 | -2.55 | -3.37 | -9.6 | -12.95 | -14.05
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | System Transformation | Thermal headroom (MW) | 1.22 | 1.28 | 1.22 | 1.04 | 0.87 | 0.71 | 0.53 | 0.33 | 0.09 | -0.2 | -0.61 | -1.1 | -1.6 | -2.4 | -3.34 | -9.82 | -13.55 | -14.05
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | WPD Best View | Thermal headroom (MW) | 1.22 | 1.34 | 1.36 | 1.27 | 1.22 | 0.96 | 0.7 | 0.44 | 0.16 | -0.17 | -0.66 | -1.19 | -1.77 | -2.55 | -3.37 | -9.6 | -12.95 | -14.05
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Consumer Transformation | Thermal headroom (MW) | -4.1 | -4.63 | -4.86 | -5.22 | -5.79 | -7.15 | -8.24 | -9.22 | -10.64 | -12.23 | -14.36 | -16.57 | -18.79 | -20.93 | -23.01 | -31.99 | -36.26 | -37.71
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Leading the Way | Thermal headroom (MW) | -4.1 | -4.59 | -5.49 | -6.13 | -7.09 | -9.22 | -10.9 | -12.77 | -14.81 | -17.06 | -19.16 | -21.45 | -23.7 | -25.92 | -27.94 | -33.93 | -35.94 | -36.12
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Steady Progression | Thermal headroom (MW) | -4.1 | -3.99 | -4.02 | -4.08 | -4.18 | -4.92 | -5.48 | -5.94 | -6.43 | -7.09 | -7.97 | -8.75 | -9.56 | -10.84 | -12.16 | -19.64 | -24.32 | -26.4
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | System Transformation | Thermal headroom (MW) | -4.1 | -4.1 | -4.24 | -4.43 | -4.72 | -5.5 | -6.04 | -6.49 | -7.01 | -7.56 | -8.87 | -10.12 | -11.67 | -13.16 | -14.81 | -23.66 | -28.11 | -29.03
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | WPD Best View | Thermal headroom (MW) | -4.1 | -3.99 | -4.02 | -4.08 | -4.18 | -4.92 | -5.48 | -5.94 | -6.43 | -7.09 | -7.97 | -8.75 | -9.56 | -10.84 | -12.16 | -19.64 | -24.32 | -26.4
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Consumer Transformation | Thermal headroom (MW) | 19.65 | 18.98 | 17.95 | 16.61 | 14.57 | 12.05 | 9.4 | 6.62 | 3.71 | 0.59 | -5.3 | -11.45 | -17.36 | -23.07 | -28.57 | -57.8 | -74.66 | -82.63
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Leading the Way | Thermal headroom (MW) | 19.65 | 18.36 | 16.66 | 14.34 | 11.42 | 7.48 | 3.07 | -1.98 | -7.2 | -13.03 | -19.61 | -26.36 | -32.8 | -38.9 | -44.44 | -60.39 | -66.34 | -68.29
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Steady Progression | Thermal headroom (MW) | 19.65 | 19.75 | 19.58 | 19.3 | 18.88 | 17.96 | 16.92 | 15.7 | 14.34 | 12.82 | 10.81 | 8.72 | 6.54 | 4.27 | 2.03 | -10.89 | -21.03 | -25.1
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | System Transformation | Thermal headroom (MW) | 19.65 | 19.49 | 18.99 | 18.38 | 17.51 | 16.45 | 15.12 | 13.53 | 11.72 | 9.67 | 7.23 | 4.64 | 2.16 | -0.25 | -2.59 | -17.09 | -23.92 | -26.32
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | WPD Best View | Thermal headroom (MW) | 19.65 | 19.72 | 19.5 | 19.19 | 18.73 | 17.76 | 16.63 | 15.3 | 13.82 | 12.16 | 10.05 | 7.86 | 5.72 | 3.49 | 1.25 | -11.9 | -21.99 | -26.07
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Consumer Transformation | Thermal headroom (MW) | 1.55 | 1.38 | 1.09 | 0.62 | 0.01 | -1.01 | -1.95 | -2.88 | -3.82 | -4.86 | -8.77 | -12.72 | -16.65 | -20.5 | -24.49 | -38.13 | -56.26 | -69.66
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Leading the Way | Thermal headroom (MW) | 1.55 | 1.15 | 0.6 | -0.13 | -1.37 | -3.08 | -4.95 | -7.38 | -11.96 | -16.9 | -19.47 | -23.06 | -27.46 | -32.05 | -36.39 | -53.84 | -71.35 | -88.27
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Steady Progression | Thermal headroom (MW) | 1.55 | 1.6 | 1.55 | 1.42 | 1.24 | 0.83 | 0.4 | -0.07 | -0.59 | -2.7 | -5.39 | -6.12 | -7 | -8.56 | -9.59 | -17.3 | -21.47 | -23.52
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | System Transformation | Thermal headroom (MW) | 1.55 | 1.37 | 1.13 | 0.75 | 0.26 | -0.2 | -0.75 | -1.49 | -2.43 | -3.08 | -5.26 | -6.31 | -8.56 | -9.91 | -12.47 | -24.29 | -35.69 | -41.91
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | WPD Best View | Thermal headroom (MW) | 1.55 | 1.6 | 1.55 | 1.42 | 1.24 | 0.83 | 0.4 | -0.07 | -0.59 | -2.7 | -5.39 | -6.12 | -7 | -8.56 | -9.59 | -17.3 | -21.47 | -23.52
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Consumer Transformation | Thermal headroom (MW) | 0.12 | 0.09 | 0.07 | 0.02 | -0.1 | -0.35 | -0.59 | -0.83 | -1.35 | -1.95 | -2.85 | -3.77 | -4.62 | -5.44 | -6.23 | -9.66 | -10.97 | -11.45
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Leading the Way | Thermal headroom (MW) | 0.12 | 0.03 | -0.06 | -0.16 | -0.35 | -0.72 | -1.2 | -2.03 | -3 | -4.08 | -4.86 | -5.78 | -6.71 | -7.58 | -8.36 | -11.06 | -11.78 | -11.97
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Steady Progression | Thermal headroom (MW) | 0.12 | 0.16 | 0.19 | 0.21 | 0.22 | 0.11 | 0.01 | -0.13 | -0.28 | -0.54 | -1.09 | -1.52 | -2 | -2.53 | -3.07 | -6.7 | -8.36 | -8.97
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | System Transformation | Thermal headroom (MW) | 0.12 | 0.11 | 0.11 | 0.08 | 0 | -0.05 | -0.13 | -0.24 | -0.38 | -0.52 | -0.9 | -1.37 | -2.01 | -2.61 | -3.32 | -7.47 | -9.71 | -10.17
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | WPD Best View | Thermal headroom (MW) | 0.12 | 0.16 | 0.19 | 0.21 | 0.22 | 0.11 | 0.01 | -0.13 | -0.28 | -0.54 | -1.09 | -1.52 | -2 | -2.53 | -3.07 | -6.7 | -8.36 | -8.97
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Consumer Transformation | Thermal headroom (MW) | 3.45 | 2.88 | 1.89 | 0.62 | -1.07 | -2.99 | -4.92 | -7.37 | -10.67 | -14.39 | -20.34 | -26.14 | -31.94 | -37.45 | -42.84 | -66.82 | -79.34 | -84.03
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Leading the Way | Thermal headroom (MW) | 3.45 | 2.26 | 0.59 | -1.37 | -3.96 | -7.52 | -11.53 | -16.28 | -21.16 | -26.54 | -32.54 | -38.53 | -44.44 | -50.08 | -55.21 | -69.37 | -72.13 | -70.49
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Steady Progression | Thermal headroom (MW) | 3.45 | 3.59 | 3.31 | 2.89 | 2.33 | 1.49 | 0.66 | -0.29 | -1.34 | -2.47 | -4.14 | -6.25 | -8.5 | -10.84 | -13.33 | -29.84 | -39.73 | -43.26
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | System Transformation | Thermal headroom (MW) | 3.45 | 3.29 | 2.69 | 1.92 | 0.89 | 0.05 | -0.81 | -1.81 | -3 | -4.49 | -6.48 | -9.32 | -12.36 | -15.65 | -19.09 | -35.9 | -41.94 | -42.76
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | WPD Best View | Thermal headroom (MW) | 3.45 | 3.59 | 3.31 | 2.89 | 2.33 | 1.49 | 0.66 | -0.29 | -1.34 | -2.47 | -4.14 | -6.25 | -8.5 | -10.84 | -13.33 | -29.84 | -39.73 | -43.26
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Consumer Transformation | Thermal headroom (MW) | -0.31 | -0.15 | -0.13 | -0.22 | -0.35 | -0.64 | -0.91 | -1.18 | -1.46 | -1.76 | -2.07 | -2.34 | -2.77 | -3.17 | -3.6 | -6.43 | -7.53 | -7.95
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Leading the Way | Thermal headroom (MW) | -0.31 | -0.18 | -0.19 | -0.33 | -0.54 | -0.97 | -1.39 | -1.85 | -2.43 | -3.14 | -3.43 | -3.76 | -4.12 | -4.67 | -5.22 | -7.48 | -8.47 | -9.19
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Steady Progression | Thermal headroom (MW) | -0.31 | -0.11 | -0.04 | -0.01 | 0.01 | -0.12 | -0.26 | -0.42 | -0.6 | -0.87 | -1.24 | -1.52 | -1.82 | -2.15 | -2.47 | -4.95 | -5.75 | -5.95
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | System Transformation | Thermal headroom (MW) | -0.31 | -0.14 | -0.1 | -0.12 | -0.19 | -0.24 | -0.3 | -0.41 | -0.55 | -0.69 | -1.08 | -1.35 | -1.73 | -2 | -2.33 | -4.06 | -6.37 | -7.08
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | WPD Best View | Thermal headroom (MW) | -0.31 | -0.11 | -0.04 | -0.01 | 0.01 | -0.12 | -0.26 | -0.42 | -0.6 | -0.87 | -1.24 | -1.52 | -1.82 | -2.15 | -2.47 | -4.95 | -5.75 | -5.95
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Consumer Transformation | Thermal headroom (MW) | 5.95 | 5.95 | 5.9 | 5.87 | 5.83 | 5.61 | 5.2 | 4.96 | 4.68 | 4.4 | 4 | 3.61 | 3.19 | 2.76 | 2.35 | 0.4 | -0.56 | -1
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Leading the Way | Thermal headroom (MW) | 5.95 | 5.89 | 5.77 | 5.68 | 5.56 | 5.12 | 4.44 | 3.94 | 3.36 | 2.74 | 2.41 | 1.99 | 1.51 | 1.02 | 0.56 | -1.2 | -2.17 | -2.93
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Steady Progression | Thermal headroom (MW) | 5.95 | 5.97 | 5.94 | 5.92 | 5.9 | 5.77 | 5.54 | 5.4 | 5.25 | 5.01 | 4.7 | 4.46 | 4.22 | 3.96 | 3.72 | 2.01 | 1.49 | 1.29
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | System Transformation | Thermal headroom (MW) | 5.95 | 5.93 | 5.88 | 5.83 | 5.76 | 5.7 | 5.46 | 5.37 | 5.26 | 5.13 | 4.78 | 4.54 | 4.17 | 3.91 | 3.56 | 1.7 | 0.29 | -0.36
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | WPD Best View | Thermal headroom (MW) | 5.95 | 5.97 | 5.94 | 5.92 | 5.9 | 5.77 | 5.54 | 5.4 | 5.25 | 5.01 | 4.7 | 4.46 | 4.22 | 3.96 | 3.72 | 2.01 | 1.49 | 1.29
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Consumer Transformation | Thermal headroom (MW) | 24.88 | 24.21 | 23.46 | 22.58 | 20.55 | 18.44 | 16.22 | 13.97 | 11.68 | 9.25 | 4.54 | -1.67 | -7.98 | -14.14 | -20.38 | -44.16 | -70.17 | -87.55
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Leading the Way | Thermal headroom (MW) | 24.88 | 24.13 | 22.52 | 21.25 | 18.51 | 15.85 | 12.93 | 9.7 | 5.76 | 0.68 | -3.91 | -8.94 | -14.06 | -19.06 | -23.64 | -37.54 | -43.7 | -47.05
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Steady Progression | Thermal headroom (MW) | 24.88 | 25.22 | 25.18 | 25.14 | 24.41 | 23.69 | 23.09 | 22.45 | 21.69 | 19.88 | 17.52 | 16.18 | 14.38 | 12.29 | 10.48 | 0.1 | -8.26 | -11.66
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | System Transformation | Thermal headroom (MW) | 24.88 | 24.98 | 24.67 | 24.36 | 23.17 | 22.42 | 21.8 | 20.98 | 19.92 | 18.71 | 16.8 | 14.83 | 12.89 | 11 | 8.92 | -3.43 | -9.55 | -10.87
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | WPD Best View | Thermal headroom (MW) | 24.88 | 24.98 | 24.67 | 24.36 | 23.17 | 22.42 | 21.8 | 20.98 | 19.92 | 18.71 | 16.8 | 14.83 | 12.89 | 11 | 8.92 | -3.43 | -9.55 | -10.87
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Consumer Transformation | Thermal headroom (MW) | -9.31 | -9.24 | -9.47 | -9.72 | -10.23 | -10.96 | -11.84 | -12.58 | -13.29 | -14.09 | -15.05 | -15.86 | -16.63 | -18.06 | -19.73 | -28.88 | -34.07 | -36.65
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Leading the Way | Thermal headroom (MW) | -9.31 | -9.43 | -9.9 | -10.33 | -11.06 | -12.08 | -13.24 | -14.35 | -15.31 | -16.54 | -17.69 | -19.13 | -21 | -22.77 | -24.38 | -29.98 | -31.99 | -32.88
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Steady Progression | Thermal headroom (MW) | -9.31 | -8.93 | -8.83 | -8.69 | -8.64 | -8.81 | -9.05 | -9.33 | -9.63 | -10.01 | -10.54 | -11.11 | -11.71 | -12.34 | -12.99 | -16.39 | -18.26 | -18.96
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | System Transformation | Thermal headroom (MW) | -9.31 | -9.04 | -9.07 | -9.04 | -9.18 | -9.32 | -9.59 | -9.91 | -10.33 | -10.77 | -11.33 | -11.96 | -12.56 | -13.15 | -13.67 | -16.26 | -19.16 | -19.91
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | WPD Best View | Thermal headroom (MW) | -9.31 | -9.04 | -9.07 | -9.04 | -9.18 | -9.32 | -9.59 | -9.91 | -10.33 | -10.77 | -11.33 | -11.96 | -12.56 | -13.15 | -13.67 | -16.26 | -19.16 | -19.91
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Consumer Transformation | Thermal headroom (MW) | 5.18 | 5.14 | 4.88 | 4.52 | 3.82 | 2.83 | 1.83 | 0.79 | -0.26 | -1.39 | -2.97 | -5.13 | -7.55 | -9.91 | -12.25 | -24.41 | -32.73 | -36.86
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Leading the Way | Thermal headroom (MW) | 5.18 | 4.83 | 4.22 | 3.54 | 2.36 | 0.8 | -0.7 | -2.34 | -3.91 | -5.85 | -8.29 | -10.84 | -13.43 | -16 | -18.39 | -26.69 | -30.47 | -32.25
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Steady Progression | Thermal headroom (MW) | 5.18 | 5.5 | 5.6 | 5.64 | 5.58 | 5.33 | 5.04 | 4.61 | 4.08 | 3.47 | 2.64 | 1.78 | 0.85 | -0.12 | -1.11 | -6.43 | -10.13 | -12.14
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | System Transformation | Thermal headroom (MW) | 5.18 | 5.38 | 5.34 | 5.25 | 4.98 | 4.72 | 4.3 | 3.75 | 3.12 | 2.35 | 1.35 | 0.29 | -0.8 | -1.85 | -2.97 | -7.9 | -11 | -12.13
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | WPD Best View | Thermal headroom (MW) | 5.18 | 5.38 | 5.34 | 5.25 | 4.98 | 4.72 | 4.3 | 3.75 | 3.12 | 2.35 | 1.35 | 0.29 | -0.8 | -1.85 | -2.97 | -7.9 | -11 | -12.13
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Consumer Transformation | Thermal headroom (MW) | -0.33 | -0.38 | -0.62 | -0.8 | -1.27 | -1.75 | -2.3 | -2.85 | -3.48 | -4.2 | -5.22 | -6.26 | -7.29 | -8.32 | -9.32 | -14.53 | -17.18 | -18.38
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Leading the Way | Thermal headroom (MW) | -0.33 | -0.5 | -0.93 | -1.25 | -2 | -2.75 | -3.52 | -4.4 | -5.28 | -6.28 | -7.26 | -8.26 | -9.31 | -10.29 | -11.24 | -14.77 | -15.76 | -15.85
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Steady Progression | Thermal headroom (MW) | -0.33 | -0.27 | -0.36 | -0.42 | -0.65 | -0.86 | -1.06 | -1.3 | -1.57 | -1.88 | -2.31 | -2.73 | -3.19 | -3.68 | -4.25 | -8.19 | -10.56 | -11.66
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | System Transformation | Thermal headroom (MW) | -0.33 | -0.34 | -0.54 | -0.63 | -1.01 | -1.18 | -1.33 | -1.55 | -1.77 | -2.06 | -2.56 | -3.03 | -3.58 | -4.19 | -4.87 | -9.2 | -11.15 | -11.35
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | WPD Best View | Thermal headroom (MW) | -0.33 | -0.34 | -0.54 | -0.63 | -1.01 | -1.18 | -1.33 | -1.54 | -1.77 | -2.06 | -2.56 | -3.03 | -3.58 | -4.19 | -4.87 | -9.2 | -11.16 | -11.38
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Consumer Transformation | Thermal headroom (MW) | 2.08 | 2.05 | 1.87 | 1.67 | 1.36 | 0.78 | 0.15 | -0.5 | -1.16 | -1.86 | -2.62 | -3.8 | -5.19 | -6.56 | -7.9 | -16.16 | -21.16 | -24.33
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Leading the Way | Thermal headroom (MW) | 2.08 | 1.96 | 1.63 | 1.33 | 0.88 | 0.04 | -0.96 | -2.05 | -3.08 | -4.44 | -5.87 | -7.32 | -8.8 | -10.23 | -11.57 | -17.47 | -20.45 | -22.53
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Steady Progression | Thermal headroom (MW) | 2.08 | 2.24 | 2.24 | 2.25 | 2.22 | 2.05 | 1.86 | 1.64 | 1.36 | 1.02 | 0.58 | 0.11 | -0.39 | -0.92 | -1.45 | -5.09 | -7.6 | -8.89
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | System Transformation | Thermal headroom (MW) | 2.08 | 2.19 | 2.12 | 2.08 | 1.97 | 1.86 | 1.74 | 1.38 | 0.86 | 0.47 | -0.05 | -0.59 | -1.15 | -1.7 | -2.21 | -6.73 | -9.94 | -11.43
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | WPD Best View | Thermal headroom (MW) | 2.08 | 2.19 | 2.12 | 2.08 | 1.97 | 1.86 | 1.74 | 1.38 | 0.86 | 0.47 | -0.05 | -0.59 | -1.15 | -1.7 | -2.21 | -6.73 | -9.94 | -11.43
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Consumer Transformation | Thermal headroom (MW) | 6.85 | 6.32 | 5.68 | 5.57 | 5.14 | 4.59 | 4.23 | 3.67 | 3.12 | 2.64 | 1.91 | 1.19 | 0.51 | -0.09 | -0.69 | -4.16 | -5.87 | -6.82
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Leading the Way | Thermal headroom (MW) | 6.85 | 6.1 | 5.3 | 5.08 | 4.48 | 3.69 | 3.2 | 2.25 | 1.44 | 0.76 | 0.07 | -0.66 | -1.33 | -1.95 | -2.51 | -4.39 | -5.1 | -5.49
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Steady Progression | Thermal headroom (MW) | 6.85 | 6.48 | 6.01 | 6.01 | 5.75 | 5.48 | 5.34 | 5.06 | 4.8 | 4.62 | 4.39 | 4.14 | 3.86 | 3.61 | 3.36 | 1.3 | 0.32 | 0.31
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | System Transformation | Thermal headroom (MW) | 6.85 | 6.39 | 5.82 | 5.79 | 5.45 | 5.2 | 5.11 | 4.75 | 4.41 | 4.23 | 3.91 | 3.6 | 3.3 | 2.98 | 2.63 | 0.47 | -0.79 | -1.04
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | WPD Best View | Thermal headroom (MW) | 6.85 | 6.48 | 6.01 | 6.01 | 5.75 | 5.48 | 5.35 | 5.07 | 4.8 | 4.63 | 4.4 | 4.14 | 3.87 | 3.61 | 3.36 | 1.3 | 0.29 | 0.26
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Consumer Transformation | Thermal headroom (MW) | 0.66 | 0.6 | 0.44 | 0.2 | -0.17 | -0.73 | -1.29 | -1.85 | -2.41 | -3.01 | -3.88 | -5.15 | -6.4 | -7.69 | -8.95 | -15.5 | -19.03 | -20.77
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Leading the Way | Thermal headroom (MW) | 0.66 | 0.5 | 0.2 | -0.16 | -0.68 | -1.5 | -2.46 | -3.47 | -4.66 | -5.97 | -7.05 | -8.24 | -9.43 | -10.56 | -11.63 | -15.84 | -17.42 | -18.12
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Steady Progression | Thermal headroom (MW) | 0.66 | 0.76 | 0.76 | 0.72 | 0.64 | 0.36 | 0.06 | -0.27 | -0.66 | -1.08 | -1.62 | -2.16 | -2.73 | -3.33 | -3.94 | -8.88 | -11.34 | -12.36
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | System Transformation | Thermal headroom (MW) | 0.66 | 0.71 | 0.65 | 0.54 | 0.35 | 0.17 | -0.05 | -0.33 | -0.65 | -1.04 | -1.52 | -2.04 | -2.58 | -3.09 | -3.58 | -7.88 | -10.97 | -11.9
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | WPD Best View | Thermal headroom (MW) | 0.66 | 0.76 | 0.76 | 0.72 | 0.64 | 0.36 | 0.06 | -0.27 | -0.66 | -1.08 | -1.62 | -2.16 | -2.73 | -3.33 | -3.94 | -8.88 | -11.34 | -12.36
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Consumer Transformation | Thermal headroom (MW) | 0.27 | 0.01 | -0.06 | -0.22 | -0.45 | -0.96 | -1.5 | -2.02 | -2.54 | -3.16 | -4.02 | -4.94 | -5.86 | -6.73 | -7.54 | -10.88 | -12.1 | -12.59
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Leading the Way | Thermal headroom (MW) | 0.27 | -0.03 | -0.23 | -0.49 | -0.84 | -1.52 | -2.23 | -3.03 | -3.81 | -4.69 | -5.38 | -6.15 | -6.94 | -7.66 | -8.3 | -10.47 | -10.92 | -10.7
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Steady Progression | Thermal headroom (MW) | 0.27 | 0.08 | 0.03 | -0.06 | -0.19 | -0.48 | -0.76 | -1.08 | -1.39 | -1.72 | -2.19 | -2.65 | -3.15 | -3.69 | -4.21 | -8.25 | -10.21 | -10.8
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | System Transformation | Thermal headroom (MW) | 0.27 | 0.06 | 0.01 | -0.15 | -0.29 | -0.44 | -0.58 | -0.77 | -0.97 | -1.22 | -1.58 | -2.04 | -2.56 | -3.1 | -3.76 | -7.5 | -9.84 | -10.19
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | WPD Best View | Thermal headroom (MW) | 0.27 | 0.08 | 0.03 | -0.06 | -0.19 | -0.48 | -0.76 | -1.08 | -1.39 | -1.72 | -2.19 | -2.65 | -3.15 | -3.69 | -4.21 | -8.25 | -10.21 | -10.8
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Consumer Transformation | Thermal headroom (MW) | 11.73 | 10.93 | 10.19 | 9.33 | 7.82 | 6.08 | 4.32 | 2.57 | 0.76 | -1.49 | -6.61 | -11.84 | -17.11 | -22.2 | -27.09 | -53.05 | -67.93 | -74.52
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Leading the Way | Thermal headroom (MW) | 11.73 | 10.73 | 9.4 | 8.02 | 5.69 | 2.69 | -0.25 | -4.21 | -8.63 | -13.41 | -18.65 | -24.24 | -29.79 | -35.12 | -40.08 | -55.9 | -61.43 | -62.65
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Steady Progression | Thermal headroom (MW) | 11.73 | 12.03 | 11.97 | 11.95 | 11.72 | 11.15 | 10.52 | 9.75 | 8.77 | 7.67 | 6.19 | 4.67 | 3.02 | 1.28 | -0.84 | -16.31 | -26.43 | -30.55
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | System Transformation | Thermal headroom (MW) | 11.73 | 11.78 | 11.47 | 11.17 | 10.53 | 9.99 | 9.29 | 8.34 | 7.21 | 5.92 | 4.01 | 1.94 | -0.15 | -2.28 | -5.4 | -22.11 | -29.46 | -31.71
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | WPD Best View | Thermal headroom (MW) | 11.73 | 12.03 | 11.97 | 11.95 | 11.72 | 11.15 | 10.52 | 9.75 | 8.77 | 7.67 | 6.19 | 4.67 | 3.02 | 1.28 | -0.84 | -16.31 | -26.43 | -30.55
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Consumer Transformation | Thermal headroom (MW) | 7.87 | 7.41 | 7.15 | 6.27 | 5.74 | 5.04 | 4.31 | 3.58 | 2.85 | 2.09 | 0.97 | -0.64 | -2.29 | -3.89 | -5.49 | -15.4 | -21.23 | -23.8
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Leading the Way | Thermal headroom (MW) | 7.87 | 7.09 | 6.53 | 5.17 | 4.19 | 2.94 | 1.79 | 0.53 | -0.91 | -2.45 | -4.12 | -5.87 | -7.66 | -9.43 | -11.09 | -17.17 | -19.2 | -20.07
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Steady Progression | Thermal headroom (MW) | 7.87 | 7.75 | 7.78 | 7.3 | 7.19 | 6.93 | 6.65 | 6.33 | 5.98 | 5.53 | 4.9 | 4.24 | 3.57 | 2.88 | 2.18 | -2.38 | -5.29 | -6.6
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | System Transformation | Thermal headroom (MW) | 7.87 | 7.61 | 7.52 | 6.85 | 6.59 | 6.35 | 6.1 | 5.75 | 5.31 | 4.81 | 4.19 | 3.54 | 2.88 | 2.24 | 1.66 | -3.32 | -6.15 | -7.14
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | WPD Best View | Thermal headroom (MW) | 7.87 | 7.75 | 7.78 | 7.3 | 7.19 | 6.93 | 6.65 | 6.33 | 5.98 | 5.53 | 4.9 | 4.24 | 3.57 | 2.88 | 2.18 | -2.38 | -5.29 | -6.6
Iron Acton 132kV | Ryeford 132 33 | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Consumer Transformation | Thermal headroom (MW) | 9.08 | 9.08 | 8.93 | 8.68 | 8.24 | 7.58 | 6.93 | 6.21 | 5.43 | 4.63 | 3.47 | 1.48 | -0.61 | -2.67 | -4.67 | -13.73 | -18.12 | -19.94
Iron Acton 132kV | Ryeford 132 33 | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Leading the Way | Thermal headroom (MW) | 9.08 | 8.94 | 8.63 | 8.25 | 7.6 | 6.65 | 5.69 | 4.41 | 3.13 | 1.46 | -0.37 | -2.3 | -4.28 | -6.17 | -7.66 | -13.09 | -15.13 | -15.52
Iron Acton 132kV | Ryeford 132 33 | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Steady Progression | Thermal headroom (MW) | 9.08 | 9.29 | 9.35 | 9.38 | 9.31 | 8.99 | 8.66 | 8.26 | 7.8 | 7.29 | 6.66 | 6.01 | 5.33 | 4.62 | 3.89 | -3.31 | -7.5 | -8.88
Iron Acton 132kV | Ryeford 132 33 | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | System Transformation | Thermal headroom (MW) | 9.08 | 9.21 | 9.19 | 9.12 | 8.89 | 8.7 | 8.46 | 8.12 | 7.7 | 7.24 | 6.69 | 6.06 | 5.05 | 4.09 | 3.18 | -3.89 | -8.6 | -9.4
Iron Acton 132kV | Ryeford 132 33 | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | WPD Best View | Thermal headroom (MW) | 9.08 | 9.27 | 9.3 | 9.29 | 9.17 | 8.93 | 8.66 | 8.31 | 7.89 | 7.42 | 6.83 | 6.21 | 5.56 | 4.9 | 4.26 | -2.49 | -7.11 | -8.44
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Consumer Transformation | Thermal headroom (MW) | 6.77 | 5.73 | 5.38 | 4.89 | 4.34 | 3.58 | 2.86 | 2.05 | 1.36 | 0.75 | -0.61 | -1.97 | -3.35 | -4.67 | -5.95 | -10.37 | -12.68 | -13.95
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Leading the Way | Thermal headroom (MW) | 6.77 | 5.55 | 5.12 | 4.55 | 4.01 | 3.22 | 2.39 | 1.34 | 0.29 | -0.82 | -2.12 | -3.49 | -4.84 | -6.11 | -7.22 | -10.56 | -12.1 | -12.71
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Steady Progression | Thermal headroom (MW) | 6.77 | 6 | 5.84 | 5.62 | 5.44 | 5.14 | 4.83 | 4.5 | 4.25 | 4.02 | 3.73 | 3.45 | 3.16 | 2.84 | 2.54 | -1.26 | -3.61 | -4.66
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | System Transformation | Thermal headroom (MW) | 6.77 | 5.83 | 5.61 | 5.32 | 5.05 | 4.78 | 4.53 | 4.14 | 3.71 | 3.44 | 3.11 | 2.41 | 1.72 | 1.03 | 0.22 | -4.46 | -7.27 | -8.25
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | WPD Best View | Thermal headroom (MW) | 6.77 | 6 | 5.84 | 5.62 | 5.44 | 5.14 | 4.83 | 4.5 | 4.25 | 4.02 | 3.73 | 3.45 | 3.16 | 2.84 | 2.54 | -1.26 | -3.61 | -4.66
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Consumer Transformation | Thermal headroom (MW) | 23.67 | 23.87 | 23.19 | 22.65 | 22.32 | 21.94 | 21.59 | 21.2 | 20.8 | 20.34 | 19.66 | 18.59 | 17.31 | 16.07 | 14.89 | 7.83 | 3.94 | 2.51
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Leading the Way | Thermal headroom (MW) | 23.67 | 23.66 | 22.71 | 21.85 | 21.25 | 20.73 | 20.11 | 19.3 | 18.51 | 17.49 | 16.08 | 14.6 | 13.18 | 11.84 | 10.62 | 6.82 | 5.82 | 6.01
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Steady Progression | Thermal headroom (MW) | 23.67 | 24.07 | 23.67 | 23.4 | 23.4 | 23.34 | 23.26 | 23.14 | 23 | 22.88 | 22.63 | 22.37 | 22.12 | 21.78 | 21.44 | 18.73 | 16.36 | 15.82
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | System Transformation | Thermal headroom (MW) | 23.67 | 23.99 | 23.44 | 23.02 | 22.89 | 22.83 | 22.75 | 22.63 | 22.46 | 22.27 | 22.03 | 21.67 | 21.31 | 20.97 | 20.68 | 17.17 | 15.53 | 15.53
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | WPD Best View | Thermal headroom (MW) | 23.67 | 24.07 | 23.67 | 23.4 | 23.4 | 23.34 | 23.26 | 23.14 | 23 | 22.88 | 22.63 | 22.37 | 22.12 | 21.78 | 21.44 | 18.73 | 16.36 | 15.82
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Consumer Transformation | Thermal headroom (MW) | 27.48 | 27.01 | 25.31 | 23.29 | 21.66 | 20.12 | 18.47 | 17.13 | 15.59 | 14.14 | 11.11 | 8.14 | 5.1 | 2.14 | -0.8 | -15.75 | -25.2 | -29.34
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Leading the Way | Thermal headroom (MW) | 27.48 | 26.34 | 23.87 | 20.85 | 18.35 | 15.9 | 13.51 | 11.34 | 8.85 | 6.49 | 3.56 | 0.41 | -2.8 | -5.91 | -8.88 | -18.03 | -21.53 | -22.35
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Steady Progression | Thermal headroom (MW) | 27.48 | 27.52 | 26.38 | 25.05 | 24.18 | 23.42 | 22.59 | 21.9 | 21.15 | 20.48 | 19.58 | 18.73 | 17.88 | 17.01 | 16.11 | 8.94 | 4.52 | 2.94
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | System Transformation | Thermal headroom (MW) | 27.48 | 27.31 | 25.85 | 24.12 | 22.9 | 22.05 | 21.08 | 20.4 | 19.54 | 18.81 | 17.94 | 16.62 | 15.19 | 13.67 | 12.04 | 3.75 | 0.74 | 0.4
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | WPD Best View | Thermal headroom (MW) | 27.48 | 26.34 | 23.87 | 20.85 | 18.35 | 15.9 | 13.51 | 11.34 | 8.85 | 6.49 | 3.56 | 0.41 | -2.8 | -5.91 | -8.88 | -18.03 | -21.53 | -22.35
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Consumer Transformation | Thermal headroom (MW) | 1.71 | 1.58 | 1.38 | 1.12 | 0.71 | 0.26 | -0.18 | -0.63 | -1.08 | -1.59 | -2.63 | -3.9 | -5.17 | -6.38 | -7.59 | -14.46 | -18.15 | -19.81
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Leading the Way | Thermal headroom (MW) | 1.71 | 1.46 | 1.13 | 0.75 | 0.17 | -0.67 | -1.52 | -2.49 | -3.58 | -4.85 | -6.05 | -7.34 | -8.62 | -9.81 | -10.94 | -14.87 | -16.23 | -16.64
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Steady Progression | Thermal headroom (MW) | 1.71 | 1.75 | 1.74 | 1.72 | 1.63 | 1.42 | 1.2 | 0.94 | 0.66 | 0.34 | -0.1 | -0.53 | -1 | -1.49 | -1.99 | -6.28 | -8.55 | -9.35
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | System Transformation | Thermal headroom (MW) | 1.71 | 1.68 | 1.6 | 1.5 | 1.28 | 1.12 | 0.93 | 0.68 | 0.39 | 0.06 | -0.38 | -0.86 | -1.34 | -1.81 | -2.22 | -6.41 | -8.63 | -9.24
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | WPD Best View | Thermal headroom (MW) | 1.71 | 1.64 | 1.5 | 1.31 | 0.99 | 0.73 | 0.44 | 0.11 | -0.24 | -0.62 | -1.05 | -1.56 | -2.33 | -3.08 | -3.84 | -7.98 | -10.17 | -10.81
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Consumer Transformation | Thermal headroom (MW) | 2.2 | 2.24 | 2.26 | 2.27 | 2.25 | 2.04 | 1.79 | 1.51 | 1.23 | 0.97 | 0.57 | 0.19 | -0.2 | -0.59 | -0.97 | -2.28 | -2.82 | -3.07
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Leading the Way | Thermal headroom (MW) | 2.2 | 2.22 | 2.22 | 2.22 | 2.14 | 1.77 | 1.38 | 0.91 | 0.36 | -0.21 | -0.44 | -0.76 | -1.12 | -1.49 | -1.82 | -3.23 | -4.08 | -4.7
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Steady Progression | Thermal headroom (MW) | 2.2 | 2.2 | 2.18 | 2.15 | 2.1 | 1.94 | 1.79 | 1.64 | 1.49 | 1.26 | 0.92 | 0.66 | 0.4 | 0.07 | -0.23 | -2.06 | -2.63 | -2.9
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | System Transformation | Thermal headroom (MW) | 2.2 | 2.2 | 2.17 | 2.13 | 2.07 | 2.02 | 1.98 | 1.9 | 1.81 | 1.7 | 1.33 | 1.13 | 0.8 | 0.55 | 0.22 | -1.58 | -3.23 | -3.91
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | WPD Best View | Thermal headroom (MW) | 2.2 | 2.2 | 2.17 | 2.13 | 2.07 | 2.02 | 1.98 | 1.9 | 1.81 | 1.7 | 1.33 | 1.13 | 0.8 | 0.55 | 0.22 | -1.58 | -3.23 | -3.91
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Consumer Transformation | Thermal headroom (MW) | 22.28 | 22.38 | 22.39 | 21.96 | 21.67 | 21.18 | 20.8 | 20.35 | 19.79 | 18.98 | 17.38 | 15.71 | 14.02 | 12.42 | 10.85 | 3.88 | 0.21 | -0.82
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Leading the Way | Thermal headroom (MW) | 22.28 | 22.09 | 21.83 | 21.05 | 20.44 | 19.54 | 18.83 | 18.04 | 17.15 | 15.94 | 14.34 | 12.59 | 10.85 | 9.2 | 7.65 | 3.6 | 2.69 | 3.6
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Steady Progression | Thermal headroom (MW) | 22.28 | 22.61 | 22.82 | 22.64 | 22.71 | 22.56 | 22.48 | 22.41 | 22.3 | 22.07 | 21.74 | 21.42 | 21.09 | 20.69 | 20.26 | 15.89 | 12.4 | 11.08
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | System Transformation | Thermal headroom (MW) | 22.28 | 22.49 | 22.55 | 22.19 | 22.1 | 21.91 | 21.74 | 21.59 | 21.44 | 21.03 | 20.67 | 19.86 | 18.94 | 17.95 | 16.89 | 11.48 | 9.48 | 9.65
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | WPD Best View | Thermal headroom (MW) | 22.28 | 22.09 | 21.83 | 21.05 | 20.44 | 19.54 | 18.83 | 18.04 | 17.15 | 15.94 | 14.34 | 12.59 | 10.85 | 9.2 | 7.65 | 3.59 | 2.67 | 3.59
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Consumer Transformation | Thermal headroom (MW) | 2.4 | 2.4 | 2.3 | 2.13 | 1.85 | 1.45 | 1.05 | 0.66 | 0.26 | -0.17 | -1.05 | -2.11 | -3.2 | -4.24 | -5.22 | -10.49 | -13.04 | -14.21
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Leading the Way | Thermal headroom (MW) | 2.4 | 2.33 | 2.13 | 1.87 | 1.48 | 0.87 | 0.13 | -0.65 | -1.59 | -2.66 | -3.59 | -4.61 | -5.6 | -6.57 | -7.48 | -10.64 | -11.62 | -11.87
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Steady Progression | Thermal headroom (MW) | 2.4 | 2.52 | 2.54 | 2.55 | 2.5 | 2.3 | 2.09 | 1.86 | 1.6 | 1.31 | 0.92 | 0.53 | 0.09 | -0.44 | -1.04 | -5.1 | -6.97 | -7.51
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | System Transformation | Thermal headroom (MW) | 2.4 | 2.48 | 2.46 | 2.39 | 2.25 | 2.12 | 1.96 | 1.76 | 1.54 | 1.28 | 0.92 | 0.52 | 0.12 | -0.27 | -0.66 | -4.5 | -6.8 | -7.34
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | WPD Best View | Thermal headroom (MW) | 2.4 | 2.48 | 2.46 | 2.39 | 2.25 | 2.12 | 1.96 | 1.76 | 1.54 | 1.28 | 0.92 | 0.52 | 0.12 | -0.27 | -0.66 | -4.5 | -6.8 | -7.34
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Consumer Transformation | Thermal headroom (MW) | 4.35 | 4.04 | 3.51 | 2.85 | 1.87 | 0.33 | -1.02 | -2.35 | -3.62 | -4.97 | -7.84 | -11.21 | -14.65 | -18.01 | -21.29 | -40.09 | -52.77 | -58.86
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Leading the Way | Thermal headroom (MW) | 4.35 | 3.53 | 2.45 | 1.09 | -0.71 | -3.26 | -5.53 | -8.02 | -10.59 | -13.36 | -16.79 | -20.36 | -23.95 | -27.47 | -30.78 | -41.96 | -46.8 | -48.74
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Steady Progression | Thermal headroom (MW) | 4.35 | 4.51 | 4.48 | 4.41 | 4.24 | 3.75 | 3.27 | 2.72 | 2.08 | 1.36 | 0.33 | -0.7 | -1.8 | -2.94 | -4.09 | -10.97 | -17.27 | -20.5
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | System Transformation | Thermal headroom (MW) | 4.35 | 4.32 | 4.09 | 3.79 | 3.33 | 2.76 | 2.16 | 1.42 | 0.61 | -0.28 | -1.58 | -2.95 | -4.34 | -5.67 | -6.92 | -14.16 | -18.49 | -20.09
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | WPD Best View | Thermal headroom (MW) | 4.35 | 3.53 | 2.45 | 1.09 | -0.71 | -3.26 | -5.53 | -8.02 | -10.59 | -13.36 | -16.79 | -20.36 | -23.95 | -27.47 | -30.78 | -41.96 | -46.8 | -48.74
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Consumer Transformation | Thermal headroom (MW) | -5.9 | -5.91 | -6.56 | -7.15 | -8.41 | -9.71 | -10.93 | -12.29 | -13.76 | -15.33 | -18.36 | -21.34 | -24.34 | -27.27 | -30.19 | -41.1 | -50.53 | -56.05
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Leading the Way | Thermal headroom (MW) | -5.9 | -6.32 | -7.41 | -8.42 | -10.35 | -12.3 | -14.03 | -16.18 | -18.77 | -21.53 | -24.13 | -26.99 | -30.04 | -32.99 | -35.66 | -43.31 | -46.73 | -48.46
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Steady Progression | Thermal headroom (MW) | -5.9 | -5.61 | -5.93 | -6.13 | -6.77 | -7.4 | -7.93 | -8.53 | -9.2 | -9.88 | -10.76 | -11.68 | -12.71 | -13.7 | -14.73 | -22.01 | -25.99 | -27.18
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | System Transformation | Thermal headroom (MW) | -5.9 | -5.78 | -6.3 | -6.7 | -7.65 | -8.2 | -8.7 | -9.31 | -10.03 | -10.85 | -11.84 | -13.25 | -14.72 | -16.35 | -17.97 | -25.85 | -28.8 | -28.88
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | WPD Best View | Thermal headroom (MW) | -5.9 | -5.78 | -6.3 | -6.7 | -7.65 | -8.2 | -8.7 | -9.31 | -10.03 | -10.85 | -11.84 | -13.25 | -14.72 | -16.35 | -17.97 | -25.85 | -28.8 | -28.88
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Consumer Transformation | Thermal headroom (MW) | 3.5 | 3.5 | 3.52 | 3.53 | 3.52 | 3.3 | 3.06 | 2.84 | 2.59 | 2.34 | 1.97 | 1.62 | 1.25 | 0.92 | 0.6 | -0.59 | -1.11 | -1.36
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Leading the Way | Thermal headroom (MW) | 3.5 | 3.48 | 3.48 | 3.48 | 3.45 | 3.08 | 2.69 | 2.31 | 1.95 | 1.53 | 1.32 | 1.1 | 0.91 | 0.72 | 0.53 | -0.52 | -0.88 | -1.04
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Steady Progression | Thermal headroom (MW) | 3.5 | 3.47 | 3.45 | 3.42 | 3.38 | 3.22 | 3.06 | 2.91 | 2.75 | 2.6 | 2.37 | 2.16 | 1.9 | 1.58 | 1.26 | -0.46 | -0.9 | -1.12
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | System Transformation | Thermal headroom (MW) | 3.5 | 3.47 | 3.46 | 3.43 | 3.39 | 3.37 | 3.36 | 3.34 | 3.32 | 3.3 | 3.08 | 2.87 | 2.66 | 2.45 | 2.26 | 0.84 | -0.31 | -0.64
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | WPD Best View | Thermal headroom (MW) | 3.5 | 3.47 | 3.46 | 3.43 | 3.39 | 3.37 | 3.36 | 3.34 | 3.32 | 3.3 | 3.08 | 2.87 | 2.66 | 2.45 | 2.26 | 0.84 | -0.31 | -0.64
Ironbridge & Shrewsbury 132kV | Ketley 132 11 (GT3) | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Consumer Transformation | Thermal headroom (MW) | 37.12 | 36.15 | 35.48 | 34.63 | 33.62 | 32.19 | 30.9 | 29.57 | 28.25 | 26.33 | 23.12 | 19.88 | 16.67 | 13.49 | 10.48 | -6.63 | -16.77 | -21.05
Ironbridge & Shrewsbury 132kV | Ketley 132 11 (GT3) | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Leading the Way | Thermal headroom (MW) | 37.12 | 35.79 | 34.32 | 32.78 | 31.09 | 28.65 | 26.33 | 23.85 | 21.17 | 18.11 | 14.78 | 11.32 | 7.84 | 4.49 | 1.37 | -8.53 | -12.15 | -12.93
Ironbridge & Shrewsbury 132kV | Ketley 132 11 (GT3) | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Steady Progression | Thermal headroom (MW) | 37.12 | 37.03 | 36.88 | 36.71 | 36.5 | 35.89 | 35.3 | 34.6 | 33.93 | 33.18 | 32.19 | 31.2 | 30.17 | 29.09 | 27.61 | 19.06 | 13.35 | 10.83
Ironbridge & Shrewsbury 132kV | Ketley 132 11 (GT3) | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | System Transformation | Thermal headroom (MW) | 37.12 | 36.89 | 36.57 | 36.2 | 35.72 | 35.12 | 34.53 | 33.88 | 33.18 | 32.37 | 30.95 | 29.4 | 27.77 | 26.04 | 24.27 | 14.72 | 10.76 | 9.16
Ironbridge & Shrewsbury 132kV | Ketley 132 11 (GT3) | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | WPD Best View | Thermal headroom (MW) | 37.12 | 35.79 | 34.32 | 32.78 | 31.09 | 28.65 | 26.33 | 23.85 | 21.17 | 18.11 | 14.78 | 11.32 | 7.84 | 4.49 | 1.37 | -8.53 | -12.15 | -12.93
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Consumer Transformation | Thermal headroom (MW) | 4.18 | 4.22 | 4.13 | 3.96 | 3.63 | 3.17 | 2.75 | 2.38 | 1.99 | 1.55 | 0.96 | 0.28 | -0.58 | -1.55 | -2.58 | -9.5 | -13.38 | -15.1
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Leading the Way | Thermal headroom (MW) | 4.18 | 4.1 | 3.86 | 3.57 | 3.09 | 2.21 | 1.41 | 0.63 | -0.09 | -0.86 | -1.84 | -2.94 | -4.08 | -5.17 | -6.2 | -10.51 | -12.06 | -12.63
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Steady Progression | Thermal headroom (MW) | 4.18 | 4.38 | 4.46 | 4.51 | 4.5 | 4.31 | 4.14 | 3.98 | 3.77 | 3.53 | 3.18 | 2.8 | 2.41 | 2 | 1.59 | -0.76 | -2.36 | -3.35
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | System Transformation | Thermal headroom (MW) | 4.18 | 4.34 | 4.36 | 4.36 | 4.26 | 4.04 | 3.85 | 3.65 | 3.42 | 3.14 | 2.76 | 2.34 | 1.93 | 1.53 | 1.17 | -1.51 | -3.2 | -3.66
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | WPD Best View | Thermal headroom (MW) | 4.18 | 4.1 | 3.86 | 3.57 | 3.1 | 2.23 | 1.45 | 0.69 | -0.01 | -0.77 | -1.73 | -2.84 | -3.94 | -4.99 | -5.99 | -10.33 | -11.94 | -12.55
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Consumer Transformation | Thermal headroom (MW) | 8.12 | 7.96 | 7.71 | 7.39 | 7.01 | 6.46 | 5.68 | 4.72 | 3.93 | 3.03 | 1.15 | -0.7 | -2.57 | -4.4 | -6.2 | -15.18 | -19.9 | -21.76
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Leading the Way | Thermal headroom (MW) | 8.12 | 7.84 | 7.44 | 7 | 6.41 | 5.39 | 3.95 | 1.76 | 0.08 | -1.39 | -3.3 | -5.23 | -7.16 | -9.03 | -10.42 | -15.65 | -17.65 | -18.15
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Steady Progression | Thermal headroom (MW) | 8.12 | 8.16 | 8.15 | 8.1 | 8.02 | 7.77 | 7.36 | 6.81 | 6.31 | 5.83 | 5.23 | 4.63 | 3.99 | 3.3 | 2.56 | -2.71 | -5.44 | -6.52
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | System Transformation | Thermal headroom (MW) | 8.12 | 8.11 | 8.02 | 7.89 | 7.72 | 7.5 | 7.01 | 6.27 | 5.68 | 5.18 | 4.55 | 3.9 | 2.87 | 1.83 | 0.66 | -4.97 | -7.47 | -8.08
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | WPD Best View | Thermal headroom (MW) | 8.12 | 7.84 | 7.44 | 7 | 6.41 | 5.41 | 3.97 | 1.8 | 0.13 | -1.32 | -3.23 | -5.16 | -7.09 | -8.96 | -10.35 | -15.62 | -17.64 | -18.14
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Consumer Transformation | Thermal headroom (MW) | -4.05 | -3.98 | -4.13 | -4.3 | -4.59 | -5.44 | -6.02 | -6.6 | -7.61 | -8.41 | -10.23 | -12.05 | -13.89 | -15.69 | -17.43 | -25.97 | -30.41 | -31.88
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Leading the Way | Thermal headroom (MW) | -4.05 | -4.29 | -4.77 | -5.24 | -5.83 | -7.35 | -8.45 | -9.66 | -11.37 | -12.75 | -14.55 | -16.48 | -18.33 | -20.15 | -21.89 | -27.18 | -28.72 | -28.63
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Steady Progression | Thermal headroom (MW) | -4.05 | -3.73 | -3.67 | -3.61 | -3.57 | -3.95 | -4.15 | -4.37 | -4.84 | -5.23 | -5.77 | -6.28 | -6.84 | -7.44 | -8.08 | -13.3 | -16.15 | -17.17
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | System Transformation | Thermal headroom (MW) | -4.05 | -3.79 | -3.78 | -3.79 | -3.83 | -4.16 | -4.35 | -4.55 | -5.14 | -5.47 | -5.98 | -6.97 | -7.99 | -9.09 | -10.17 | -16.13 | -18.6 | -19
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | WPD Best View | Thermal headroom (MW) | -4.05 | -4.29 | -4.77 | -5.24 | -5.82 | -7.32 | -8.41 | -9.59 | -11.28 | -12.65 | -14.45 | -16.38 | -18.25 | -20.07 | -21.82 | -27.18 | -28.77 | -28.7
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Consumer Transformation | Thermal headroom (MW) | 8.95 | 8.74 | 8.47 | 8.17 | 7.52 | 6.9 | 6.27 | 5.62 | 4.89 | 4.01 | 2.72 | 1.46 | 0.2 | -1.07 | -2.33 | -8.89 | -11.59 | -12.51
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Leading the Way | Thermal headroom (MW) | 8.95 | 8.64 | 8.26 | 7.86 | 6.96 | 5.86 | 4.86 | 3.68 | 2.44 | 1.15 | -0.13 | -1.47 | -2.78 | -4.03 | -5.21 | -9.65 | -10.52 | -10.47
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Steady Progression | Thermal headroom (MW) | 8.95 | 8.9 | 8.82 | 8.75 | 8.4 | 8.05 | 7.71 | 7.32 | 6.91 | 6.47 | 5.92 | 5.39 | 4.69 | 3.92 | 3.15 | -1.67 | -3.6 | -4.05
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | System Transformation | Thermal headroom (MW) | 8.95 | 8.85 | 8.71 | 8.57 | 8.11 | 7.75 | 7.38 | 6.95 | 6.47 | 6.01 | 5.46 | 4.79 | 4.06 | 3.24 | 2.45 | -2.24 | -3.9 | -4.08
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | WPD Best View | Thermal headroom (MW) | 8.95 | 8.85 | 8.71 | 8.57 | 8.11 | 7.75 | 7.38 | 6.95 | 6.47 | 6.01 | 5.46 | 4.79 | 4.06 | 3.24 | 2.45 | -2.25 | -3.9 | -4.09
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Consumer Transformation | Thermal headroom (MW) | 4.26 | 3.67 | 2.65 | 1.67 | 0.75 | -0.11 | -0.96 | -1.87 | -2.66 | -3.52 | -5.5 | -7.96 | -10.43 | -12.76 | -14.97 | -27.1 | -32.25 | -33.67
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Leading the Way | Thermal headroom (MW) | 4.26 | 3.34 | 1.97 | 0.6 | -0.59 | -1.84 | -3.28 | -5.06 | -6.81 | -9.37 | -11.9 | -14.61 | -17.25 | -19.67 | -21.81 | -28.18 | -28.97 | -27.64
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Steady Progression | Thermal headroom (MW) | 4.26 | 4.15 | 3.63 | 3.2 | 2.95 | 2.63 | 2.27 | 1.83 | 1.48 | 1.08 | 0.59 | 0.11 | -0.39 | -0.9 | -1.41 | -7 | -10.32 | -10.6
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | System Transformation | Thermal headroom (MW) | 4.26 | 3.94 | 3.19 | 2.54 | 2.07 | 1.7 | 1.26 | 0.74 | 0.31 | -0.24 | -0.77 | -1.35 | -1.93 | -2.56 | -3.91 | -10.72 | -12.2 | -11.49
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | WPD Best View | Thermal headroom (MW) | 4.26 | 3.34 | 1.97 | 0.6 | -0.59 | -1.84 | -3.28 | -5.06 | -6.81 | -9.37 | -11.9 | -14.61 | -17.25 | -19.67 | -21.81 | -28.18 | -28.97 | -27.64
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Consumer Transformation | Thermal headroom (MW) | 6.55 | 6.11 | 5.82 | 5.47 | 4.94 | 4.25 | 3.54 | 2.81 | 2.1 | 1 | -0.52 | -2.74 | -5.01 | -7.23 | -9.44 | -20.88 | -28.09 | -31.43
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Leading the Way | Thermal headroom (MW) | 6.55 | 6.25 | 5.72 | 5.17 | 4.39 | 3.1 | 1.86 | 0.52 | -1.38 | -3.53 | -5.7 | -8.01 | -10.35 | -12.64 | -14.78 | -22.1 | -25.2 | -26.4
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Steady Progression | Thermal headroom (MW) | 6.55 | 6.75 | 6.75 | 6.74 | 6.67 | 6.45 | 6.21 | 5.94 | 5.59 | 5.16 | 4.56 | 3.96 | 3.3 | 2.63 | 1.59 | -4.01 | -8.04 | -9.76
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | System Transformation | Thermal headroom (MW) | 6.55 | 6.67 | 6.56 | 6.44 | 6.22 | 6.07 | 5.86 | 5.51 | 5.12 | 4.65 | 3.67 | 2.65 | 1.6 | 0.58 | -0.38 | -6.69 | -10.13 | -11.39
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | WPD Best View | Thermal headroom (MW) | 6.55 | 6.67 | 6.56 | 6.44 | 6.22 | 6.07 | 5.86 | 5.51 | 5.12 | 4.65 | 3.67 | 2.65 | 1.6 | 0.58 | -0.38 | -6.69 | -10.13 | -11.39
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Consumer Transformation | Thermal headroom (MW) | 2.72 | 2.7 | 2.68 | 2.64 | 2.56 | 2.44 | 2.27 | 2.07 | 1.86 | 1.62 | 1.32 | 0.99 | 0.65 | 0.35 | 0.04 | -1.4 | -1.91 | -2.19
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Leading the Way | Thermal headroom (MW) | 2.72 | 2.68 | 2.63 | 2.57 | 2.46 | 2.25 | 2 | 1.7 | 1.4 | 1.06 | 0.83 | 0.55 | 0.29 | 0.05 | -0.19 | -1.06 | -1.39 | -1.48
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Steady Progression | Thermal headroom (MW) | 2.72 | 2.7 | 2.68 | 2.66 | 2.62 | 2.52 | 2.41 | 2.31 | 2.21 | 2.1 | 1.95 | 1.78 | 1.6 | 1.36 | 1.13 | -0.59 | -1.56 | -1.83
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | System Transformation | Thermal headroom (MW) | 2.72 | 2.7 | 2.68 | 2.65 | 2.6 | 2.57 | 2.53 | 2.48 | 2.42 | 2.35 | 2.2 | 1.99 | 1.79 | 1.6 | 1.38 | -0.24 | -1.45 | -1.7
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | WPD Best View | Thermal headroom (MW) | 2.72 | 2.7 | 2.68 | 2.65 | 2.6 | 2.57 | 2.53 | 2.48 | 2.42 | 2.35 | 2.2 | 1.99 | 1.79 | 1.6 | 1.38 | -0.24 | -1.45 | -1.7
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Consumer Transformation | Thermal headroom (MW) | 7.44 | 7.35 | 7.18 | 6.98 | 6.54 | 6.07 | 5.6 | 5.04 | 4.4 | 3.54 | 1.48 | -0.62 | -2.72 | -4.77 | -6.94 | -13.58 | -24.2 | -32.4
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Leading the Way | Thermal headroom (MW) | 7.44 | 7.18 | 6.85 | 6.46 | 5.28 | 4.17 | 2.91 | 1.13 | -3.6 | -8.92 | -10.47 | -13.38 | -17.51 | -21.9 | -26.09 | -41.49 | -59.76 | -78.54
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Steady Progression | Thermal headroom (MW) | 7.44 | 7.44 | 7.41 | 7.34 | 7.11 | 6.94 | 6.73 | 6.52 | 6.26 | 3.61 | 0.41 | 0.03 | -0.45 | -1.66 | -2.12 | -5.48 | -7.8 | -8.73
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | System Transformation | Thermal headroom (MW) | 7.44 | 7.28 | 7.07 | 6.83 | 6.4 | 6.14 | 5.79 | 5.37 | 4.84 | 4.3 | 2.78 | 2.32 | 0.92 | 0.18 | -1.27 | -7.74 | -13.74 | -16.8
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | WPD Best View | Thermal headroom (MW) | 7.44 | 7.28 | 7.07 | 6.83 | 6.4 | 6.14 | 5.79 | 5.37 | 4.84 | 4.3 | 2.78 | 2.32 | 0.92 | 0.18 | -1.27 | -7.74 | -13.74 | -16.8
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Consumer Transformation | Thermal headroom (MW) | 4.87 | 4.9 | 4.86 | 4.8 | 4.68 | 4.24 | 3.66 | 3.22 | 2.78 | 2.27 | 1.59 | 0.9 | 0.19 | -0.48 | -1.14 | -3.87 | -6.12 | -7.63
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Leading the Way | Thermal headroom (MW) | 4.87 | 4.83 | 4.73 | 4.62 | 4.41 | 3.73 | 2.9 | 2.18 | 1.36 | 0.41 | 0 | -0.55 | -1.13 | -1.66 | -2.13 | -4.22 | -5.35 | -6.14
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Steady Progression | Thermal headroom (MW) | 4.87 | 4.88 | 4.84 | 4.79 | 4.72 | 4.49 | 4.2 | 3.97 | 3.74 | 3.48 | 3.16 | 2.79 | 2.43 | 2.06 | 1.7 | -0.64 | -1.34 | -1.62
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | System Transformation | Thermal headroom (MW) | 4.87 | 4.89 | 4.84 | 4.79 | 4.71 | 4.62 | 4.41 | 4.31 | 4.2 | 3.94 | 3.65 | 3.35 | 3.05 | 2.76 | 2.41 | 0.4 | -0.95 | -1.37
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | WPD Best View | Thermal headroom (MW) | 4.87 | 4.83 | 4.72 | 4.59 | 4.38 | 3.93 | 3.31 | 2.8 | 2.18 | 1.43 | 1.05 | 0.52 | -0.02 | -0.52 | -1.03 | -3.25 | -4.84 | -5.72
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Consumer Transformation | Thermal headroom (MW) | 7.41 | 7.42 | 7.35 | 7.27 | 7.15 | 6.72 | 6.29 | 5.88 | 5.44 | 4.97 | 4.24 | 3.48 | 2.76 | 2.04 | 1.33 | -2.52 | -4.33 | -5.1
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Leading the Way | Thermal headroom (MW) | 7.41 | 7.25 | 7.01 | 6.79 | 6.51 | 5.83 | 5.17 | 4.43 | 3.72 | 2.94 | 2.34 | 1.68 | 1.02 | 0.37 | -0.24 | -2.55 | -3.28 | -3.54
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Steady Progression | Thermal headroom (MW) | 7.41 | 7.47 | 7.44 | 7.42 | 7.39 | 7.17 | 6.97 | 6.77 | 6.51 | 6.23 | 5.84 | 5.44 | 5.05 | 4.65 | 4.25 | 1.22 | -0.02 | -0.35
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | System Transformation | Thermal headroom (MW) | 7.41 | 7.46 | 7.42 | 7.39 | 7.33 | 7.28 | 7.17 | 7.06 | 6.94 | 6.78 | 6.49 | 6.12 | 5.76 | 5.36 | 4.94 | 2.1 | 0.16 | -0.29
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | WPD Best View | Thermal headroom (MW) | 7.41 | 7.46 | 7.42 | 7.39 | 7.33 | 7.28 | 7.17 | 7.06 | 6.94 | 6.78 | 6.49 | 6.12 | 5.76 | 5.36 | 4.94 | 2.1 | 0.16 | -0.29
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Consumer Transformation | Thermal headroom (MW) | -0.98 | -0.89 | -0.84 | -0.79 | -0.81 | -1.12 | -1.41 | -1.72 | -2.09 | -2.46 | -2.96 | -3.44 | -3.92 | -4.37 | -4.84 | -6.25 | -6.68 | -6.74
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Leading the Way | Thermal headroom (MW) | -0.98 | -0.89 | -0.91 | -0.91 | -0.99 | -1.53 | -2.08 | -2.66 | -3.49 | -4.39 | -4.74 | -5.19 | -5.73 | -6.3 | -6.81 | -8.73 | -9.91 | -10.87
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Steady Progression | Thermal headroom (MW) | -0.98 | -0.9 | -0.9 | -0.89 | -0.9 | -1.08 | -1.25 | -1.43 | -1.62 | -1.98 | -2.52 | -2.8 | -3.18 | -3.65 | -4.04 | -6.35 | -6.93 | -7.03
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | System Transformation | Thermal headroom (MW) | -0.98 | -0.93 | -0.94 | -0.98 | -1.04 | -1.09 | -1.15 | -1.23 | -1.38 | -1.48 | -2.1 | -2.4 | -2.98 | -3.37 | -3.92 | -6.5 | -8.88 | -9.79
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | WPD Best View | Thermal headroom (MW) | -0.98 | -0.91 | -0.95 | -0.96 | -1.03 | -1.32 | -1.6 | -1.9 | -2.35 | -2.8 | -3.29 | -3.69 | -4.26 | -4.73 | -5.23 | -7.51 | -9.32 | -10.25
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Consumer Transformation | Thermal headroom (MW) | 6.36 | 5.56 | 4.77 | 3.88 | 3.21 | 2.2 | 1.2 | 0.15 | -1.06 | -2.56 | -8.15 | -13.78 | -19.43 | -24.92 | -30.83 | -43.77 | -69.45 | -89.77
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Leading the Way | Thermal headroom (MW) | 6.36 | 5.22 | 4 | 2.66 | 1.28 | -0.15 | -1.59 | -3.53 | -7.44 | -11.71 | -13.95 | -17.05 | -20.91 | -24.79 | -28.38 | -33.92 | -37.03 | -39.38
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Steady Progression | Thermal headroom (MW) | 6.36 | 5.94 | 5.5 | 5.03 | 4.85 | 4.54 | 4.18 | 3.76 | 3.33 | 0.94 | -2 | -2.6 | -3.34 | -4.69 | -5.44 | -10.07 | -12.59 | -12.75
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | System Transformation | Thermal headroom (MW) | 6.36 | 5.55 | 4.77 | 3.91 | 3.35 | 2.85 | 2.21 | 1.45 | 0.5 | -0.26 | -2.86 | -3.69 | -6.14 | -7.44 | -9.87 | -17.15 | -22.32 | -25.07
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | WPD Best View | Thermal headroom (MW) | 6.36 | 5.55 | 4.77 | 3.91 | 3.35 | 2.85 | 2.21 | 1.45 | 0.5 | -0.26 | -2.86 | -3.69 | -6.14 | -7.44 | -9.87 | -17.15 | -22.32 | -25.07
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Consumer Transformation | Thermal headroom (MW) | -0.23 | -0.2 | -0.18 | -0.18 | -0.21 | -0.31 | -0.42 | -0.53 | -0.64 | -0.78 | -1.13 | -1.48 | -1.84 | -2.19 | -2.54 | -4.14 | -4.65 | -4.83
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Leading the Way | Thermal headroom (MW) | -0.23 | -0.22 | -0.21 | -0.22 | -0.29 | -0.44 | -0.6 | -0.83 | -1.06 | -1.42 | -1.69 | -2 | -2.31 | -2.57 | -2.8 | -3.73 | -3.97 | -3.93
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Steady Progression | Thermal headroom (MW) | -0.23 | -0.19 | -0.17 | -0.16 | -0.15 | -0.21 | -0.27 | -0.33 | -0.41 | -0.5 | -0.63 | -0.78 | -0.92 | -1.13 | -1.35 | -3.15 | -4.05 | -4.29
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | System Transformation | Thermal headroom (MW) | -0.23 | -0.2 | -0.19 | -0.19 | -0.21 | -0.22 | -0.23 | -0.26 | -0.3 | -0.35 | -0.46 | -0.57 | -0.69 | -0.8 | -0.94 | -2.58 | -3.74 | -3.91
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | WPD Best View | Thermal headroom (MW) | -0.23 | -0.2 | -0.19 | -0.19 | -0.21 | -0.22 | -0.23 | -0.26 | -0.3 | -0.35 | -0.46 | -0.57 | -0.69 | -0.8 | -0.94 | -2.58 | -3.74 | -3.91
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Consumer Transformation | Thermal headroom (MW) | 6.09 | 5.49 | 4.6 | 3.6 | 2.01 | 0.23 | -1.6 | -3.49 | -5.84 | -8.38 | -14.04 | -19.63 | -25.31 | -30.82 | -36.25 | -60.13 | -78.05 | -87.98
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Leading the Way | Thermal headroom (MW) | 6.09 | 5.34 | 3.45 | 1.88 | -0.69 | -4.03 | -7.15 | -11.26 | -17.68 | -24.6 | -30.07 | -36.3 | -43.15 | -50 | -56.44 | -78.34 | -92.54 | -103.84
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Steady Progression | Thermal headroom (MW) | 6.09 | 6.43 | 6.22 | 6.04 | 5.54 | 4.84 | 4.17 | 3.42 | 2.56 | 0.36 | -2.53 | -3.95 | -5.58 | -7.97 | -9.96 | -24.38 | -32.96 | -36.62
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | System Transformation | Thermal headroom (MW) | 6.09 | 6.16 | 5.62 | 5.08 | 4.13 | 3.36 | 2.56 | 1.58 | 0.26 | -1.12 | -3.78 | -5.88 | -8.47 | -10.65 | -13.21 | -30.1 | -38.73 | -41.91
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | WPD Best View | Thermal headroom (MW) | 6.09 | 6.16 | 5.62 | 5.08 | 4.13 | 3.36 | 2.56 | 1.58 | 0.26 | -1.12 | -3.78 | -5.88 | -8.47 | -10.65 | -13.21 | -30.1 | -38.73 | -41.91
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Consumer Transformation | Thermal headroom (MW) | 0.62 | 0.32 | -0.04 | -0.58 | -1.41 | -2.23 | -2.81 | -3.41 | -4.02 | -4.68 | -5.62 | -6.63 | -7.74 | -8.87 | -9.8 | -14.64 | -17.14 | -18.15
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Leading the Way | Thermal headroom (MW) | 0.62 | 0.21 | -0.25 | -0.89 | -1.9 | -3.05 | -3.94 | -4.84 | -5.73 | -6.78 | -7.97 | -9.22 | -10.45 | -11.62 | -12.49 | -15.63 | -16.58 | -16.87
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Steady Progression | Thermal headroom (MW) | 0.62 | 0.53 | 0.41 | 0.23 | -0.16 | -0.54 | -0.83 | -1.14 | -1.49 | -1.88 | -2.38 | -2.9 | -3.52 | -4.14 | -4.64 | -7.39 | -8.52 | -8.83
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | System Transformation | Thermal headroom (MW) | 0.62 | 0.46 | 0.27 | 0.01 | -0.52 | -0.94 | -1.26 | -1.65 | -2.09 | -2.56 | -3.14 | -3.74 | -4.36 | -5 | -5.47 | -8.38 | -9.31 | -9.5
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | WPD Best View | Thermal headroom (MW) | 0.62 | 0.46 | 0.27 | 0.01 | -0.52 | -0.94 | -1.26 | -1.65 | -2.09 | -2.56 | -3.14 | -3.74 | -4.36 | -5 | -5.47 | -8.38 | -9.31 | -9.5
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Consumer Transformation | Thermal headroom (MW) | 12.49 | 12.34 | 11.83 | 11.14 | 10.23 | 8.35 | 6.49 | 4.62 | 2.74 | 0.72 | -6.84 | -15.44 | -24.06 | -32.59 | -41.59 | -71.88 | -110.51 | -137.57
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Leading the Way | Thermal headroom (MW) | 12.49 | 11.64 | 10.3 | 8.75 | 6.25 | 2.93 | -0.26 | -3.89 | -9.27 | -15.45 | -20.65 | -26.81 | -33.81 | -40.93 | -47.72 | -64.3 | -73.65 | -79.67
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Steady Progression | Thermal headroom (MW) | 12.49 | 12.96 | 13.08 | 13.16 | 13.17 | 12.72 | 12.2 | 11.58 | 10.77 | 7.99 | 4.33 | 3.02 | 1.55 | -0.54 | -2 | -11.06 | -19.04 | -23.29
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | System Transformation | Thermal headroom (MW) | 12.49 | 12.45 | 12.14 | 11.67 | 11.06 | 10.37 | 9.44 | 8.14 | 6.57 | 5.24 | 1.77 | -0.29 | -3.89 | -6.22 | -9.62 | -21.94 | -32.54 | -38.5
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | WPD Best View | Thermal headroom (MW) | 12.49 | 11.64 | 10.31 | 8.76 | 6.26 | 2.95 | -0.23 | -3.86 | -9.23 | -15.41 | -20.61 | -26.76 | -33.74 | -40.87 | -47.65 | -64.29 | -73.66 | -79.7
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Consumer Transformation | Thermal headroom (MW) | 50.96 | 50.17 | 49.05 | 47.61 | 45.84 | 43.02 | 40.16 | 37.19 | 33.79 | 30.44 | 22.27 | 14.08 | 3.5 | -6.9 | -17.59 | -54 | -97.6 | -127.69
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Leading the Way | Thermal headroom (MW) | 50.96 | 49.69 | 47.18 | 44.81 | 41.6 | 37.67 | 33.65 | 28.38 | 21.1 | 13.72 | 6.83 | -1.25 | -10.2 | -19.13 | -27.45 | -47.28 | -57.28 | -63.17
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Steady Progression | Thermal headroom (MW) | 50.96 | 51.61 | 51.59 | 51.49 | 51.34 | 50.62 | 49.8 | 48.82 | 47.43 | 44.06 | 39.89 | 38.01 | 35.89 | 32.75 | 30.22 | 17.35 | 9.62 | 4.71
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | System Transformation | Thermal headroom (MW) | 50.96 | 50.94 | 50.3 | 49.45 | 48.43 | 47.45 | 46.25 | 44.46 | 42.3 | 40.33 | 36.21 | 33.77 | 29.79 | 27.06 | 23.57 | 10.12 | -0.64 | -5.57
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | WPD Best View | Thermal headroom (MW) | 50.96 | 49.7 | 47.2 | 44.83 | 41.64 | 37.73 | 33.75 | 28.51 | 21.27 | 13.97 | 7.12 | -0.93 | -9.84 | -18.73 | -27.01 | -46.88 | -56.88 | -62.76
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Consumer Transformation | Thermal headroom (MW) | 30.92 | 30.37 | 29.34 | 27.92 | 25.91 | 22.89 | 19.83 | 16.72 | 13.53 | 10.2 | 3.32 | -4.79 | -13.04 | -20.96 | -28.57 | -63.14 | -84.4 | -94.51
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Leading the Way | Thermal headroom (MW) | 30.92 | 29.36 | 27.14 | 24.64 | 21.57 | 17.18 | 12.92 | 7.51 | 1.47 | -5.09 | -13.23 | -21.74 | -30.18 | -38.17 | -45.19 | -65.03 | -70.47 | -70.13
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Steady Progression | Thermal headroom (MW) | 30.92 | 31.65 | 31.86 | 31.96 | 31.96 | 31.21 | 30.33 | 29.01 | 27.46 | 25.71 | 23.47 | 21.12 | 18.58 | 15.88 | 13.1 | -6.38 | -23.02 | -30.14
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | System Transformation | Thermal headroom (MW) | 30.92 | 31.17 | 30.85 | 30.33 | 29.66 | 28.94 | 27.83 | 26.35 | 24.62 | 22.6 | 20.39 | 17.9 | 14.92 | 11.99 | 9.2 | -11.54 | -19.75 | -22.23
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | WPD Best View | Thermal headroom (MW) | 30.92 | 30.17 | 28.78 | 27.17 | 25.23 | 22.43 | 19.59 | 16.38 | 13.18 | 9 | 3.63 | -2.18 | -8.47 | -14.57 | -20.38 | -40.14 | -46.51 | -47.19
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Consumer Transformation | Thermal headroom (MW) | 34.31 | 33.81 | 32.93 | 31.69 | 29.85 | 27.13 | 24.46 | 21.81 | 18.96 | 15.47 | 9.54 | 3.59 | -2.56 | -8.41 | -14.11 | -42.49 | -59.36 | -66.68
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Leading the Way | Thermal headroom (MW) | 34.31 | 32.62 | 30.51 | 28.18 | 25.02 | 20.78 | 16.62 | 12.22 | 7.7 | 2.44 | -3.61 | -10.04 | -16.43 | -22.59 | -27.83 | -45.69 | -52.14 | -53.31
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Steady Progression | Thermal headroom (MW) | 34.31 | 34.78 | 34.87 | 34.85 | 34.62 | 33.67 | 32.68 | 31.63 | 30.46 | 29.17 | 27.45 | 25.62 | 23.55 | 21.35 | 19.04 | 2.89 | -8.19 | -12.7
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | System Transformation | Thermal headroom (MW) | 34.31 | 34.42 | 34.17 | 33.79 | 33.07 | 32.09 | 31.03 | 29.91 | 28.66 | 27.06 | 25.04 | 22.69 | 19.72 | 16.45 | 13.06 | -4.49 | -11.67 | -13.38
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | WPD Best View | Thermal headroom (MW) | 34.31 | 33.96 | 33.3 | 32.4 | 31.04 | 29 | 26.91 | 24.82 | 22.61 | 19.8 | 14.98 | 10.03 | 4.95 | -0.08 | -5 | -29.88 | -43.88 | -49.52
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Consumer Transformation | Thermal headroom (MW) | 35.52 | 35.22 | 34.43 | 33.37 | 31.69 | 29.1 | 26.5 | 23.83 | 21.13 | 18.49 | 13.82 | 7.23 | 0.57 | -5.83 | -12.04 | -45.41 | -67.26 | -77.64
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Leading the Way | Thermal headroom (MW) | 35.52 | 34.36 | 32.6 | 30.67 | 27.61 | 23.29 | 19.18 | 14.56 | 9.29 | 3.89 | -2.78 | -9.84 | -16.81 | -23.52 | -29.76 | -50.07 | -57.69 | -60.25
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Steady Progression | Thermal headroom (MW) | 35.52 | 36.23 | 36.44 | 36.55 | 36.46 | 35.75 | 34.95 | 33.91 | 32.6 | 31.17 | 29.21 | 27.17 | 25 | 22.73 | 20.41 | 6.99 | -4.27 | -9.72
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | System Transformation | Thermal headroom (MW) | 35.52 | 35.87 | 35.68 | 35.37 | 34.74 | 34 | 32.98 | 31.58 | 29.96 | 28.22 | 25.96 | 23.51 | 20.98 | 18.54 | 16.18 | 2.84 | -4.66 | -7.4
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | WPD Best View | Thermal headroom (MW) | 35.52 | 34.45 | 32.79 | 30.94 | 28.16 | 24.01 | 20.09 | 15.85 | 10.99 | 5.81 | -0.84 | -7.82 | -14.73 | -21.41 | -27.63 | -49.47 | -58.74 | -62.25
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Consumer Transformation | Thermal headroom (MW) | 51.21 | 50.47 | 49.79 | 48.88 | 47.51 | 45.49 | 43.22 | 40.89 | 38.75 | 36.15 | 31.45 | 26.06 | 20.56 | 15.21 | 9.99 | -17.13 | -33.99 | -41.78
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Leading the Way | Thermal headroom (MW) | 51.21 | 50.11 | 48.59 | 46.65 | 44.27 | 41.06 | 37.51 | 33.64 | 29.4 | 24.83 | 19.38 | 13.57 | 7.71 | 2.06 | -3.24 | -20.66 | -27.69 | -30.27
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Steady Progression | Thermal headroom (MW) | 51.21 | 51.62 | 51.72 | 51.73 | 51.69 | 51.14 | 50.28 | 49.21 | 48.12 | 46.86 | 45.15 | 43.39 | 41.51 | 39.55 | 37.21 | 24.06 | 13.18 | 8.24
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | System Transformation | Thermal headroom (MW) | 51.21 | 51.37 | 51.15 | 50.85 | 50.43 | 49.81 | 48.7 | 47.35 | 46.07 | 44.59 | 42.24 | 39.74 | 37.22 | 34.62 | 31.96 | 17.45 | 9.67 | 6.79
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | WPD Best View | Thermal headroom (MW) | 51.21 | 50.44 | 49.3 | 48.03 | 46.29 | 43.8 | 41.11 | 38.22 | 35.3 | 31.72 | 26.79 | 21.7 | 16.47 | 11.29 | 6.35 | -13.06 | -22.27 | -25.82
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Consumer Transformation | Thermal headroom (MW) | 32.55 | 31.68 | 30.23 | 28.55 | 26.85 | 23.93 | 20.98 | 18.02 | 15.09 | 12.28 | 7.31 | 0.93 | -5.6 | -11.99 | -18.29 | -49.47 | -70.1 | -80.15
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Leading the Way | Thermal headroom (MW) | 32.55 | 30.62 | 28.02 | 25.13 | 21.9 | 17.45 | 13.21 | 8.6 | 4.01 | -1.27 | -7.72 | -14.46 | -21.21 | -27.78 | -33.97 | -54.29 | -62.79 | -66.17
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Steady Progression | Thermal headroom (MW) | 32.55 | 32.75 | 32.39 | 32 | 31.83 | 30.93 | 29.92 | 28.73 | 27.31 | 25.81 | 23.71 | 21.55 | 19.28 | 16.92 | 14.54 | 1.42 | -9.42 | -14.38
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | System Transformation | Thermal headroom (MW) | 32.55 | 32.34 | 31.53 | 30.65 | 29.96 | 29.13 | 28.05 | 26.59 | 24.93 | 23.12 | 20.68 | 18.05 | 15.37 | 12.8 | 10.24 | -2.12 | -9.71 | -12.75
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | WPD Best View | Thermal headroom (MW) | 32.55 | 30.74 | 28.25 | 25.63 | 22.6 | 18.47 | 14.58 | 10.36 | 6.21 | 1.65 | -4.49 | -10.89 | -17.32 | -23.73 | -29.74 | -49.71 | -58.13 | -61.56
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Consumer Transformation | Thermal headroom (MW) | 15.07 | 14.77 | 14.21 | 13.54 | 12.78 | 11.68 | 10.44 | 9.16 | 7.89 | 6.58 | 4.03 | 0.53 | -2.99 | -6.37 | -9.72 | -26.46 | -35.91 | -39.93
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Leading the Way | Thermal headroom (MW) | 15.07 | 14.42 | 13.44 | 12.4 | 11.25 | 9.27 | 7.3 | 5.15 | 2.65 | -0.15 | -3.6 | -7.25 | -10.91 | -14.45 | -17.37 | -27.19 | -30.76 | -31.16
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Steady Progression | Thermal headroom (MW) | 15.07 | 15.22 | 15.09 | 14.94 | 14.85 | 14.49 | 14.05 | 13.54 | 12.95 | 12.23 | 11.29 | 10.3 | 9.25 | 8.13 | 6.98 | -1.25 | -8.03 | -10.75
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | System Transformation | Thermal headroom (MW) | 15.07 | 15.07 | 14.78 | 14.45 | 14.16 | 13.81 | 13.37 | 12.73 | 11.96 | 11.12 | 9.99 | 8.76 | 7.11 | 5.48 | 3.97 | -5.21 | -9.88 | -10.87
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | WPD Best View | Thermal headroom (MW) | 15.07 | 14.82 | 14.25 | 13.63 | 13.07 | 12.31 | 11.45 | 10.34 | 9.18 | 8.01 | 6.63 | 5 | 2.58 | 0.11 | -2.32 | -11.56 | -15.24 | -15.59
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Consumer Transformation | Thermal headroom (MW) | 8.66 | 8.02 | 7.03 | 5.92 | 5.05 | 3.56 | 2.31 | 1.04 | -0.36 | -1.79 | -5.01 | -8.24 | -11.42 | -14.56 | -17.6 | -31.89 | -41.34 | -45.59
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Leading the Way | Thermal headroom (MW) | 8.66 | 7.23 | 5.39 | 3.5 | 1.96 | -0.14 | -2.1 | -4.2 | -6.37 | -8.68 | -11.87 | -15.25 | -18.56 | -21.82 | -24.9 | -33.52 | -36.43 | -36.87
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Steady Progression | Thermal headroom (MW) | 8.66 | 8.71 | 8.39 | 8.08 | 7.99 | 7.51 | 7.07 | 6.63 | 6.13 | 5.58 | 4.77 | 3.98 | 3.15 | 2.25 | 1.31 | -6.47 | -12.12 | -14.55
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | System Transformation | Thermal headroom (MW) | 8.66 | 8.41 | 7.82 | 7.22 | 6.86 | 6.44 | 5.99 | 5.52 | 4.97 | 4.4 | 3.64 | 2.37 | 1.02 | -0.45 | -1.93 | -9.67 | -12.71 | -13.72
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | WPD Best View | Thermal headroom (MW) | 8.66 | 7.23 | 5.39 | 3.5 | 1.96 | -0.14 | -2.1 | -4.2 | -6.37 | -8.68 | -11.87 | -15.25 | -18.56 | -21.82 | -24.9 | -33.52 | -36.43 | -36.87
Kitwell 132kV | Shirley 132 11 (GT2) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Consumer Transformation | Thermal headroom (MW) | 33.61 | 32.62 | 31.6 | 30.42 | 28.68 | 24.74 | 20.92 | 17.42 | 13.65 | 8.84 | -0.54 | -9.6 | -18.59 | -27.17 | -35.93 | -72.46 | -107.01 | -129.2
Kitwell 132kV | Shirley 132 11 (GT2) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Leading the Way | Thermal headroom (MW) | 33.61 | 31.8 | 29.21 | 26.99 | 24.06 | 18.15 | 12.38 | 6.73 | 0.1 | -7.9 | -15.52 | -23.22 | -30.92 | -38.03 | -44.3 | -65.21 | -74.33 | -78.36
Kitwell 132kV | Shirley 132 11 (GT2) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Steady Progression | Thermal headroom (MW) | 33.61 | 33.89 | 33.82 | 33.71 | 33.47 | 31.87 | 30.41 | 29.09 | 27.63 | 24.84 | 20.82 | 18.21 | 15.42 | 12.21 | 9.27 | -9.46 | -20.49 | -24.82
Kitwell 132kV | Shirley 132 11 (GT2) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | System Transformation | Thermal headroom (MW) | 33.61 | 33.64 | 33.23 | 32.82 | 32.13 | 30.62 | 29.04 | 27.76 | 25.9 | 23.4 | 20.45 | 17.43 | 13.94 | 10.37 | 6.71 | -13.49 | -22.12 | -24.18
Kitwell 132kV | Shirley 132 11 (GT2) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | WPD Best View | Thermal headroom (MW) | 33.61 | 32.67 | 31.65 | 30.52 | 28.87 | 25.13 | 21.53 | 18.24 | 14.7 | 10.13 | 1.05 | -7.79 | -16.55 | -24.89 | -33.38 | -69.09 | -104.09 | -126.37
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Consumer Transformation | Thermal headroom (MW) | 42.45 | 42.14 | 41.43 | 40.53 | 39.31 | 37.18 | 35.06 | 32.88 | 30.68 | 27.63 | 21.73 | 15.8 | 9.76 | 3.9 | -1.79 | -28.59 | -46.22 | -54.3
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Leading the Way | Thermal headroom (MW) | 42.45 | 41.44 | 39.97 | 38.12 | 35.69 | 32.33 | 28.81 | 24.63 | 20.33 | 15.7 | 9.76 | 3.52 | -2.72 | -8.73 | -14.03 | -31.7 | -38.78 | -40.69
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Steady Progression | Thermal headroom (MW) | 42.45 | 42.87 | 42.93 | 42.92 | 42.82 | 42.24 | 41.59 | 40.74 | 39.72 | 38.58 | 36.97 | 35.28 | 33.48 | 31.57 | 29.63 | 14.5 | 2.51 | -3.04
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | System Transformation | Thermal headroom (MW) | 42.45 | 42.62 | 42.39 | 42.06 | 41.59 | 41 | 40.2 | 39.13 | 37.88 | 36.46 | 34.39 | 32.16 | 29.49 | 26.87 | 24.13 | 9.09 | 1.59 | -1.37
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | WPD Best View | Thermal headroom (MW) | 42.45 | 41.55 | 40.22 | 38.68 | 36.43 | 33.29 | 30.27 | 26.4 | 22.38 | 18.06 | 12.14 | 5.96 | -0.23 | -6.17 | -11.43 | -30.37 | -39.18 | -41.73
Lea Marston 132kV | Castle Bromwich 132 11 (GT2A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Consumer Transformation | Thermal headroom (MW) | 25.29 | 25.49 | 25.33 | 25.12 | 24.81 | 24.39 | 23.98 | 23.56 | 23.12 | 22.64 | 21.69 | 20.87 | 19.85 | 18.68 | 17.13 | 8.91 | 4.15 | 2.4
Lea Marston 132kV | Castle Bromwich 132 11 (GT2A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Leading the Way | Thermal headroom (MW) | 25.29 | 25.23 | 24.79 | 24.32 | 23.73 | 23.03 | 22.35 | 21.59 | 20.76 | 19.87 | 18.8 | 17.66 | 15.95 | 14.3 | 12.75 | 7.71 | 6.26 | 6.54
Lea Marston 132kV | Castle Bromwich 132 11 (GT2A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Steady Progression | Thermal headroom (MW) | 25.29 | 25.74 | 25.83 | 25.92 | 26.04 | 26.02 | 25.97 | 25.91 | 25.82 | 25.74 | 25.54 | 25.32 | 25.07 | 24.71 | 24.34 | 22 | 20.35 | 19.24
Lea Marston 132kV | Castle Bromwich 132 11 (GT2A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | System Transformation | Thermal headroom (MW) | 25.29 | 25.63 | 25.62 | 25.58 | 25.54 | 25.51 | 25.46 | 25.36 | 25.2 | 25.06 | 24.76 | 24.28 | 23.78 | 23.31 | 22.9 | 21.21 | 19.77 | 19.83
Lea Marston 132kV | Castle Bromwich 132 11 (GT2A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | WPD Best View | Thermal headroom (MW) | 25.29 | 25.23 | 24.79 | 24.32 | 23.73 | 23.03 | 22.35 | 21.6 | 20.77 | 19.88 | 18.81 | 17.67 | 15.96 | 14.31 | 12.76 | 7.7 | 6.25 | 6.52
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Consumer Transformation | Thermal headroom (MW) | 18.64 | 18.51 | 18.23 | 17.83 | 17.23 | 16.1 | 15.12 | 13.58 | 12.48 | 11.24 | 8.78 | 6.32 | 3.84 | 1.51 | -0.73 | -10.68 | -15.97 | -18.23
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Leading the Way | Thermal headroom (MW) | 18.64 | 17.98 | 17.11 | 16.18 | 15.07 | 13.39 | 11.86 | 9.31 | 7.53 | 5.65 | 3.21 | 0.69 | -1.82 | -4.19 | -6.36 | -11.19 | -11.85 | -10.78
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Steady Progression | Thermal headroom (MW) | 18.64 | 18.97 | 19.06 | 19.12 | 19.13 | 18.83 | 18.55 | 17.95 | 17.48 | 16.99 | 16.3 | 15.61 | 14.86 | 14.08 | 13.25 | 7.45 | 3.3 | 1.99
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | System Transformation | Thermal headroom (MW) | 18.64 | 18.8 | 18.75 | 18.65 | 18.47 | 18.19 | 17.91 | 16.98 | 16.49 | 15.92 | 15.13 | 14.29 | 13.31 | 12.28 | 11.16 | 5.86 | 4.36 | 4.51
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | WPD Best View | Thermal headroom (MW) | 18.64 | 18.51 | 18.23 | 17.82 | 17.22 | 16.08 | 15.1 | 13.55 | 12.44 | 11.2 | 8.74 | 6.28 | 3.8 | 1.47 | -0.76 | -10.69 | -15.94 | -18.18
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Consumer Transformation | Thermal headroom (MW) | 53.44 | 53.51 | 53.27 | 52.9 | 52.27 | 51.42 | 50.5 | 49.35 | 48.07 | 46.66 | 44.84 | 43.3 | 40.94 | 38.36 | 35.85 | 22.52 | 15.41 | 12.45
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Leading the Way | Thermal headroom (MW) | 53.44 | 53.32 | 52.82 | 52.23 | 51.32 | 49.91 | 48.42 | 46.4 | 44.2 | 41.86 | 39 | 35.9 | 32.98 | 30.14 | 27.52 | 19.24 | 15.94 | 14.78
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Steady Progression | Thermal headroom (MW) | 53.44 | 53.88 | 53.99 | 54.06 | 54.05 | 53.76 | 53.41 | 52.93 | 52.23 | 51.34 | 50.28 | 49.31 | 48.29 | 47.19 | 46.13 | 40.27 | 37.43 | 35.69
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | System Transformation | Thermal headroom (MW) | 53.44 | 53.77 | 53.75 | 53.68 | 53.48 | 53.27 | 52.92 | 52.27 | 51.46 | 50.53 | 49.42 | 48.12 | 46.76 | 45.54 | 44.32 | 38.21 | 33.88 | 32.29
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | WPD Best View | Thermal headroom (MW) | 53.44 | 53.51 | 53.27 | 52.9 | 52.27 | 51.42 | 50.5 | 49.35 | 48.07 | 46.66 | 44.84 | 43.3 | 40.94 | 38.36 | 35.85 | 22.52 | 15.41 | 12.45
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Consumer Transformation | Thermal headroom (MW) | 58.83 | 59.63 | 59.8 | 59.8 | 59.49 | 58.86 | 57.8 | 56.65 | 55.11 | 53.46 | 51.03 | 48.67 | 46.39 | 44.48 | 42.67 | 36.65 | 35.66 | 36.75
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Leading the Way | Thermal headroom (MW) | 58.83 | 59.46 | 59.42 | 59.25 | 58.67 | 57.67 | 56.26 | 54.45 | 52.04 | 49.75 | 47.07 | 44.42 | 42.04 | 40.14 | 38.59 | 36.12 | 37.45 | 40.55
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Steady Progression | Thermal headroom (MW) | 58.83 | 59.86 | 60.29 | 60.71 | 61 | 61.1 | 61.06 | 60.97 | 60.7 | 60.41 | 60.02 | 59.56 | 58.96 | 58.28 | 57.6 | 52.17 | 49.19 | 49.23
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | System Transformation | Thermal headroom (MW) | 58.83 | 59.78 | 60.12 | 60.41 | 60.52 | 60.63 | 60.34 | 60.03 | 59.35 | 58.74 | 57.95 | 56.73 | 55.44 | 54.08 | 52.66 | 46.04 | 45.04 | 46.74
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | WPD Best View | Thermal headroom (MW) | 58.83 | 59.63 | 59.8 | 59.8 | 59.49 | 58.86 | 57.8 | 56.65 | 55.11 | 53.46 | 51.03 | 48.67 | 46.39 | 44.48 | 42.67 | 36.65 | 35.66 | 36.75
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Consumer Transformation | Thermal headroom (MW) | 39.52 | 38.29 | 36.57 | 35.4 | 34.49 | 33.28 | 32.25 | 31.43 | 30.49 | 29.38 | 27.67 | 25.94 | 24.2 | 22.55 | 20.96 | 12.48 | 8.12 | 6.14
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Leading the Way | Thermal headroom (MW) | 39.52 | 37.73 | 35.47 | 33.8 | 32.52 | 30.83 | 29.36 | 28.04 | 26.63 | 25.05 | 23.31 | 21.5 | 19.66 | 17.91 | 16.32 | 11.5 | 10.25 | 10.3
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Steady Progression | Thermal headroom (MW) | 39.52 | 38.76 | 37.46 | 36.71 | 36.25 | 35.59 | 35.02 | 34.64 | 34.28 | 33.96 | 33.5 | 33 | 32.52 | 31.99 | 31.43 | 26.71 | 24.34 | 24.48
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | System Transformation | Thermal headroom (MW) | 39.52 | 38.42 | 36.8 | 35.8 | 35.06 | 34.58 | 34.22 | 33.94 | 33.48 | 33.12 | 32.59 | 31.99 | 31.24 | 30.42 | 29.46 | 24.42 | 22.47 | 22.53
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | WPD Best View | Thermal headroom (MW) | 39.52 | 38.29 | 36.57 | 35.4 | 34.48 | 33.26 | 32.22 | 31.4 | 30.44 | 29.33 | 27.6 | 25.91 | 24.15 | 22.48 | 20.89 | 12.46 | 8.14 | 6.2
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Consumer Transformation | Thermal headroom (MW) | 107.47 | 106.38 | 105.47 | 104.32 | 102.79 | 99.6 | 96.5 | 93.38 | 89.84 | 85.84 | 76.98 | 67.45 | 57.93 | 48.53 | 39.21 | -5.12 | -40.39 | -59.27
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Leading the Way | Thermal headroom (MW) | 107.47 | 105.82 | 103.21 | 100.33 | 96.68 | 91.28 | 86.18 | 79.56 | 71.97 | 64.05 | 55.09 | 45.52 | 35.68 | 26.04 | 16.8 | -12.25 | -26.85 | -34.37
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Steady Progression | Thermal headroom (MW) | 107.47 | 108.17 | 108.34 | 108.42 | 108.43 | 107.58 | 106.64 | 105.57 | 104.18 | 102.66 | 100.32 | 97.93 | 95.4 | 92.41 | 89.03 | 70.62 | 53.79 | 45.37
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | System Transformation | Thermal headroom (MW) | 107.47 | 107.77 | 107.49 | 107.07 | 106.5 | 105.63 | 104.52 | 103.02 | 101.25 | 99.29 | 95.5 | 91.48 | 87.41 | 83.47 | 79.32 | 58.41 | 46.81 | 42.29
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | WPD Best View | Thermal headroom (MW) | 107.47 | 105.87 | 104.04 | 101.97 | 98.85 | 94.13 | 89.73 | 85.02 | 78.34 | 71.33 | 62.39 | 53.01 | 43.33 | 33.84 | 24.68 | -9.69 | -29.69 | -40.03
Lea Marston 132kV | Solihull 132 11 (GT1A) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Consumer Transformation | Thermal headroom (MW) | -0.69 | -1.01 | -1.43 | -2.12 | -3.34 | -5.02 | -6.83 | -8.89 | -11.44 | -13.97 | -16.88 | -19.35 | -22.67 | -26.84 | -30.84 | -52.02 | -64.27 | -69.6
Lea Marston 132kV | Solihull 132 11 (GT1A) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Leading the Way | Thermal headroom (MW) | -0.69 | -1.05 | -2.32 | -3.46 | -5.15 | -7.65 | -10.2 | -13.73 | -17.39 | -20.99 | -25.55 | -30.54 | -35.17 | -39.63 | -43.64 | -55.81 | -60.11 | -61.32
Lea Marston 132kV | Solihull 132 11 (GT1A) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Steady Progression | Thermal headroom (MW) | -0.69 | 0.07 | 0.35 | 0.51 | 0.51 | 0.08 | -0.46 | -1.22 | -2.26 | -3.43 | -4.87 | -6.38 | -7.98 | -10 | -12.04 | -21.2 | -24.98 | -27.97
Lea Marston 132kV | Solihull 132 11 (GT1A) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | System Transformation | Thermal headroom (MW) | -0.69 | -0.12 | -0.08 | -0.18 | -0.52 | -0.92 | -1.57 | -2.63 | -3.9 | -5.3 | -7.19 | -9.15 | -11.06 | -12.9 | -14.56 | -22.29 | -27.14 | -28.59
Lea Marston 132kV | Solihull 132 11 (GT1A) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | WPD Best View | Thermal headroom (MW) | -0.69 | -1.01 | -1.43 | -2.13 | -3.34 | -5.02 | -6.83 | -8.9 | -11.46 | -14 | -16.91 | -19.39 | -22.77 | -26.94 | -30.91 | -51.94 | -64.05 | -69.24
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Consumer Transformation | Thermal headroom (MW) | 38.1 | 37.22 | 36.16 | 34.68 | 32.21 | 29.38 | 25.99 | 22.44 | 18.78 | 15.34 | 9.63 | 3.64 | -4.24 | -11.86 | -19.74 | -57.31 | -91.84 | -113.33
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Leading the Way | Thermal headroom (MW) | 38.1 | 36.94 | 34.73 | 32.55 | 29.23 | 24.68 | 19.86 | 14.43 | 8.45 | 2.23 | -4.11 | -10.98 | -18.14 | -25.23 | -31.88 | -54.63 | -64.95 | -71.07
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Steady Progression | Thermal headroom (MW) | 38.1 | 38.6 | 38.55 | 38.36 | 37.99 | 37.03 | 35.86 | 34.35 | 32.64 | 30.03 | 26.83 | 24.55 | 21.7 | 18.48 | 15.51 | 0.62 | -6.39 | -11.04
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | System Transformation | Thermal headroom (MW) | 38.1 | 38.31 | 37.91 | 37.35 | 36.49 | 35.51 | 34.08 | 32.34 | 30.31 | 28.23 | 25.63 | 22.83 | 19.97 | 17.17 | 14.14 | 0.64 | -7.1 | -10.12
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | WPD Best View | Thermal headroom (MW) | 38.1 | 36.96 | 34.76 | 32.6 | 29.29 | 24.76 | 19.96 | 14.54 | 8.58 | 2.41 | -3.9 | -10.74 | -17.86 | -24.92 | -31.48 | -54.22 | -64.6 | -70.75
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Consumer Transformation | Thermal headroom (MW) | 50.93 | 50.66 | 50.17 | 49.55 | 48.25 | 46.82 | 45.29 | 43.54 | 41.54 | 39.67 | 37.27 | 34.76 | 32.27 | 29.88 | 27.63 | 19.77 | 17.47 | 17.02
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Leading the Way | Thermal headroom (MW) | 50.93 | 50.41 | 49.67 | 48.78 | 47.05 | 45.3 | 43.48 | 41.18 | 38.56 | 36.32 | 33.85 | 31.17 | 28.58 | 26.22 | 24.22 | 19.65 | 20.17 | 22.51
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Steady Progression | Thermal headroom (MW) | 50.93 | 51.06 | 51.01 | 50.9 | 50.52 | 50.11 | 49.67 | 49.16 | 48.59 | 48.03 | 47.32 | 46.49 | 45.57 | 44.58 | 43.45 | 36.2 | 31.4 | 30.46
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | System Transformation | Thermal headroom (MW) | 50.93 | 50.94 | 50.77 | 50.58 | 49.89 | 49.36 | 48.71 | 47.85 | 46.77 | 45.94 | 44.88 | 43.64 | 42.2 | 40.58 | 38.85 | 30.68 | 28.87 | 29.77
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | WPD Best View | Thermal headroom (MW) | 50.93 | 50.41 | 49.67 | 48.78 | 47.05 | 45.3 | 43.48 | 41.18 | 38.56 | 36.32 | 33.85 | 31.17 | 28.58 | 26.22 | 24.22 | 19.65 | 20.17 | 22.51
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Consumer Transformation | Thermal headroom (MW) | 19.99 | 19.28 | 18.11 | 16.72 | 14.45 | 12.05 | 9.74 | 7.24 | 4.45 | 2 | -1.79 | -5.55 | -9.33 | -12.89 | -16.21 | -26.44 | -28.81 | -28.59
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Leading the Way | Thermal headroom (MW) | 19.99 | 18.76 | 17.02 | 15.08 | 12.19 | 9.39 | 6.73 | 3.53 | 0.03 | -2.92 | -6.52 | -10.31 | -13.97 | -17.26 | -19.71 | -23.92 | -21.5 | -16.86
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Steady Progression | Thermal headroom (MW) | 19.99 | 20.05 | 19.73 | 19.37 | 18.56 | 17.68 | 16.88 | 15.97 | 14.95 | 14.13 | 13 | 11.78 | 10.47 | 9.07 | 7.62 | -2.16 | -7.19 | -6.85
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | System Transformation | Thermal headroom (MW) | 19.99 | 19.76 | 19.08 | 18.39 | 17.07 | 16.12 | 15.15 | 13.99 | 12.64 | 11.57 | 10.23 | 8.74 | 6.64 | 4.32 | 1.98 | -7.19 | -7.32 | -4.85
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | WPD Best View | Thermal headroom (MW) | 19.99 | 18.76 | 17.02 | 15.08 | 12.19 | 9.39 | 6.73 | 3.53 | 0.03 | -2.92 | -6.52 | -10.31 | -13.97 | -17.26 | -19.71 | -23.92 | -21.5 | -16.86
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Consumer Transformation | Thermal headroom (MW) | 40.88 | 40.69 | 40.2 | 39.59 | 38.65 | 37.05 | 35.45 | 33.73 | 31.89 | 29.82 | 26.35 | 22.86 | 19.32 | 15.92 | 12.65 | -0.79 | -6.54 | -9.07
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Leading the Way | Thermal headroom (MW) | 40.88 | 40.03 | 38.85 | 37.63 | 36.01 | 33.91 | 31.86 | 29.45 | 26.87 | 24.1 | 20.68 | 17.03 | 13.47 | 10.08 | 7 | 0.1 | -0.33 | 1.91
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Steady Progression | Thermal headroom (MW) | 40.88 | 41.26 | 41.35 | 41.4 | 41.38 | 40.99 | 40.58 | 40.11 | 39.5 | 38.84 | 37.96 | 36.97 | 35.89 | 34.65 | 33.29 | 23.31 | 15.34 | 12.52
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | System Transformation | Thermal headroom (MW) | 40.88 | 41.03 | 40.83 | 40.59 | 40.22 | 39.74 | 39.3 | 38.57 | 37.7 | 36.83 | 35.64 | 34.26 | 32.62 | 30.81 | 28.85 | 18.91 | 15.66 | 15.92
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | WPD Best View | Thermal headroom (MW) | 40.88 | 40.03 | 38.85 | 37.63 | 36.01 | 33.91 | 31.86 | 29.45 | 26.87 | 24.1 | 20.68 | 17.03 | 13.47 | 10.08 | 7 | 0.1 | -0.33 | 1.91
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Consumer Transformation | Thermal headroom (MW) | 39.31 | 39.37 | 39 | 38.48 | 37.63 | 36.43 | 35.08 | 33.47 | 31.82 | 30.36 | 26.86 | 22.21 | 17.53 | 12.98 | 8.54 | -13.25 | -28.47 | -35.65
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Leading the Way | Thermal headroom (MW) | 39.31 | 38.74 | 37.69 | 36.57 | 35 | 32.52 | 30.16 | 27.24 | 23.56 | 19.97 | 15.4 | 10.58 | 5.72 | 0.96 | -3.5 | -16.71 | -21.74 | -23.48
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Steady Progression | Thermal headroom (MW) | 39.31 | 40.01 | 40.28 | 40.5 | 40.58 | 40.3 | 39.98 | 39.48 | 38.87 | 38.22 | 37.12 | 35.98 | 34.78 | 33.52 | 32.24 | 23.05 | 15.49 | 12.38
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | System Transformation | Thermal headroom (MW) | 39.31 | 39.77 | 39.77 | 39.7 | 39.41 | 39.12 | 38.76 | 38.04 | 37.05 | 36.17 | 34.89 | 33.13 | 31.35 | 29.61 | 28.02 | 18.11 | 13.3 | 11.38
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | WPD Best View | Thermal headroom (MW) | 39.31 | 38.74 | 37.69 | 36.57 | 35 | 32.52 | 30.16 | 27.24 | 23.56 | 19.97 | 15.4 | 10.58 | 5.72 | 0.96 | -3.5 | -16.71 | -21.74 | -23.48
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Consumer Transformation | Thermal headroom (MW) | 30.88 | 29.76 | 28.59 | 27 | 24.82 | 22.42 | 19.79 | 16.58 | 12.49 | 7.73 | 1.93 | -4.14 | -10.16 | -15.72 | -20.81 | -34.75 | -37.36 | -36.52
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Leading the Way | Thermal headroom (MW) | 30.88 | 29.69 | 27.63 | 25.56 | 22.72 | 20.01 | 16.99 | 12.66 | 7.65 | 2.2 | -3.65 | -9.89 | -15.96 | -21.4 | -25.93 | -32.61 | -28.29 | -19.36
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Steady Progression | Thermal headroom (MW) | 30.88 | 31.03 | 30.8 | 30.46 | 29.93 | 29.28 | 28.46 | 27.39 | 26.1 | 24.58 | 22.62 | 20.4 | 17.86 | 14.56 | 10.92 | -11.59 | -28.3 | -32.51
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | System Transformation | Thermal headroom (MW) | 30.88 | 30.79 | 30.25 | 29.6 | 28.59 | 27.73 | 26.68 | 25.19 | 23.27 | 21.02 | 17.83 | 14.05 | 9.65 | 4.71 | -0.66 | -25.43 | -31.13 | -28.26
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | WPD Best View | Thermal headroom (MW) | 30.88 | 29.69 | 27.63 | 25.56 | 22.72 | 20.01 | 16.99 | 12.66 | 7.65 | 2.2 | -3.65 | -9.89 | -15.96 | -21.4 | -25.93 | -32.61 | -28.29 | -19.36
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Consumer Transformation | Thermal headroom (MW) | 96.33 | 95.61 | 94.81 | 93.8 | 91.74 | 88.05 | 84.55 | 80.87 | 76.93 | 72.77 | 63.41 | 54.02 | 44.58 | 35.37 | 26.03 | -6.98 | -40.25 | -62.81
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Leading the Way | Thermal headroom (MW) | 96.33 | 94.84 | 92.49 | 90.41 | 86.82 | 82.1 | 77.58 | 72.46 | 66.34 | 60.08 | 53.04 | 45.35 | 37.4 | 29.72 | 22.92 | 5.1 | -2.1 | -3.74
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Steady Progression | Thermal headroom (MW) | 96.33 | 97.06 | 97.26 | 97.39 | 96.95 | 95.97 | 95.03 | 93.96 | 92.75 | 90.47 | 87.15 | 85.14 | 82.9 | 80.17 | 77.65 | 59.78 | 45.48 | 39.7
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | System Transformation | Thermal headroom (MW) | 96.33 | 96.64 | 96.39 | 96.05 | 94.96 | 93.94 | 92.88 | 91.49 | 89.45 | 87.62 | 85.28 | 82.63 | 79.36 | 75.82 | 72.14 | 54.07 | 47.1 | 46.35
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | WPD Best View | Thermal headroom (MW) | 96.33 | 94.84 | 92.49 | 90.41 | 86.82 | 82.1 | 77.58 | 72.46 | 66.34 | 60.08 | 53.04 | 45.35 | 37.4 | 29.72 | 22.92 | 5.1 | -2.1 | -3.74
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Consumer Transformation | Thermal headroom (MW) | 22.75 | 22.22 | 21.13 | 19.81 | 18 | 15.09 | 12.31 | 8.06 | 3.23 | -2.29 | -14.47 | -26.78 | -39.46 | -51.37 | -63.37 | -103.56 | -144.36 | -173.55
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Leading the Way | Thermal headroom (MW) | 22.75 | 21.25 | 19.13 | 16.89 | 13.82 | 10.36 | 5.47 | -0.64 | -8.2 | -16.41 | -25.27 | -35.34 | -45.46 | -55.16 | -64.09 | -84.24 | -90.87 | -91.18
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Steady Progression | Thermal headroom (MW) | 22.75 | 23.53 | 23.69 | 23.8 | 23.78 | 23.16 | 22.46 | 21.66 | 20.78 | 18.27 | 14.7 | 12.8 | 10.14 | 6.46 | 3.06 | -21.85 | -41.32 | -49.28
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | System Transformation | Thermal headroom (MW) | 22.75 | 23.09 | 22.8 | 22.44 | 21.8 | 21.18 | 20.14 | 18.94 | 17.6 | 15.99 | 13.38 | 9.49 | 5.14 | 0.13 | -5.15 | -29.95 | -37.99 | -37.71
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | WPD Best View | Thermal headroom (MW) | 22.75 | 21.25 | 19.13 | 16.89 | 13.82 | 10.36 | 5.47 | -0.64 | -8.2 | -16.41 | -25.27 | -35.34 | -45.46 | -55.16 | -64.09 | -84.24 | -90.87 | -91.18
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Consumer Transformation | Thermal headroom (MW) | 84.01 | 84.07 | 83.73 | 83.25 | 82.74 | 82.36 | 82.08 | 81.7 | 80.65 | 78.58 | 76.19 | 73.64 | 71.16 | 68.88 | 66.84 | 62.32 | 62.6 | 63.78
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Leading the Way | Thermal headroom (MW) | 84.01 | 84.07 | 83.71 | 83.22 | 82.7 | 82.39 | 82.1 | 81.65 | 79.55 | 77.24 | 74.84 | 72.24 | 69.79 | 67.64 | 65.94 | 64.16 | 67.33 | 72.17
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Steady Progression | Thermal headroom (MW) | 84.01 | 84.47 | 84.6 | 84.71 | 84.75 | 84.85 | 84.96 | 85.02 | 85.03 | 85 | 84.88 | 84.57 | 83.45 | 82.17 | 80.73 | 71.6 | 65.74 | 65.33
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | System Transformation | Thermal headroom (MW) | 84.01 | 84.32 | 84.28 | 84.23 | 84.07 | 84.21 | 84.35 | 84.41 | 84.38 | 84.37 | 83.55 | 82.02 | 80.19 | 78.13 | 75.9 | 66.28 | 65.72 | 68.14
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | WPD Best View | Thermal headroom (MW) | 84.01 | 84.07 | 83.71 | 83.22 | 82.7 | 82.39 | 82.1 | 81.65 | 79.55 | 77.24 | 74.84 | 72.24 | 69.79 | 67.64 | 65.94 | 64.16 | 67.33 | 72.17
Ocker Hill 132kV | Black Lake 132 11 (GT1A1) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Consumer Transformation | Thermal headroom (MW) | -21.12 | -20.06 | -20.04 | -21.07 | -22.97 | -25.43 | -27.84 | -30.27 | -33.07 | -36.55 | -44.3 | -51.98 | -59.76 | -67.36 | -74.94 | -103.03 | -130.69 | -146.51
Ocker Hill 132kV | Black Lake 132 11 (GT1A1) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Leading the Way | Thermal headroom (MW) | -21.12 | -20.87 | -22.36 | -24.59 | -27.87 | -31.72 | -35.4 | -39.57 | -44.81 | -50.82 | -56.85 | -63.35 | -70.04 | -76.47 | -82.23 | -96.85 | -100.66 | -99.02
Ocker Hill 132kV | Black Lake 132 11 (GT1A1) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Steady Progression | Thermal headroom (MW) | -21.12 | -18.66 | -17.6 | -17.05 | -16.56 | -16.61 | -16.61 | -16.69 | -16.93 | -18.13 | -20.07 | -20.97 | -22.5 | -24.45 | -26.3 | -39.07 | -47.52 | -48.48
Ocker Hill 132kV | Black Lake 132 11 (GT1A1) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | System Transformation | Thermal headroom (MW) | -21.12 | -18.95 | -18.26 | -18.19 | -18.35 | -18.45 | -18.53 | -18.81 | -19.33 | -20.16 | -21.89 | -23.9 | -26.2 | -28.78 | -31.89 | -46.15 | -48.76 | -46
Ocker Hill 132kV | Black Lake 132 11 (GT1A1) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | WPD Best View | Thermal headroom (MW) | -21.12 | -18.95 | -18.26 | -18.19 | -18.35 | -18.45 | -18.53 | -18.81 | -19.33 | -20.16 | -21.89 | -23.9 | -26.2 | -28.78 | -31.89 | -46.15 | -48.76 | -46
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Consumer Transformation | Thermal headroom (MW) | 25.49 | 25.93 | 25.62 | 23.95 | 22.64 | 21.25 | 19.76 | 18.32 | 16.78 | 15.05 | 11.48 | 6.58 | 1.59 | -3.29 | -8.04 | -30.38 | -43.8 | -49.19
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Leading the Way | Thermal headroom (MW) | 25.49 | 25.38 | 24.46 | 21.96 | 19.88 | 17.77 | 15.24 | 12.45 | 9.83 | 5.88 | 1.07 | -4.08 | -9.22 | -14.17 | -18.86 | -32.78 | -37.71 | -37.61
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Steady Progression | Thermal headroom (MW) | 25.49 | 26.47 | 26.78 | 26.15 | 26.08 | 25.78 | 25.41 | 25 | 24.58 | 24.05 | 23.2 | 22.34 | 21.28 | 20.16 | 19.02 | 8.59 | -0.86 | -4.67
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | System Transformation | Thermal headroom (MW) | 25.49 | 26.29 | 26.39 | 25.36 | 24.88 | 24.58 | 24.09 | 23.54 | 22.99 | 22.26 | 20.96 | 19.12 | 17.26 | 15.43 | 13.76 | 1.63 | -4.09 | -5.41
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | WPD Best View | Thermal headroom (MW) | 25.49 | 26.23 | 26.26 | 25.16 | 24.58 | 24.1 | 23.44 | 22.73 | 22.04 | 21.1 | 19.54 | 17.58 | 15.66 | 13.82 | 11.25 | -4.36 | -12.04 | -14.29
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Consumer Transformation | Thermal headroom (MW) | 33.44 | 33.05 | 32.44 | 31.51 | 29.94 | 27.83 | 25.54 | 23.06 | 20.28 | 17.38 | 11.85 | 5.44 | -1.02 | -7.36 | -13.43 | -44.27 | -63.88 | -72.48
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Leading the Way | Thermal headroom (MW) | 33.44 | 32.62 | 30.77 | 29.06 | 26.2 | 22.51 | 19.02 | 14.58 | 9.42 | 3.9 | -2.47 | -9.21 | -15.97 | -22.46 | -28.56 | -48.62 | -56.75 | -59.01
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Steady Progression | Thermal headroom (MW) | 33.44 | 34.25 | 34.52 | 34.64 | 34.49 | 33.94 | 33.34 | 32.6 | 31.74 | 30.64 | 29.01 | 27.33 | 25.52 | 23.28 | 21.02 | 6.61 | -5.87 | -11.53
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | System Transformation | Thermal headroom (MW) | 33.44 | 34 | 33.94 | 33.73 | 33.08 | 32.55 | 31.9 | 30.88 | 29.61 | 28.13 | 25.68 | 23.08 | 20.41 | 17.8 | 15.45 | -0.16 | -8.76 | -12.14
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | WPD Best View | Thermal headroom (MW) | 33.44 | 33.85 | 33.64 | 33.27 | 32.43 | 31.64 | 30.68 | 29.29 | 27.79 | 26.15 | 23.46 | 20.76 | 18.13 | 15.65 | 12.53 | -7.88 | -18.28 | -22.5
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Consumer Transformation | Thermal headroom (MW) | 19.07 | 18.71 | 18.53 | 18.3 | 17.86 | 17.23 | 16.59 | 15.88 | 15.02 | 13.69 | 11.7 | 9.69 | 7.64 | 5.69 | 3.78 | -3.7 | -7.54 | -8.77
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Leading the Way | Thermal headroom (MW) | 19.07 | 18.76 | 18.3 | 17.81 | 17.03 | 16.13 | 15.24 | 14.1 | 12.51 | 10.77 | 8.77 | 6.7 | 4.61 | 2.6 | 0.77 | -3.94 | -5.08 | -4.33
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Steady Progression | Thermal headroom (MW) | 19.07 | 19.4 | 19.51 | 19.61 | 19.68 | 19.56 | 19.39 | 19.22 | 19.01 | 18.7 | 18.27 | 17.82 | 17.32 | 16.75 | 15.79 | 10.07 | 5.57 | 4.09
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | System Transformation | Thermal headroom (MW) | 19.07 | 19.28 | 19.26 | 19.23 | 19.1 | 18.98 | 18.85 | 18.6 | 18.28 | 17.88 | 16.98 | 15.93 | 14.79 | 13.6 | 12.3 | 5.69 | 3.41 | 3.27
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | WPD Best View | Thermal headroom (MW) | 19.07 | 19.28 | 19.26 | 19.23 | 19.1 | 18.97 | 18.84 | 18.59 | 18.26 | 17.86 | 16.95 | 15.88 | 14.73 | 13.52 | 12.21 | 5.57 | 3.23 | 3.05
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Consumer Transformation | Thermal headroom (MW) | 38.28 | 38.34 | 37.92 | 37.19 | 36.04 | 34.42 | 33.14 | 31.77 | 30.41 | 28.75 | 25.52 | 22.31 | 19.05 | 15.93 | 12.9 | 0.07 | -7.19 | -9.45
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Leading the Way | Thermal headroom (MW) | 38.28 | 37.72 | 36.67 | 35.32 | 33.5 | 31.25 | 29.4 | 27.32 | 25.21 | 22.78 | 19.6 | 16.24 | 12.97 | 9.91 | 7.45 | -0.11 | -2.13 | -0.92
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Steady Progression | Thermal headroom (MW) | 38.28 | 38.86 | 39.05 | 39.15 | 39.17 | 38.8 | 38.5 | 38.14 | 37.8 | 37.35 | 36.65 | 35.93 | 35.07 | 34.12 | 33.08 | 25.19 | 19.5 | 17.88
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | System Transformation | Thermal headroom (MW) | 38.28 | 38.71 | 38.71 | 38.57 | 38.23 | 37.87 | 37.54 | 37.15 | 36.7 | 36.12 | 35.22 | 34.2 | 32.71 | 31.05 | 29.4 | 21.37 | 18.35 | 18.31
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | WPD Best View | Thermal headroom (MW) | 38.28 | 38.62 | 38.52 | 38.27 | 37.81 | 37.21 | 36.64 | 35.96 | 35.3 | 34.39 | 33.04 | 31.58 | 29.68 | 27.71 | 25.77 | 16.45 | 12.49 | 11.85
Penn 132kV | Coseley 132 11 (GT1A) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Consumer Transformation | Thermal headroom (MW) | 18.01 | 17.01 | 15.79 | 14.47 | 12.73 | 10.54 | 8.34 | 6.12 | 3.13 | -0.13 | -6.55 | -13.95 | -21.4 | -28.58 | -35.61 | -71.96 | -94.18 | -103.77
Penn 132kV | Coseley 132 11 (GT1A) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Leading the Way | Thermal headroom (MW) | 18.01 | 16.88 | 13.98 | 11.84 | 9.16 | 4.83 | 0.95 | -3.97 | -9.9 | -16.61 | -24.18 | -32.06 | -39.92 | -47.49 | -54.62 | -76.84 | -85.45 | -87.54
Penn 132kV | Coseley 132 11 (GT1A) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Steady Progression | Thermal headroom (MW) | 18.01 | 18.7 | 18.66 | 18.65 | 18.52 | 17.82 | 17.15 | 16.4 | 15.55 | 14.39 | 12.6 | 10.79 | 8.83 | 6.06 | 3.3 | -13.98 | -27.99 | -34.64
Penn 132kV | Coseley 132 11 (GT1A) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | System Transformation | Thermal headroom (MW) | 18.01 | 18.39 | 17.93 | 17.52 | 16.88 | 16.12 | 15.38 | 14.44 | 13.11 | 11.5 | 8.45 | 5.22 | 1.97 | -1.19 | -4.11 | -24.28 | -34.22 | -37.48
Penn 132kV | Coseley 132 11 (GT1A) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | WPD Best View | Thermal headroom (MW) | 18.01 | 17.01 | 15.79 | 14.47 | 12.73 | 10.54 | 8.33 | 6.11 | 3.12 | -0.15 | -6.57 | -13.97 | -21.41 | -28.6 | -35.62 | -71.96 | -94.17 | -103.76
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Consumer Transformation | Thermal headroom (MW) | 25.95 | 25.25 | 24.29 | 23.17 | 21.26 | 18.45 | 15.07 | 11.26 | 7.76 | 2.78 | -7.87 | -18.48 | -29.16 | -39.6 | -50.05 | -95.19 | -137.61 | -162.97
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Leading the Way | Thermal headroom (MW) | 25.95 | 24.6 | 22.19 | 20.11 | 16.36 | 11.31 | 6.06 | -1.54 | -9.44 | -18.06 | -26.86 | -36.37 | -46.14 | -55.69 | -64.62 | -93.09 | -106.4 | -112.52
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Steady Progression | Thermal headroom (MW) | 25.95 | 26.71 | 26.88 | 27.03 | 26.92 | 26.09 | 25.23 | 24.03 | 22.86 | 20.5 | 17.3 | 15.08 | 12.32 | 9.2 | 6.34 | -16.29 | -32.64 | -39.62
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | System Transformation | Thermal headroom (MW) | 25.95 | 26.35 | 26.12 | 25.86 | 25.16 | 24.34 | 23.45 | 21.76 | 20.07 | 18.15 | 15 | 11.67 | 8.29 | 4.98 | 1.25 | -23.53 | -34.09 | -37.9
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | WPD Best View | Thermal headroom (MW) | 25.95 | 25.29 | 24.35 | 23.26 | 21.41 | 18.74 | 15.47 | 11.76 | 8.35 | 3.58 | -6.8 | -17.14 | -27.59 | -37.83 | -48.12 | -92.45 | -134.05 | -159.13
Penn 132kV | Hinksford 132 11 (GT1B) | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Consumer Transformation | Thermal headroom (MW) | 7.12 | 6.3 | 5.38 | 4.26 | 2.7 | 0.05 | -2.54 | -5.13 | -7.98 | -11.31 | -16.95 | -22.49 | -28.1 | -33.55 | -38.84 | -67.16 | -83.59 | -91.31
Penn 132kV | Hinksford 132 11 (GT1B) | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Leading the Way | Thermal headroom (MW) | 7.12 | 5.19 | 3.17 | 1.01 | -1.74 | -5.91 | -10 | -14.42 | -19.09 | -24.27 | -30.16 | -36.19 | -42.21 | -48.06 | -53.55 | -72.36 | -80.32 | -83.67
Penn 132kV | Hinksford 132 11 (GT1B) | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Steady Progression | Thermal headroom (MW) | 7.12 | 7.12 | 6.96 | 6.78 | 6.45 | 5.43 | 4.39 | 3.23 | 2.05 | 0.64 | -1.25 | -3.06 | -5.03 | -7.15 | -9.35 | -25.4 | -35.78 | -40.29
Penn 132kV | Hinksford 132 11 (GT1B) | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | System Transformation | Thermal headroom (MW) | 7.12 | 6.82 | 6.43 | 5.95 | 5.18 | 4.28 | 3.31 | 2.1 | 0.69 | -0.8 | -3.05 | -5.67 | -8.68 | -11.81 | -15.16 | -33.61 | -42.88 | -46.19
Penn 132kV | Hinksford 132 11 (GT1B) | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | WPD Best View | Thermal headroom (MW) | 7.12 | 5.9 | 4.62 | 3.13 | 1.17 | -1.96 | -5.08 | -8.31 | -11.73 | -15.58 | -21.4 | -26.97 | -32.76 | -38.27 | -43.61 | -68.96 | -83.61 | -89.98
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Consumer Transformation | Thermal headroom (MW) | -21.534 | -21.87 | -22.4878 | -23.253 | -24.4786 | -26.6074 | -28.589 | -30.5266 | -32.6409 | -35.1815 | -39.6399 | -44.0246 | -48.4763 | -52.8171 | -56.952 | -80.4127 | -93.8152 | -99.9208
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Leading the Way | Thermal headroom (MW) | -21.534 | -22.8839 | -24.4604 | -26.1496 | -28.4245 | -31.9776 | -35.3127 | -38.8619 | -42.5291 | -46.7071 | -51.3271 | -56.1201 | -60.9239 | -65.4907 | -69.7415 | -84.7459 | -90.8117 | -93.2903
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Steady Progression | Thermal headroom (MW) | -21.534 | -21.2208 | -21.2033 | -21.2127 | -21.3649 | -22.1242 | -22.8654 | -23.7472 | -24.6435 | -25.6825 | -27.147 | -28.56 | -30.0792 | -31.7687 | -33.5754 | -46.1167 | -53.5757 | -56.4932
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | System Transformation | Thermal headroom (MW) | -21.534 | -21.4311 | -21.6 | -21.8341 | -22.3356 | -23.0419 | -23.7589 | -24.5939 | -25.5659 | -26.6369 | -28.3021 | -30.2689 | -32.5394 | -34.8746 | -37.3478 | -51.2823 | -58.0367 | -60.331
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | WPD Best View | Thermal headroom (MW) | -21.534 | -22.3641 | -23.3969 | -24.5846 | -26.2831 | -29.0518 | -31.6597 | -34.3788 | -37.1845 | -40.4344 | -44.9338 | -49.3597 | -53.9269 | -58.1982 | -62.2756 | -81.178 | -91.293 | -95.4526
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Consumer Transformation | Thermal headroom (MW) | 11.49 | 10.54 | 9.31 | 7.64 | 5.04 | 1.45 | -2.12 | -5.89 | -9.89 | -14.11 | -23.94 | -35.51 | -47.24 | -58.64 | -70.01 | -121.43 | -168.09 | -196.75
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Leading the Way | Thermal headroom (MW) | 11.49 | 10 | 7.38 | 4.83 | 0.6 | -5.09 | -10.62 | -17.22 | -25.59 | -34.75 | -44.34 | -54.71 | -65.37 | -75.81 | -85.15 | -116.16 | -130.89 | -137.76
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Steady Progression | Thermal headroom (MW) | 11.49 | 12.19 | 12.26 | 12.2 | 11.87 | 10.94 | 9.91 | 8.52 | 6.76 | 3.72 | -0.54 | -3.58 | -6.88 | -10.65 | -14.08 | -35.96 | -53.88 | -61.73
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | System Transformation | Thermal headroom (MW) | 11.49 | 11.8 | 11.42 | 10.89 | 9.91 | 9.02 | 7.73 | 5.98 | 3.46 | 0.67 | -2.78 | -6.47 | -10.63 | -14.7 | -18.71 | -43.53 | -56.1 | -60.19
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | WPD Best View | Thermal headroom (MW) | 11.49 | 10.61 | 9.43 | 7.84 | 5.38 | 1.91 | -1.54 | -5.21 | -9.14 | -13.29 | -22.35 | -33.57 | -45 | -56.18 | -67.37 | -117.06 | -162.87 | -190.85
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Consumer Transformation | Thermal headroom (MW) | 0.66 | 0.66 | 0.64 | 0.6 | 0.53 | 0.43 | 0.33 | 0.22 | 0.12 | 0.01 | -0.14 | -0.34 | -0.64 | -0.94 | -1.19 | -2.59 | -3.31 | -3.62
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Leading the Way | Thermal headroom (MW) | 0.66 | 0.63 | 0.58 | 0.52 | 0.42 | 0.26 | 0.06 | -0.16 | -0.36 | -0.57 | -0.75 | -1.02 | -1.29 | -1.55 | -1.77 | -2.7 | -3.03 | -3.15
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Steady Progression | Thermal headroom (MW) | 0.66 | 0.68 | 0.69 | 0.69 | 0.68 | 0.62 | 0.56 | 0.49 | 0.42 | 0.34 | 0.22 | 0.11 | -0.01 | -0.14 | -0.27 | -1.16 | -1.62 | -1.81
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | System Transformation | Thermal headroom (MW) | 0.66 | 0.67 | 0.67 | 0.65 | 0.62 | 0.58 | 0.54 | 0.49 | 0.43 | 0.36 | 0.27 | 0.17 | 0.06 | -0.05 | -0.14 | -0.88 | -1.5 | -1.67
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | WPD Best View | Thermal headroom (MW) | 0.66 | 0.64 | 0.59 | 0.53 | 0.44 | 0.31 | 0.17 | -0.01 | -0.17 | -0.34 | -0.48 | -0.66 | -0.86 | -1.08 | -1.34 | -2.4 | -2.91 | -3.08
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Consumer Transformation | Thermal headroom (MW) | 12.94 | 12.62 | 11.7 | 10.46 | 8.6 | 5.75 | 2.76 | -0.23 | -3.25 | -6.39 | -11.19 | -17.93 | -24.94 | -31.75 | -38.5 | -73.41 | -96.54 | -107.77
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Leading the Way | Thermal headroom (MW) | 12.94 | 11.76 | 9.85 | 7.6 | 4.44 | -0.2 | -4.72 | -9.54 | -14.37 | -20.32 | -27.47 | -34.81 | -42.29 | -49.6 | -56.43 | -79.53 | -89.89 | -94.52
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Steady Progression | Thermal headroom (MW) | 12.94 | 13.7 | 13.89 | 13.97 | 13.93 | 13.12 | 12.12 | 10.81 | 9.3 | 7.61 | 5.34 | 3 | 0.5 | -2.13 | -4.8 | -19.82 | -30.69 | -36.14
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | System Transformation | Thermal headroom (MW) | 12.94 | 13.39 | 13.19 | 12.84 | 12.3 | 11.58 | 10.38 | 8.84 | 6.99 | 5.02 | 2.51 | -0.52 | -3.62 | -6.62 | -9.77 | -24.51 | -34.1 | -38.9
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | WPD Best View | Thermal headroom (MW) | 12.94 | 12.54 | 11.52 | 10.2 | 8.24 | 5.15 | 1.96 | -1.31 | -4.55 | -7.86 | -13.63 | -20.69 | -27.78 | -34.71 | -41.47 | -74.03 | -95.71 | -106.16
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Consumer Transformation | Thermal headroom (MW) | 32.41 | 31.46 | 30.59 | 29.23 | 27.17 | 24.51 | 21.66 | 18.54 | 15.41 | 11.87 | 5.32 | -1.3 | -7.94 | -14.39 | -20.86 | -42.94 | -65.91 | -80.63
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Leading the Way | Thermal headroom (MW) | 32.41 | 31.12 | 29.18 | 27.21 | 24.39 | 20.95 | 17.38 | 13.13 | 8.3 | 2.94 | -2 | -7.33 | -12.85 | -18.14 | -22.77 | -35.06 | -39.11 | -39.15
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Steady Progression | Thermal headroom (MW) | 32.41 | 32.69 | 32.65 | 32.34 | 32 | 31.2 | 30.41 | 29.66 | 28.84 | 27.05 | 24.78 | 23.44 | 21.55 | 19.27 | 17.16 | 3.49 | -6.21 | -8.87
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | System Transformation | Thermal headroom (MW) | 32.41 | 32.38 | 32.11 | 31.5 | 30.66 | 29.77 | 28.95 | 27.88 | 26.74 | 25.36 | 23.26 | 20.98 | 18.37 | 15.52 | 12.11 | -3.4 | -8.3 | -7.76
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | WPD Best View | Thermal headroom (MW) | 32.41 | 31.52 | 30.73 | 29.47 | 27.6 | 25.16 | 22.51 | 19.63 | 16.72 | 13.39 | 7.2 | 0.95 | -5.43 | -11.64 | -17.93 | -39.63 | -62.49 | -76.76
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Consumer Transformation | Thermal headroom (MW) | 128.3 | 127.365 | 126.0677 | 124.9966 | 123.6354 | 121.7979 | 120.0918 | 118.2419 | 116.343 | 114.4798 | 111.3026 | 107.9789 | 104.3542 | 100.7583 | 97.3624 | 79.6746 | 69.9814 | 65.898
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Leading the Way | Thermal headroom (MW) | 128.3 | 126.94 | 125.0697 | 123.5558 | 121.6795 | 118.9267 | 116.4303 | 113.2964 | 110.0136 | 106.7275 | 102.979 | 99.0466 | 95.1801 | 91.4397 | 88.0901 | 77.2017 | 73.6066 | 72.7956
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Steady Progression | Thermal headroom (MW) | 128.3 | 128.0123 | 127.3406 | 126.968 | 126.5059 | 125.6742 | 124.9556 | 124.1052 | 123.2415 | 122.3806 | 121.2092 | 120.0334 | 118.8002 | 117.4754 | 116.1342 | 107.4175 | 101.6547 | 99.4127
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | System Transformation | Thermal headroom (MW) | 128.3 | 127.7535 | 126.7995 | 126.1804 | 125.4199 | 124.5416 | 123.7534 | 122.722 | 121.5453 | 120.4433 | 119.0564 | 117.491 | 115.9014 | 114.2581 | 112.7108 | 103.0855 | 98.5755 | 97.4013
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | WPD Best View | Thermal headroom (MW) | 128.3 | 128.0123 | 127.3406 | 126.968 | 126.5059 | 125.6742 | 124.9556 | 124.1052 | 123.2415 | 122.3806 | 121.2092 | 120.0334 | 118.8002 | 117.4754 | 116.1342 | 107.4175 | 101.6547 | 99.4127
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Consumer Transformation | Thermal headroom (MW) | 15.5 | 15.43 | 15.1 | 14.71 | 13.73 | 12.71 | 11.56 | 10.09 | 8.86 | 7.79 | 6.15 | 4.53 | 2.49 | 0.44 | -1.54 | -13.61 | -19.36 | -21.41
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Leading the Way | Thermal headroom (MW) | 15.5 | 15.17 | 14.55 | 13.9 | 12.54 | 10.89 | 8.98 | 6.36 | 4.34 | 2.37 | 0.22 | -2.01 | -4.24 | -6.37 | -8.38 | -15.5 | -17.24 | -17.35
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Steady Progression | Thermal headroom (MW) | 15.5 | 15.72 | 15.72 | 15.72 | 15.3 | 14.82 | 14.32 | 13.58 | 12.93 | 12.32 | 11.53 | 10.72 | 9.89 | 9.04 | 8.19 | 3.14 | 0.21 | -0.72
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | System Transformation | Thermal headroom (MW) | 15.5 | 15.62 | 15.5 | 15.38 | 14.76 | 14.22 | 13.57 | 12.52 | 11.68 | 10.92 | 10.05 | 9.17 | 8.3 | 7.44 | 6.66 | 0.81 | -1.51 | -1.93
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | WPD Best View | Thermal headroom (MW) | 15.5 | 15.72 | 15.72 | 15.72 | 15.3 | 14.82 | 14.32 | 13.58 | 12.93 | 12.32 | 11.53 | 10.72 | 9.89 | 9.04 | 8.19 | 3.14 | 0.21 | -0.72
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Consumer Transformation | Thermal headroom (MW) | 21.04 | 20.72 | 19.53 | 18.82 | 17.83 | 16.57 | 15.28 | 13.82 | 11.87 | 9.35 | 4.66 | -0.05 | -4.73 | -9.25 | -13.48 | -31.78 | -41.25 | -45.28
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Leading the Way | Thermal headroom (MW) | 21.04 | 20.67 | 18.56 | 17.43 | 15.94 | 14.24 | 12.38 | 8.97 | 4.7 | 0.21 | -4.49 | -9.47 | -14.4 | -19.08 | -23.3 | -34.68 | -37.63 | -37.51
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Steady Progression | Thermal headroom (MW) | 21.04 | 21.69 | 21.24 | 21.34 | 21.37 | 21.1 | 20.75 | 20.32 | 19.78 | 19.19 | 18.14 | 17.13 | 16.05 | 14.53 | 12.72 | -0.85 | -9.48 | -12.25
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | System Transformation | Thermal headroom (MW) | 21.04 | 21.46 | 20.65 | 20.45 | 20.12 | 19.92 | 19.55 | 19.01 | 18.27 | 17.45 | 15.82 | 14.21 | 12.46 | 10.08 | 7.15 | -8.12 | -14.1 | -15.25
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | WPD Best View | Thermal headroom (MW) | 21.04 | 21.69 | 21.24 | 21.34 | 21.37 | 21.1 | 20.75 | 20.32 | 19.78 | 19.19 | 18.14 | 17.13 | 16.05 | 14.53 | 12.72 | -0.85 | -9.48 | -12.25
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Consumer Transformation | Thermal headroom (MW) | 20.23 | 18.01 | 16.02 | 14.49 | 13.01 | 10.64 | 8.81 | 6.84 | 4.74 | 2.96 | 0.98 | -1.23 | -3.91 | -6.69 | -9.12 | -23.1 | -30.33 | -33.7
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Leading the Way | Thermal headroom (MW) | 20.23 | 17.51 | 15.03 | 13.16 | 11.57 | 8.3 | 5.98 | 3.13 | 0.05 | -2.6 | -5.63 | -8.77 | -11.81 | -14.72 | -16.99 | -24.7 | -27.52 | -28.89
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Steady Progression | Thermal headroom (MW) | 20.23 | 18.66 | 17.29 | 16.45 | 15.83 | 14.52 | 13.6 | 12.58 | 11.53 | 10.59 | 9.45 | 8.29 | 7.1 | 5.84 | 4.68 | -0.87 | -3.47 | -4.24
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | System Transformation | Thermal headroom (MW) | 20.23 | 18.32 | 16.65 | 15.58 | 14.75 | 13.35 | 12.45 | 11.26 | 9.74 | 8.6 | 7.32 | 5.99 | 4.67 | 3.35 | 2.32 | -2.94 | -6.19 | -7.09
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | WPD Best View | Thermal headroom (MW) | 20.23 | 18.66 | 17.29 | 16.45 | 15.83 | 14.52 | 13.6 | 12.58 | 11.53 | 10.59 | 9.45 | 8.29 | 7.1 | 5.84 | 4.68 | -0.87 | -3.47 | -4.24
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Consumer Transformation | Thermal headroom (MW) | 8.39 | 7.77 | 6.59 | 5.55 | 4.43 | 2.84 | 1.36 | -0.03 | -1.51 | -3.12 | -6.72 | -10.53 | -14.37 | -18.09 | -21.72 | -39.1 | -50.03 | -54.77
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Leading the Way | Thermal headroom (MW) | 8.39 | 7.31 | 5.6 | 4.07 | 2.23 | -0.29 | -2.51 | -4.75 | -7.55 | -10.65 | -14.43 | -18.42 | -22.34 | -26.22 | -29.82 | -41.48 | -46.02 | -47.06
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Steady Progression | Thermal headroom (MW) | 8.39 | 8.35 | 7.76 | 7.37 | 7.05 | 6.42 | 5.86 | 5.29 | 4.67 | 3.92 | 2.88 | 1.82 | 0.71 | -0.45 | -1.61 | -10.57 | -17.81 | -21.23
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | System Transformation | Thermal headroom (MW) | 8.39 | 8.11 | 7.25 | 6.61 | 5.99 | 5.34 | 4.74 | 4.18 | 3.34 | 2.36 | 1.12 | -0.55 | -2.24 | -3.88 | -5.39 | -15.53 | -20.54 | -22.13
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | WPD Best View | Thermal headroom (MW) | 8.39 | 8.35 | 7.76 | 7.37 | 7.05 | 6.42 | 5.86 | 5.29 | 4.67 | 3.92 | 2.88 | 1.82 | 0.71 | -0.45 | -1.61 | -10.57 | -17.81 | -21.23
Port Ham 132kV | Cheltenham 132 11 (GT1B) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Consumer Transformation | Thermal headroom (MW) | 26.75 | 26.36 | 24.84 | 23.04 | 20.62 | 17.43 | 13.65 | 9.78 | 6.07 | 1.72 | -4.24 | -10.32 | -16.47 | -22.29 | -27.71 | -50 | -59.78 | -63
Port Ham 132kV | Cheltenham 132 11 (GT1B) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Leading the Way | Thermal headroom (MW) | 26.75 | 26.21 | 24 | 21.47 | 18.26 | 13.96 | 8.74 | 2.83 | -4.06 | -11.33 | -17.65 | -24.18 | -30.59 | -36.39 | -41.47 | -53.31 | -55.22 | -53.74
Port Ham 132kV | Cheltenham 132 11 (GT1B) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Steady Progression | Thermal headroom (MW) | 26.75 | 27.34 | 26.66 | 25.97 | 25.07 | 23.55 | 21.88 | 20.04 | 18.2 | 16.25 | 14.28 | 12.11 | 9.86 | 7.57 | 5.02 | -7.81 | -14.76 | -16.29
Port Ham 132kV | Cheltenham 132 11 (GT1B) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | System Transformation | Thermal headroom (MW) | 26.75 | 27.13 | 26.08 | 24.98 | 23.59 | 21.83 | 19.48 | 16.97 | 14.58 | 11.94 | 9.24 | 6.43 | 3.6 | 0.92 | -1.69 | -16.48 | -19.96 | -19.96
Port Ham 132kV | Cheltenham 132 11 (GT1B) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | WPD Best View | Thermal headroom (MW) | 26.75 | 27.34 | 26.66 | 25.97 | 25.07 | 23.55 | 21.88 | 20.04 | 18.2 | 16.25 | 14.28 | 12.11 | 9.86 | 7.57 | 5.02 | -7.81 | -14.76 | -16.29
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Consumer Transformation | Thermal headroom (MW) | 29.376 | 29.2339 | 26.3133 | 25.8732 | 25.2021 | 24.2845 | 23.2428 | 21.9368 | 20.6228 | 19.1624 | 16.8645 | 14.1714 | 11.218 | 8.3407 | 5.6024 | -8.2772 | -15.3881 | -18.3696
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Leading the Way | Thermal headroom (MW) | 29.376 | 28.9558 | 25.6681 | 24.8913 | 23.8612 | 22.429 | 20.842 | 18.5627 | 16.1307 | 13.4785 | 10.5443 | 7.4559 | 4.3556 | 1.3378 | -1.1757 | -9.9815 | -12.4562 | -12.8018
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Steady Progression | Thermal headroom (MW) | 29.376 | 29.6093 | 29.6245 | 29.6635 | 29.6207 | 29.3009 | 28.8991 | 28.3049 | 27.6527 | 26.9 | 26.0054 | 25.0767 | 24.0846 | 23.0318 | 21.9732 | 14.6936 | 9.946 | 7.9852
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | System Transformation | Thermal headroom (MW) | 29.376 | 29.4909 | 29.3686 | 29.27 | 29.026 | 28.7183 | 28.2865 | 27.5357 | 26.6904 | 25.7421 | 24.7834 | 23.7563 | 22.4476 | 21.109 | 19.8333 | 11.2066 | 7.5265 | 6.8668
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | WPD Best View | Thermal headroom (MW) | 29.376 | 29.6093 | 29.6245 | 29.6635 | 29.6207 | 29.3009 | 28.8991 | 28.3049 | 27.6527 | 26.9 | 26.0054 | 25.0767 | 24.0846 | 23.0318 | 21.9732 | 14.6936 | 9.946 | 7.9852
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Consumer Transformation | Thermal headroom (MW) | -2.06 | -1.9 | -7.02 | -7.06 | -7.22 | -7.49 | -7.85 | -8.33 | -8.68 | -9.22 | -9.68 | -10.28 | -11.37 | -12.43 | -13.42 | -18.98 | -21.15 | -21.91
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Leading the Way | Thermal headroom (MW) | -2.06 | -1.99 | -7.21 | -7.34 | -7.6 | -8.03 | -8.57 | -9.37 | -10.02 | -11.06 | -11.99 | -13.04 | -14.09 | -15.12 | -16.06 | -19.7 | -20.18 | -19.94
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Steady Progression | Thermal headroom (MW) | -2.06 | -1.79 | -1.67 | -1.57 | -1.51 | -1.58 | -1.7 | -1.92 | -2.09 | -2.38 | -2.69 | -3.02 | -3.37 | -3.73 | -4.1 | -7.43 | -9.47 | -10.38
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | System Transformation | Thermal headroom (MW) | -2.06 | -1.83 | -1.75 | -1.7 | -1.71 | -1.74 | -1.83 | -2.1 | -2.27 | -2.66 | -2.97 | -3.3 | -3.65 | -3.98 | -4.29 | -8.54 | -10.66 | -10.72
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | WPD Best View | Thermal headroom (MW) | -2.06 | -1.79 | -1.67 | -1.57 | -1.51 | -1.58 | -1.7 | -1.92 | -2.09 | -2.38 | -2.69 | -3.02 | -3.37 | -3.73 | -4.1 | -7.43 | -9.47 | -10.38
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Consumer Transformation | Thermal headroom (MW) | 14.41 | 14.09 | 13.73 | 13.31 | 12.78 | 12.12 | 11.42 | 10.49 | 9.47 | 8.46 | 6.49 | 4.47 | 2.46 | 0.5 | -1.38 | -11.3 | -17.11 | -19.64
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Leading the Way | Thermal headroom (MW) | 14.41 | 13.9 | 13.25 | 12.56 | 11.76 | 10.63 | 9.41 | 7.55 | 5.56 | 3.84 | 1.78 | -0.35 | -2.49 | -4.61 | -6.2 | -12.32 | -14.88 | -15.81
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Steady Progression | Thermal headroom (MW) | 14.41 | 14.36 | 14.27 | 14.21 | 14.1 | 13.82 | 13.47 | 12.95 | 12.35 | 11.77 | 11.09 | 10.4 | 9.67 | 8.91 | 8.15 | 2.7 | -0.56 | -2.04
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | System Transformation | Thermal headroom (MW) | 14.41 | 14.28 | 14.11 | 13.96 | 13.73 | 13.43 | 13.05 | 12.39 | 11.63 | 10.94 | 10.23 | 9.48 | 8.36 | 7.17 | 6.03 | 0.01 | -2.78 | -3.59
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | WPD Best View | Thermal headroom (MW) | 14.41 | 14.36 | 14.27 | 14.21 | 14.1 | 13.82 | 13.47 | 12.95 | 12.35 | 11.77 | 11.09 | 10.4 | 9.67 | 8.91 | 8.15 | 2.7 | -0.56 | -2.04
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Consumer Transformation | Thermal headroom (MW) | 29.61 | 29.52 | 29.12 | 28.55 | 27.06 | 25.17 | 23.63 | 22.05 | 20.51 | 18.52 | 15.48 | 11.98 | 7.82 | 3.51 | -0.66 | -23.54 | -38.46 | -44.82
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Leading the Way | Thermal headroom (MW) | 29.61 | 29.25 | 28.14 | 26.93 | 24.56 | 21.04 | 18.43 | 15.68 | 12.77 | 9.7 | 5.11 | 0.32 | -4.4 | -9.01 | -13.38 | -27.56 | -33 | -34.72
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Steady Progression | Thermal headroom (MW) | 29.61 | 30.56 | 30.87 | 31.13 | 30.75 | 30.03 | 29.63 | 29.17 | 28.65 | 27.94 | 26.72 | 25.46 | 24.1 | 22.72 | 20.97 | 12.7 | 5.96 | 2.89
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | System Transformation | Thermal headroom (MW) | 29.61 | 30.32 | 30.35 | 30.31 | 29.47 | 28.63 | 28.23 | 27.71 | 26.9 | 25.9 | 24.1 | 22.22 | 20.32 | 18.48 | 16.84 | 8.15 | 3.09 | 1.31
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | WPD Best View | Thermal headroom (MW) | 29.61 | 30.56 | 30.87 | 31.13 | 30.75 | 30.03 | 29.63 | 29.17 | 28.65 | 27.94 | 26.72 | 25.46 | 24.1 | 22.72 | 20.97 | 12.7 | 5.96 | 2.89
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Consumer Transformation | Thermal headroom (MW) | 63.8 | 63.1356 | 62.3509 | 61.3691 | 60.0644 | 57.443 | 54.8928 | 52.1918 | 49.0099 | 45.632 | 40.1321 | 34.6411 | 29.1096 | 23.7918 | 18.607 | -4.1289 | -20.4657 | -29.892
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Leading the Way | Thermal headroom (MW) | 63.8 | 62.6883 | 60.8857 | 59.1318 | 56.9348 | 53.0117 | 49.2357 | 44.7579 | 39.4711 | 34.2705 | 29.0938 | 23.5746 | 18.0312 | 12.6654 | 7.9395 | -6.9491 | -13.846 | -17.2926
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Steady Progression | Thermal headroom (MW) | 63.8 | 64.0886 | 63.9468 | 63.7979 | 63.615 | 62.5772 | 61.5826 | 60.5275 | 59.2629 | 58.1143 | 56.5483 | 54.9652 | 53.2639 | 51.2372 | 48.9263 | 35.0278 | 26.417 | 23.2324
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | System Transformation | Thermal headroom (MW) | 63.8 | 63.8785 | 63.4661 | 62.9973 | 62.4253 | 61.5224 | 60.5861 | 59.3335 | 57.6226 | 56.3424 | 54.186 | 51.8234 | 49.077 | 46.1796 | 43.1829 | 27.847 | 20.7898 | 18.8725
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | WPD Best View | Thermal headroom (MW) | 63.8 | 63.1356 | 62.3509 | 61.3691 | 60.0644 | 57.443 | 54.8928 | 52.1918 | 49.0099 | 45.632 | 40.1321 | 34.6411 | 29.1096 | 23.7918 | 18.607 | -4.1289 | -20.4657 | -29.892
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Consumer Transformation | Thermal headroom (MW) | 27.76 | 27.81 | 27.31 | 26.68 | 25.77 | 23.52 | 21.43 | 19.22 | 16.82 | 14.77 | 10.42 | 6.07 | 1.73 | -2.52 | -6.81 | -25.09 | -42.72 | -54.05
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Leading the Way | Thermal headroom (MW) | 27.76 | 27.17 | 26.03 | 24.8 | 23.12 | 19.65 | 16.47 | 12.77 | 8.19 | 4.24 | 0.68 | -3.26 | -7.43 | -11.59 | -15.09 | -27.76 | -35.6 | -41.31
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Steady Progression | Thermal headroom (MW) | 27.76 | 28.23 | 28.25 | 28.26 | 28.2 | 27.24 | 26.37 | 25.42 | 24.36 | 23.46 | 22.3 | 21.15 | 19.92 | 18.62 | 17.25 | 8.16 | 3.51 | 1.94
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | System Transformation | Thermal headroom (MW) | 27.76 | 28.06 | 27.87 | 27.64 | 27.27 | 26.35 | 25.5 | 24.35 | 22.98 | 22.14 | 20.91 | 19.6 | 17.8 | 15.94 | 14.02 | 4.56 | 0.05 | -1.08
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | WPD Best View | Thermal headroom (MW) | 27.76 | 27.81 | 27.31 | 26.68 | 25.77 | 23.52 | 21.43 | 19.22 | 16.82 | 14.77 | 10.42 | 6.07 | 1.73 | -2.52 | -6.81 | -25.09 | -42.72 | -54.05
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Consumer Transformation | Thermal headroom (MW) | 12.45 | 11.56 | 10.74 | 9.82 | 8.82 | 6.64 | 4.52 | 2.39 | -0.02 | -2.99 | -7.35 | -11.64 | -15.97 | -20.19 | -24.32 | -46.08 | -60 | -68.2
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Leading the Way | Thermal headroom (MW) | 12.45 | 11.14 | 9.52 | 7.83 | 6.05 | 2.62 | -0.68 | -4.18 | -8.35 | -12.78 | -17.22 | -21.74 | -26.23 | -30.57 | -34.63 | -48.94 | -56.28 | -60.9
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Steady Progression | Thermal headroom (MW) | 12.45 | 12.35 | 11.97 | 11.61 | 11.38 | 10.42 | 9.5 | 8.61 | 7.52 | 6.48 | 5.06 | 3.66 | 2.17 | 0.65 | -1.37 | -13.06 | -20.45 | -23.87
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | System Transformation | Thermal headroom (MW) | 12.45 | 12.13 | 11.51 | 10.86 | 10.32 | 9.64 | 8.97 | 8.02 | 6.51 | 5.39 | 3.49 | 1.43 | -0.76 | -3.04 | -5.37 | -18.46 | -26.51 | -30.5
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | WPD Best View | Thermal headroom (MW) | 12.45 | 11.56 | 10.74 | 9.82 | 8.82 | 6.64 | 4.52 | 2.39 | -0.02 | -2.99 | -7.35 | -11.64 | -15.97 | -20.19 | -24.32 | -46.08 | -60 | -68.2
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Consumer Transformation | Thermal headroom (MW) | 16.72 | 16.16 | 15.83 | 15.32 | 14.53 | 13.46 | 12.34 | 11.04 | 9.24 | 7.23 | 4.48 | 1.68 | -1.18 | -3.79 | -6.2 | -14.16 | -17.18 | -17.71
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Leading the Way | Thermal headroom (MW) | 16.72 | 16.26 | 15.25 | 14.49 | 13.36 | 12.01 | 10.56 | 8.42 | 6.12 | 3.63 | 0.82 | -2.22 | -5.11 | -7.8 | -10.12 | -14.64 | -14.31 | -11.69
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Steady Progression | Thermal headroom (MW) | 16.72 | 16.92 | 16.95 | 16.97 | 16.87 | 16.6 | 16.29 | 15.91 | 15.41 | 14.93 | 14.22 | 13.46 | 12.62 | 11.26 | 9.83 | 1.69 | -4.15 | -5.86
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | System Transformation | Thermal headroom (MW) | 16.72 | 16.86 | 16.78 | 16.65 | 16.36 | 16.07 | 15.64 | 15.12 | 14.42 | 13.7 | 12.35 | 10.81 | 9.1 | 7.23 | 5.28 | -4.08 | -6.52 | -5.75
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | WPD Best View | Thermal headroom (MW) | 16.72 | 16.16 | 15.83 | 15.32 | 14.53 | 13.46 | 12.34 | 11.04 | 9.24 | 7.23 | 4.48 | 1.68 | -1.18 | -3.79 | -6.2 | -14.16 | -17.18 | -17.71
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Consumer Transformation | Thermal headroom (MW) | 2.65 | 2.33 | 2.13 | 1.8 | 1.32 | -0.17 | -2.07 | -3.94 | -5.91 | -8.5 | -13.41 | -18.39 | -23.5 | -28.61 | -33.97 | -53.79 | -73.6 | -87.05
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Leading the Way | Thermal headroom (MW) | 2.65 | 2.31 | 1.39 | 0.73 | -0.27 | -2.38 | -4.89 | -7.61 | -10.98 | -15.21 | -18.55 | -22.36 | -26.48 | -30.61 | -34.59 | -49.49 | -53.21 | -54.77
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Steady Progression | Thermal headroom (MW) | 2.65 | 2.85 | 2.82 | 2.78 | 2.68 | 2.08 | 1.39 | 0.68 | -0.08 | -1.92 | -4.3 | -5.69 | -7.87 | -10.43 | -12.83 | -26.69 | -31.6 | -32.88
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | System Transformation | Thermal headroom (MW) | 2.65 | 2.76 | 2.67 | 2.5 | 2.24 | 1.74 | 1.18 | 0.54 | -0.18 | -1.37 | -3.29 | -5.41 | -7.65 | -10.06 | -12.93 | -27.9 | -32.57 | -32.63
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | WPD Best View | Thermal headroom (MW) | 2.65 | 2.85 | 2.82 | 2.78 | 2.68 | 2.08 | 1.39 | 0.68 | -0.08 | -1.92 | -4.3 | -5.69 | -7.87 | -10.43 | -12.83 | -26.69 | -31.6 | -32.88
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Consumer Transformation | Thermal headroom (MW) | 15.01 | 14.9 | 14.65 | 14.29 | 13.79 | 13.07 | 12.53 | 11.92 | 11.36 | 10.6 | 9.16 | 7.7 | 6.25 | 4.86 | 3.55 | -3.83 | -7.7 | -9.4
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Leading the Way | Thermal headroom (MW) | 15.01 | 14.75 | 14.33 | 13.82 | 13.15 | 11.88 | 10.9 | 9.55 | 8.23 | 6.71 | 5.31 | 3.9 | 2.51 | 1.2 | -0.04 | -4.82 | -6.32 | -6.77
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Steady Progression | Thermal headroom (MW) | 15.01 | 15.06 | 15.01 | 14.92 | 14.8 | 14.45 | 14.17 | 13.84 | 13.51 | 13.11 | 12.6 | 12.07 | 11.51 | 10.77 | 10.03 | 5.24 | 2.8 | 1.64
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | System Transformation | Thermal headroom (MW) | 15.01 | 15.01 | 14.89 | 14.72 | 14.47 | 14.14 | 13.9 | 13.56 | 13.22 | 12.8 | 12.24 | 11.65 | 11.06 | 10.48 | 9.82 | 4.7 | 2.15 | 1.43
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | WPD Best View | Thermal headroom (MW) | 15.01 | 15.06 | 15.01 | 14.92 | 14.8 | 14.45 | 14.17 | 13.84 | 13.51 | 13.11 | 12.6 | 12.07 | 11.51 | 10.77 | 10.03 | 5.24 | 2.8 | 1.64
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Consumer Transformation | Thermal headroom (MW) | 4.56 | 4.55 | 4.45 | 4.37 | 4.22 | 3.83 | 3.49 | 3.14 | 2.8 | 2.44 | 1.38 | 0.29 | -0.85 | -1.98 | -3.08 | -6.77 | -8.57 | -9.25
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Leading the Way | Thermal headroom (MW) | 4.56 | 4.48 | 4.31 | 4.16 | 3.92 | 3.41 | 2.91 | 2.31 | 1.54 | 0.68 | -0.33 | -1.34 | -2.35 | -3.35 | -3.95 | -6.49 | -7.49 | -7.58
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Steady Progression | Thermal headroom (MW) | 4.56 | 4.62 | 4.61 | 4.62 | 4.59 | 4.4 | 4.23 | 4.05 | 3.85 | 3.61 | 3.25 | 2.92 | 2.51 | 2.04 | 1.58 | -2.06 | -3.91 | -4.66
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | System Transformation | Thermal headroom (MW) | 4.56 | 4.59 | 4.55 | 4.52 | 4.45 | 4.32 | 4.23 | 4.1 | 3.94 | 3.75 | 3.48 | 3.18 | 2.52 | 1.88 | 1.26 | -2.61 | -5.1 | -5.53
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | WPD Best View | Thermal headroom (MW) | 4.56 | 4.62 | 4.61 | 4.62 | 4.59 | 4.4 | 4.23 | 4.05 | 3.85 | 3.61 | 3.25 | 2.92 | 2.51 | 2.04 | 1.58 | -2.06 | -3.91 | -4.66
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Consumer Transformation | Thermal headroom (MW) | 0.96 | 0.81 | 0.55 | 0.22 | -0.23 | -0.93 | -2.16 | -3.64 | -5.29 | -7.4 | -9.37 | -11.11 | -12.63 | -14.13 | -15.52 | -23.25 | -25.98 | -26.65
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Leading the Way | Thermal headroom (MW) | 0.96 | 0.56 | 0.03 | -0.59 | -1.3 | -2.35 | -4.17 | -6.47 | -8.98 | -12.16 | -14.47 | -16.38 | -17.9 | -19.37 | -20.67 | -25.18 | -25.54 | -25.19
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Steady Progression | Thermal headroom (MW) | 0.96 | 0.94 | 0.89 | 0.81 | 0.67 | 0.36 | -0.24 | -1 | -1.88 | -3.05 | -4.2 | -5.24 | -6.17 | -7.14 | -8.07 | -13.35 | -15.06 | -15.36
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | System Transformation | Thermal headroom (MW) | 0.96 | 0.91 | 0.8 | 0.61 | 0.39 | 0.15 | -0.64 | -1.66 | -2.92 | -4.67 | -6.07 | -7.23 | -8.21 | -9.17 | -10.19 | -15.82 | -17.26 | -17.22
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | WPD Best View | Thermal headroom (MW) | 0.96 | 0.94 | 0.89 | 0.81 | 0.67 | 0.36 | -0.24 | -1 | -1.88 | -3.05 | -4.2 | -5.24 | -6.17 | -7.14 | -8.07 | -13.35 | -15.06 | -15.36
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Consumer Transformation | Thermal headroom (MW) | 15.31 | 15.68 | 15.85 | 16 | 16.1 | 15.42 | 14.98 | 14.36 | 13.7 | 13.01 | 12.54 | 11.9 | 11.09 | 10.3 | 9.52 | 6.57 | 6.64 | 7.37
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Leading the Way | Thermal headroom (MW) | 15.31 | 15.66 | 15.81 | 15.94 | 15.99 | 14.85 | 14.18 | 13.09 | 12.07 | 10.89 | 10.03 | 9.33 | 8.74 | 8.21 | 7.69 | 6.08 | 6.88 | 8.02
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Steady Progression | Thermal headroom (MW) | 15.31 | 15.71 | 15.91 | 16.09 | 16.26 | 15.8 | 15.59 | 15.25 | 14.89 | 14.42 | 14.05 | 13.72 | 13.38 | 12.97 | 12.56 | 8.95 | 8.26 | 8.48
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | System Transformation | Thermal headroom (MW) | 15.31 | 15.69 | 15.86 | 16.03 | 16.16 | 15.61 | 15.3 | 14.79 | 14.25 | 13.66 | 13.27 | 12.96 | 12.66 | 12.36 | 11.9 | 8.18 | 7.35 | 8.14
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | WPD Best View | Thermal headroom (MW) | 15.31 | 15.71 | 15.91 | 16.09 | 16.26 | 15.8 | 15.59 | 15.25 | 14.89 | 14.42 | 14.05 | 13.72 | 13.38 | 12.97 | 12.56 | 8.95 | 8.26 | 8.48
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Consumer Transformation | Thermal headroom (MW) | 7.79 | 7.75 | 7.67 | 7.6 | 7.43 | 6.77 | 6.17 | 5.56 | 4.89 | 4.12 | 3.34 | 2.58 | 1.79 | 1.04 | 0.32 | -2.97 | -4.08 | -4.35
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Leading the Way | Thermal headroom (MW) | 7.79 | 7.7 | 7.5 | 7.34 | 7.07 | 6.09 | 5.23 | 4.31 | 3.34 | 2.25 | 1.58 | 0.84 | 0.14 | -0.53 | -1.15 | -2.9 | -3.05 | -2.74
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Steady Progression | Thermal headroom (MW) | 7.79 | 7.82 | 7.82 | 7.83 | 7.75 | 7.37 | 7.05 | 6.72 | 6.36 | 5.93 | 5.48 | 5.08 | 4.68 | 4.2 | 3.73 | 0.56 | -0.77 | -0.88
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | System Transformation | Thermal headroom (MW) | 7.79 | 7.82 | 7.8 | 7.78 | 7.69 | 7.33 | 6.98 | 6.6 | 6.16 | 5.69 | 5.28 | 4.77 | 4.29 | 3.74 | 3.22 | 0.16 | -1.2 | -1.09
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | WPD Best View | Thermal headroom (MW) | 7.79 | 7.82 | 7.82 | 7.83 | 7.75 | 7.37 | 7.05 | 6.72 | 6.36 | 5.93 | 5.48 | 5.08 | 4.68 | 4.2 | 3.73 | 0.56 | -0.77 | -0.88
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Consumer Transformation | Thermal headroom (MW) | 3.58 | 3.62 | 3.51 | 3.34 | 3.11 | 2.38 | 1.61 | 0.81 | -0.22 | -1.8 | -3.63 | -5.46 | -7.34 | -8.89 | -10.41 | -17.07 | -19.56 | -20.3
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Leading the Way | Thermal headroom (MW) | 3.58 | 3.53 | 3.31 | 3.04 | 2.68 | 1.61 | 0.23 | -1.54 | -3.55 | -5.96 | -7.63 | -9.44 | -11.24 | -12.47 | -13.63 | -18.3 | -19.14 | -19.18
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Steady Progression | Thermal headroom (MW) | 3.58 | 3.71 | 3.71 | 3.69 | 3.66 | 3.21 | 2.74 | 2.14 | 1.43 | 0.56 | -0.68 | -1.89 | -3.3 | -4.44 | -5.6 | -12.06 | -13.57 | -13.9
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | System Transformation | Thermal headroom (MW) | 3.58 | 3.67 | 3.62 | 3.55 | 3.41 | 3.09 | 2.67 | 2.19 | 1.58 | 0.8 | -0.12 | -1.36 | -2.67 | -3.69 | -4.71 | -10.6 | -13.53 | -14.07
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | WPD Best View | Thermal headroom (MW) | 3.58 | 3.71 | 3.71 | 3.69 | 3.66 | 3.21 | 2.74 | 2.14 | 1.43 | 0.56 | -0.68 | -1.89 | -3.3 | -4.44 | -5.6 | -12.06 | -13.57 | -13.9
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Consumer Transformation | Thermal headroom (MW) | 3.68 | 3.69 | 3.68 | 3.65 | 3.58 | 3.28 | 2.87 | 2.51 | 2.12 | 1.68 | 0.78 | -0.13 | -1.02 | -1.9 | -2.75 | -4.99 | -5.76 | -5.82
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Leading the Way | Thermal headroom (MW) | 3.68 | 3.67 | 3.64 | 3.59 | 3.46 | 2.96 | 2.25 | 1.69 | 1.01 | 0.24 | -0.56 | -1.44 | -2.35 | -3.25 | -3.72 | -5.6 | -6.62 | -6.94
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Steady Progression | Thermal headroom (MW) | 3.68 | 3.71 | 3.71 | 3.71 | 3.69 | 3.49 | 3.26 | 3.07 | 2.83 | 2.49 | 2.06 | 1.71 | 1.33 | 0.92 | 0.55 | -2.46 | -3.93 | -4.51
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | System Transformation | Thermal headroom (MW) | 3.68 | 3.68 | 3.67 | 3.64 | 3.57 | 3.38 | 3.2 | 3.09 | 2.95 | 2.76 | 2.29 | 1.97 | 1.15 | 0.39 | -0.47 | -3.98 | -6.31 | -6.81
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | WPD Best View | Thermal headroom (MW) | 3.68 | 3.69 | 3.68 | 3.66 | 3.6 | 3.33 | 3 | 2.64 | 2.25 | 1.73 | 0.73 | -0.19 | -1.07 | -1.98 | -2.82 | -5.17 | -5.91 | -5.99
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Consumer Transformation | Thermal headroom (MW) | 38.57 | 38.2 | 37.31 | 36.16 | 34.26 | 31.67 | 29.23 | 26.71 | 24.18 | 21.06 | 17.07 | 10.83 | 4.42 | -1.74 | -7.68 | -36.29 | -54.23 | -62.37
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Leading the Way | Thermal headroom (MW) | 38.57 | 37.46 | 35.7 | 33.78 | 31.07 | 27.36 | 23.74 | 19.8 | 15.39 | 9.33 | 2.51 | -4.25 | -10.98 | -17.42 | -23.05 | -40.63 | -46.67 | -47.84
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Steady Progression | Thermal headroom (MW) | 38.57 | 39.21 | 39.32 | 39.34 | 39.23 | 38.39 | 37.5 | 36.28 | 34.86 | 33 | 30.86 | 28.74 | 26.45 | 24.04 | 21.59 | 7.43 | -2.24 | -6.19
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | System Transformation | Thermal headroom (MW) | 38.57 | 38.9 | 38.62 | 38.26 | 37.64 | 36.85 | 35.83 | 34.53 | 33.01 | 30.82 | 28.7 | 26.56 | 24.01 | 21.54 | 18.99 | 4.94 | -1.91 | -3.93
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | WPD Best View | Thermal headroom (MW) | 38.57 | 39.21 | 39.32 | 39.34 | 39.23 | 38.39 | 37.5 | 36.28 | 34.86 | 33 | 30.86 | 28.74 | 26.45 | 24.04 | 21.59 | 7.43 | -2.24 | -6.19
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Consumer Transformation | Thermal headroom (MW) | 27.84 | 26.62 | 25.88 | 24.96 | 23.01 | 21.36 | 20.17 | 18.85 | 17.81 | 16.73 | 13.72 | 10.67 | 7.57 | 4.63 | 1.84 | -10.24 | -16.44 | -18.55
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Leading the Way | Thermal headroom (MW) | 27.84 | 26.17 | 25.06 | 23.74 | 21.21 | 18.74 | 16.94 | 14.9 | 12.95 | 10.56 | 7.48 | 4.26 | 1.1 | -1.88 | -4.6 | -11.84 | -13.27 | -12.49
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Steady Progression | Thermal headroom (MW) | 27.84 | 27.15 | 26.82 | 26.37 | 25.18 | 24.29 | 23.68 | 22.94 | 22.35 | 21.72 | 20.9 | 20.04 | 19.18 | 18.36 | 17.53 | 9.01 | 3.86 | 2.41
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | System Transformation | Thermal headroom (MW) | 27.84 | 26.86 | 26.31 | 25.64 | 24.06 | 23.07 | 22.44 | 21.6 | 20.99 | 20.28 | 19.42 | 18.2 | 16.96 | 15.73 | 13.99 | 4.54 | 1.32 | 1.18
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | WPD Best View | Thermal headroom (MW) | 27.84 | 27.15 | 26.82 | 26.37 | 25.18 | 24.29 | 23.68 | 22.94 | 22.35 | 21.72 | 20.9 | 20.04 | 19.18 | 18.36 | 17.53 | 9.01 | 3.86 | 2.41
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Consumer Transformation | Thermal headroom (MW) | 15.44 | 15.44 | 14.96 | 14.45 | 13.57 | 12.26 | 10.74 | 9.07 | 7.33 | 5.36 | 2.55 | -1.44 | -5.48 | -9.45 | -13.22 | -30.15 | -38.17 | -41.58
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Leading the Way | Thermal headroom (MW) | 15.44 | 15.04 | 14.09 | 13.18 | 11.8 | 10.04 | 8.17 | 5.79 | 2.87 | -0.88 | -5.06 | -9.42 | -13.8 | -17.95 | -21.72 | -32.71 | -34.57 | -33.86
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Steady Progression | Thermal headroom (MW) | 15.44 | 15.97 | 16.04 | 16.17 | 16.17 | 15.82 | 15.42 | 14.91 | 14.3 | 13.48 | 12.42 | 11.27 | 10.01 | 8.63 | 7.22 | -0.16 | -6.03 | -7.94
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | System Transformation | Thermal headroom (MW) | 15.44 | 15.79 | 15.63 | 15.53 | 15.22 | 14.87 | 14.4 | 13.75 | 12.83 | 11.7 | 10.47 | 9.09 | 7.67 | 6.24 | 4.92 | -4.42 | -7.17 | -7.45
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | WPD Best View | Thermal headroom (MW) | 15.44 | 15.97 | 16.04 | 16.17 | 16.17 | 15.82 | 15.42 | 14.91 | 14.3 | 13.48 | 12.42 | 11.27 | 10.01 | 8.63 | 7.22 | -0.16 | -6.03 | -7.94
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Consumer Transformation | Thermal headroom (MW) | 98.14 | 97.69 | 96.98 | 95.98 | 94.51 | 92.56 | 90.37 | 88.1 | 85.73 | 82.92 | 78.08 | 71.01 | 63.54 | 56.3 | 49.24 | 11.03 | -13.57 | -24.96
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Leading the Way | Thermal headroom (MW) | 98.14 | 97.28 | 95.76 | 94.02 | 91.51 | 87.49 | 83.52 | 79.26 | 74.11 | 67.83 | 60.5 | 52.74 | 44.88 | 37.12 | 29.88 | 5.21 | -5.54 | -9.61
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Steady Progression | Thermal headroom (MW) | 98.14 | 98.99 | 99.22 | 99.32 | 99.32 | 98.75 | 98.05 | 97.25 | 96.27 | 94.98 | 93.13 | 91.19 | 89.11 | 86.93 | 84.34 | 68.62 | 55.21 | 49.48
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | System Transformation | Thermal headroom (MW) | 98.14 | 98.69 | 98.62 | 98.39 | 97.91 | 97.35 | 96.61 | 95.53 | 94.09 | 92.45 | 89.73 | 86.49 | 83.17 | 79.94 | 76.99 | 58.81 | 48.73 | 45.13
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | WPD Best View | Thermal headroom (MW) | 98.14 | 98.73 | 98.68 | 98.52 | 98.15 | 97.29 | 96.3 | 95.16 | 93.43 | 91.52 | 89.16 | 86.76 | 84.33 | 81.83 | 78.33 | 59.01 | 47.25 | 42.78
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Consumer Transformation | Thermal headroom (MW) | 36.89 | 35.85 | 34.38 | 32.55 | 29.88 | 26.67 | 22.82 | 18.87 | 13.86 | 7.71 | -4.65 | -17.11 | -29.75 | -42.03 | -54.3 | -112.02 | -158.03 | -183.82
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Leading the Way | Thermal headroom (MW) | 36.89 | 35.17 | 32.22 | 29.24 | 24.19 | 17.69 | 9.88 | 1.17 | -8.23 | -18.44 | -29.28 | -41.07 | -53.2 | -64.93 | -75.95 | -112.11 | -126.93 | -132.43
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Steady Progression | Thermal headroom (MW) | 36.89 | 37.52 | 37.32 | 36.96 | 36.39 | 35.18 | 33.93 | 32.51 | 31.01 | 28.32 | 24.59 | 21.8 | 17.81 | 13.05 | 8.27 | -21.25 | -39.69 | -47.16
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | System Transformation | Thermal headroom (MW) | 36.89 | 37.09 | 36.44 | 35.6 | 34.35 | 33.18 | 31.88 | 30.23 | 28.15 | 25.79 | 22.13 | 17.87 | 13.11 | 7.16 | 0.53 | -32.46 | -45.63 | -49.85
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | WPD Best View | Thermal headroom (MW) | 36.89 | 35.17 | 32.22 | 29.24 | 24.19 | 17.69 | 9.88 | 1.17 | -8.23 | -18.44 | -29.28 | -41.07 | -53.2 | -64.93 | -75.95 | -112.11 | -126.93 | -132.43
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Consumer Transformation | Thermal headroom (MW) | 20.34 | 18.76 | 16.96 | 14.28 | 11.33 | 7.9 | 4.59 | 1.56 | -1.44 | -4.7 | -14.93 | -27.16 | -39.41 | -51.46 | -63.62 | -106.45 | -164.84 | -207.22
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Leading the Way | Thermal headroom (MW) | 20.34 | 18.04 | 15.46 | 11.92 | 7.72 | 2.94 | -2.23 | -7.68 | -17.21 | -28.08 | -35.22 | -44.52 | -55.08 | -65.37 | -75.05 | -107.72 | -132.77 | -154.52
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Steady Progression | Thermal headroom (MW) | 20.34 | 20.22 | 19.91 | 19.08 | 18.3 | 17.07 | 15.72 | 14.34 | 12.93 | 8.1 | 1.84 | -0.41 | -2.9 | -6.42 | -9.2 | -26.24 | -38.53 | -43.34
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | System Transformation | Thermal headroom (MW) | 20.34 | 19.67 | 18.87 | 17.45 | 15.95 | 14.49 | 12.51 | 10.48 | 8.26 | 6.07 | 1.98 | -0.68 | -4.62 | -7.88 | -11.76 | -36.11 | -51.36 | -57.62
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | WPD Best View | Thermal headroom (MW) | 20.34 | 20.21 | 19.89 | 19.04 | 18.24 | 17.02 | 15.67 | 14.3 | 12.88 | 8.06 | 1.82 | -0.42 | -2.91 | -6.42 | -9.18 | -26.2 | -38.57 | -43.42
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Consumer Transformation | Thermal headroom (MW) | 11.33 | 10.7 | 9.93 | 8.99 | 7.52 | 5.49 | 3.63 | 1.69 | -0.27 | -2.75 | -6.05 | -10.71 | -15.34 | -19.79 | -24.11 | -47.7 | -61.81 | -69.12
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Leading the Way | Thermal headroom (MW) | 11.33 | 10.62 | 9.36 | 7.99 | 5.93 | 2.76 | -0.13 | -3.26 | -7.06 | -11.7 | -16.61 | -21.66 | -26.56 | -31.26 | -35.6 | -50.91 | -57.9 | -61.45
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Steady Progression | Thermal headroom (MW) | 11.33 | 11.64 | 11.53 | 11.44 | 11.08 | 10.37 | 9.68 | 8.87 | 7.97 | 6.97 | 5.63 | 4.29 | 2.84 | 1.34 | -0.5 | -11.27 | -19.55 | -22.97
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | System Transformation | Thermal headroom (MW) | 11.33 | 11.45 | 11.14 | 10.82 | 10.08 | 9.38 | 8.65 | 7.58 | 6.26 | 5.03 | 2.99 | 0.9 | -1.18 | -3.21 | -5.06 | -17.75 | -25.37 | -28.84
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | WPD Best View | Thermal headroom (MW) | 11.33 | 11.03 | 10.28 | 9.44 | 8.05 | 6.11 | 4.08 | 1.82 | -0.76 | -3.76 | -7.7 | -11.71 | -15.66 | -19.53 | -23.14 | -37.32 | -43.9 | -46.38
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Consumer Transformation | Thermal headroom (MW) | 36.1 | 35.7 | 34.86 | 33.85 | 32.38 | 30.04 | 27.97 | 25.78 | 23.12 | 19.72 | 14.41 | 8.96 | 3.48 | -1.83 | -6.93 | -29.84 | -42.89 | -48.06
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Leading the Way | Thermal headroom (MW) | 36.1 | 34.72 | 32.95 | 31.05 | 28.42 | 25.05 | 22.05 | 18.69 | 14.66 | 9.77 | 4.42 | -1.18 | -6.79 | -12.19 | -17.16 | -32.1 | -36.59 | -35.93
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Steady Progression | Thermal headroom (MW) | 36.1 | 36.56 | 36.63 | 36.6 | 36.45 | 35.66 | 34.99 | 34.23 | 33.26 | 31.95 | 30.51 | 28.94 | 27.24 | 25.43 | 23.4 | 8.66 | -2.23 | -6.56
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | System Transformation | Thermal headroom (MW) | 36.1 | 36.23 | 35.94 | 35.61 | 34.98 | 34.19 | 33.55 | 32.68 | 31.32 | 29.53 | 27.7 | 25.29 | 22.55 | 19.61 | 16.54 | 0.33 | -5.9 | -7.22
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | WPD Best View | Thermal headroom (MW) | 36.1 | 36.2 | 35.91 | 35.43 | 34.72 | 33.27 | 32.01 | 30.64 | 29 | 26.85 | 23.6 | 20.21 | 16.75 | 13.19 | 9.61 | -9.18 | -21.84 | -26.97
Willenhall 132kV | Wolverhampton 132 11 (GT1A) | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Consumer Transformation | Thermal headroom (MW) | 24.3 | 23.85 | 22.84 | 21.58 | 20.03 | 18.28 | 16.18 | 13.84 | 11.1 | 7.79 | 1.53 | -4.79 | -10.98 | -16.91 | -22.77 | -40.44 | -60.4 | -73.67
Willenhall 132kV | Wolverhampton 132 11 (GT1A) | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Leading the Way | Thermal headroom (MW) | 24.3 | 23.7 | 21.79 | 20.06 | 17.76 | 15.64 | 13.04 | 9.85 | 5.63 | 0.79 | -3.78 | -8.71 | -13.72 | -18.46 | -22.69 | -31.6 | -33.11 | -31.22
Willenhall 132kV | Wolverhampton 132 11 (GT1A) | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Steady Progression | Thermal headroom (MW) | 24.3 | 24.9 | 24.84 | 24.75 | 24.56 | 24.2 | 23.84 | 23.39 | 22.74 | 21.17 | 19.07 | 17.92 | 16.19 | 14.03 | 12.02 | -0.54 | -9.59 | -11.51
Willenhall 132kV | Wolverhampton 132 11 (GT1A) | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | System Transformation | Thermal headroom (MW) | 24.3 | 24.64 | 24.29 | 23.92 | 23.35 | 22.87 | 22.38 | 21.64 | 20.62 | 19.41 | 17.39 | 15.12 | 12.63 | 9.82 | 6.5 | -7.71 | -10.68 | -8.86
Willenhall 132kV | Wolverhampton 132 11 (GT1A) | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | WPD Best View | Thermal headroom (MW) | 24.3 | 23.85 | 22.84 | 21.58 | 20.03 | 18.28 | 16.18 | 13.84 | 11.1 | 7.79 | 1.53 | -4.79 | -10.98 | -16.91 | -22.77 | -40.44 | -60.4 | -73.67
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Consumer Transformation | Thermal headroom (MW) | 16.8 | 16.7454 | 16.6256 | 16.4765 | 16.2913 | 16.084 | 15.8338 | 15.5558 | 15.2291 | 14.836 | 14.0915 | 13.3406 | 12.6037 | 11.8984 | 11.2021 | 9.1002 | 6.7271 | 5.1484
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Leading the Way | Thermal headroom (MW) | 16.8 | 16.7277 | 16.501 | 16.295 | 16.0214 | 15.7698 | 15.4603 | 15.0805 | 14.5789 | 14.0041 | 13.4596 | 12.8735 | 12.2784 | 11.7142 | 11.2114 | 10.1516 | 9.972 | 10.1969
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Steady Progression | Thermal headroom (MW) | 16.8 | 16.8709 | 16.8633 | 16.8526 | 16.8298 | 16.7879 | 16.7448 | 16.6912 | 16.6143 | 16.4275 | 16.1777 | 16.0405 | 15.8353 | 15.5779 | 15.3387 | 13.8459 | 12.7688 | 12.5409
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | System Transformation | Thermal headroom (MW) | 16.8 | 16.8403 | 16.7979 | 16.7541 | 16.6859 | 16.6297 | 16.5717 | 16.4829 | 16.3618 | 16.2173 | 15.9772 | 15.708 | 15.4111 | 15.0775 | 14.6829 | 12.9927 | 12.6397 | 12.8559
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | WPD Best View | Thermal headroom (MW) | 16.8 | 16.7454 | 16.6256 | 16.4765 | 16.2913 | 16.084 | 15.8338 | 15.5558 | 15.2291 | 14.836 | 14.0915 | 13.3406 | 12.6037 | 11.8984 | 11.2021 | 9.1002 | 6.7271 | 5.1484

## Generation headroom
Associated GSP Group | Bulk Supply Point | Substation | Supply Level | Voltage Level (kV) | Latitude | Longitude | Scenario | Units | Limiting constraint | 0 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2040 | 2045 | 2050
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Consumer Transformation | Headroom (MW) | Thermal | 1.29 | 1.21 | 1.15 | 1.09 | 0.9 | 0.74 | 0.63 | 0.43 | 0.2 | -0.02 | -0.23 | -0.41 | -0.59 | -0.78 | -1.04 | -1.94 | -3.78 | -4.8
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Leading the Way | Headroom (MW) | Thermal | 1.29 | 1.2 | 1.15 | 1.07 | 0.86 | 0.69 | 0.57 | 0.38 | 0.16 | -0.06 | -0.27 | -0.45 | -0.63 | -0.75 | -0.87 | -1.98 | -5.11 | -6.76
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | Steady Progression | Headroom (MW) | N/A | 1.29 | 1.23 | 1.21 | 1.18 | 1.14 | 1.11 | 1.07 | 1.04 | 1.01 | 0.98 | 0.96 | 0.93 | 0.91 | 0.89 | 0.88 | 0.93 | 0.83 | 0.62
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | System Transformation | Headroom (MW) | Thermal | 1.29 | 1.22 | 1.19 | 1.14 | 1.05 | 0.97 | 0.9 | 0.84 | 0.72 | 0.59 | 0.48 | 0.41 | 0.36 | 0.31 | 0.19 | 0.04 | -1.26 | -1.69
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BODENHAM 66 11kV S STN | Primary | 11 | -2.6766 | 52.1488 | WPD Best View | Headroom (MW) | Thermal | 1.29 | 1.21 | 1.15 | 1.09 | 0.9 | 0.74 | 0.63 | 0.43 | 0.2 | -0.02 | -0.23 | -0.41 | -0.59 | -0.78 | -1.04 | -1.94 | -3.78 | -4.8
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Consumer Transformation | Headroom (MW) | Thermal | 5.85 | 5.74 | 5.66 | 5.56 | 5.23 | 4.85 | 4.43 | 3.43 | 2.29 | 1.03 | -0.37 | -1.88 | -3.47 | -4.94 | -6.72 | -11.14 | -16.01 | -21.72
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Leading the Way | Headroom (MW) | Thermal | 5.85 | 5.72 | 5.64 | 5.54 | 5.13 | 4.71 | 4.24 | 3.74 | 3.24 | 2.71 | 2.16 | 1.65 | 0.29 | -0.98 | -2.33 | -7.18 | -13.15 | -17.45
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | Steady Progression | Headroom (MW) | Thermal | 5.85 | 5.79 | 5.76 | 5.73 | 5.68 | 5.61 | 5.54 | 5.32 | 5.11 | 4.85 | 4.56 | 4.23 | 3.52 | 2.84 | 1.95 | 0.74 | -0.56 | -2.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | System Transformation | Headroom (MW) | Thermal | 5.85 | 5.76 | 5.71 | 5.66 | 5.5 | 5.39 | 5.24 | 4.43 | 3.38 | 2.38 | 1.22 | -0.05 | -1.37 | -2.55 | -4.04 | -6.44 | -9.94 | -14.09
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | BROMYARD 66/11kV | Primary | 11 | -2.5004 | 52.1861 | WPD Best View | Headroom (MW) | Thermal | 5.85 | 5.74 | 5.66 | 5.56 | 5.23 | 4.86 | 4.44 | 3.45 | 2.33 | 1.09 | -0.3 | -1.8 | -3.37 | -4.83 | -6.59 | -10.99 | -15.85 | -21.54
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Consumer Transformation | Headroom (MW) | Thermal | 1.13 | 1.07 | 1.02 | 0.97 | 0.82 | 0.71 | 0.59 | 0.46 | 0.33 | 0.22 | 0.1 | 0 | -0.11 | -0.22 | -0.35 | -1.12 | -1.93 | -2.84
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Leading the Way | Headroom (MW) | Thermal | 1.13 | 1.07 | 1.02 | 0.96 | 0.79 | 0.68 | 0.55 | 0.42 | 0.3 | 0.18 | 0.05 | -0.07 | -0.18 | -0.31 | -0.44 | -1.3 | -2.25 | -3.47
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | Steady Progression | Headroom (MW) | N/A | 1.13 | 1.09 | 1.07 | 1.06 | 1.03 | 1 | 0.98 | 0.94 | 0.91 | 0.89 | 0.86 | 0.84 | 0.83 | 0.82 | 0.81 | 0.83 | 0.75 | 0.55
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | System Transformation | Headroom (MW) | Thermal | 1.13 | 1.08 | 1.05 | 1.02 | 0.95 | 0.89 | 0.82 | 0.75 | 0.68 | 0.61 | 0.55 | 0.51 | 0.47 | 0.43 | 0.38 | 0.2 | -0.19 | -0.56
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | DYMOCK 66 11kV S STN | Primary | 11 | -2.4494 | 51.9703 | WPD Best View | Headroom (MW) | Thermal | 1.13 | 1.09 | 1.06 | 1.02 | 0.95 | 0.89 | 0.83 | 0.76 | 0.69 | 0.63 | 0.57 | 0.52 | 0.47 | 0.41 | 0.36 | 0.11 | -0.26 | -0.73
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Consumer Transformation | Headroom (MW) | Thermal | 3.38 | 3.31 | 3.25 | 3.18 | 2.99 | 2.65 | 2.3 | 1.39 | 0.36 | -0.81 | -2.35 | -4.07 | -5.88 | -7.52 | -9.49 | -14 | -19.38 | -25.78
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Leading the Way | Headroom (MW) | Thermal | 3.38 | 3.3 | 3.24 | 3.16 | 2.95 | 2.56 | 2.16 | 1.76 | 1.37 | 0.98 | 0.56 | 0.16 | -1.33 | -2.73 | -4.17 | -9.13 | -15.64 | -19.38
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | Steady Progression | Headroom (MW) | Thermal | 3.38 | 3.33 | 3.31 | 3.29 | 3.26 | 3.19 | 3.13 | 2.92 | 2.71 | 2.46 | 2.13 | 1.72 | 0.84 | -0.02 | -1.15 | -2.7 | -4.42 | -6.28
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | System Transformation | Headroom (MW) | Thermal | 3.38 | 3.32 | 3.28 | 3.24 | 3.16 | 3.08 | 2.98 | 2.21 | 1.16 | 0.21 | -1.15 | -2.68 | -4.3 | -5.73 | -7.49 | -10.36 | -14.62 | -19.74
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KENSWICK 66 11kV S STN | Primary | 11 | -2.3109 | 52.228 | WPD Best View | Headroom (MW) | Thermal | 3.38 | 3.33 | 3.31 | 3.29 | 3.26 | 3.18 | 3.1 | 2.87 | 2.65 | 2.38 | 2.02 | 1.6 | 0.69 | -0.19 | -1.34 | -2.94 | -4.69 | -6.59
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Consumer Transformation | Headroom (MW) | Thermal | 0.335 | 0.225 | 0.155 | 0.075 | -0.235 | -0.455 | -0.765 | -1.155 | -1.525 | -1.885 | -2.205 | -2.505 | -2.805 | -3.105 | -3.425 | -4.915 | -6.525 | -8.295
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Leading the Way | Headroom (MW) | Thermal | 0.335 | 0.215 | 0.135 | 0.045 | -0.305 | -0.545 | -0.865 | -1.205 | -1.535 | -1.895 | -2.235 | -2.555 | -2.885 | -3.195 | -3.495 | -5.045 | -6.855 | -9.115
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | Steady Progression | Headroom (MW) | Thermal | 0.335 | 0.265 | 0.235 | 0.195 | 0.135 | 0.085 | 0.005 | -0.075 | -0.155 | -0.265 | -0.345 | -0.395 | -0.435 | -0.465 | -0.495 | -0.545 | -0.685 | -1.015
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | System Transformation | Headroom (MW) | Thermal | 0.335 | 0.245 | 0.195 | 0.145 | -0.005 | -0.115 | -0.265 | -0.445 | -0.645 | -0.835 | -1.005 | -1.135 | -1.235 | -1.335 | -1.475 | -1.805 | -2.485 | -3.205
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KINGTON 66 11kV S STN | Primary | 11 | -3.0075 | 52.2121 | WPD Best View | Headroom (MW) | Thermal | 0.335 | 0.225 | 0.155 | 0.065 | -0.245 | -0.455 | -0.765 | -1.115 | -1.445 | -1.785 | -2.105 | -2.405 | -2.695 | -2.995 | -3.325 | -4.785 | -6.305 | -8.065
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Consumer Transformation | Headroom (MW) | Thermal | 1.91 | 1.86 | 1.89 | 1.85 | 1.71 | 1.61 | 1.52 | 1.42 | 1.32 | 1.23 | 1.14 | 1.07 | 0.99 | 0.9 | 0.8 | -0.03 | -0.97 | -1.81
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Leading the Way | Headroom (MW) | Thermal | 1.91 | 1.85 | 1.89 | 1.84 | 1.68 | 1.58 | 1.47 | 1.37 | 1.28 | 1.19 | 1.1 | 1.02 | 0.93 | 0.83 | 0.72 | -0.17 | -1.16 | -2.24
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | Steady Progression | Headroom (MW) | N/A | 1.91 | 1.87 | 1.92 | 1.9 | 1.87 | 1.85 | 1.82 | 1.8 | 1.77 | 1.75 | 1.72 | 1.7 | 1.68 | 1.67 | 1.65 | 1.64 | 1.57 | 1.39
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | System Transformation | Headroom (MW) | N/A | 1.91 | 1.87 | 1.91 | 1.88 | 1.81 | 1.76 | 1.71 | 1.65 | 1.6 | 1.54 | 1.5 | 1.46 | 1.43 | 1.4 | 1.36 | 1.12 | 0.68 | 0.29
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | KNIGHTON 66 11kV S STN | Primary | 11 | -3.042 | 52.3367 | WPD Best View | Headroom (MW) | Thermal | 1.91 | 1.86 | 1.9 | 1.86 | 1.74 | 1.65 | 1.57 | 1.49 | 1.41 | 1.34 | 1.27 | 1.21 | 1.15 | 1.08 | 1 | 0.34 | -0.46 | -1.25
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Consumer Transformation | Headroom (MW) | Thermal | 7.48 | 7.35 | 7.27 | 7.16 | 6.76 | 6.35 | 5.9 | 5.21 | 4.48 | 3.73 | 2.92 | 2.08 | 1.22 | 0.39 | -0.59 | -4.02 | -7.96 | -12.41
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Leading the Way | Headroom (MW) | Thermal | 7.48 | 7.34 | 7.26 | 7.15 | 6.69 | 6.25 | 5.76 | 5.25 | 4.76 | 4.27 | 3.77 | 3.29 | 2.49 | 1.73 | 0.91 | -2.88 | -7.53 | -12.15
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | Steady Progression | Headroom (MW) | N/A | 7.48 | 7.41 | 7.41 | 7.41 | 7.39 | 7.32 | 7.24 | 7.1 | 6.97 | 6.81 | 6.64 | 6.48 | 6.17 | 5.87 | 5.5 | 5.01 | 4.3 | 3.22
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | System Transformation | Headroom (MW) | Thermal | 7.48 | 7.39 | 7.36 | 7.32 | 7.17 | 7.02 | 6.82 | 6.33 | 5.76 | 5.24 | 4.65 | 4.04 | 3.42 | 2.87 | 2.18 | 0.87 | -1.5 | -4.12
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEDBURY 66/11kV | Primary | 11 | -2.427 | 52.0463 | WPD Best View | Headroom (MW) | Thermal | 7.48 | 7.35 | 7.27 | 7.16 | 6.76 | 6.35 | 5.91 | 5.23 | 4.52 | 3.78 | 2.99 | 2.16 | 1.32 | 0.51 | -0.46 | -3.86 | -7.79 | -12.23
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Consumer Transformation | Headroom (MW) | N/A | 19.61 | 19.42 | 19.16 | 18.99 | 18.46 | 18 | 17.51 | 16.97 | 16.41 | 15.86 | 15.31 | 14.77 | 14.29 | 13.79 | 13.21 | 10.16 | 6.79 | 3.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Leading the Way | Headroom (MW) | N/A | 19.61 | 19.4 | 19.13 | 18.95 | 18.32 | 17.83 | 17.31 | 16.75 | 16.18 | 15.58 | 14.97 | 14.37 | 13.83 | 13.32 | 12.77 | 9.57 | 5.67 | 0.91
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | Steady Progression | Headroom (MW) | N/A | 19.61 | 19.49 | 19.44 | 19.39 | 19.29 | 19.2 | 19.13 | 19.03 | 18.93 | 18.83 | 18.74 | 18.66 | 18.59 | 18.52 | 18.46 | 18.34 | 18 | 17.31
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | System Transformation | Headroom (MW) | N/A | 19.61 | 19.46 | 19.37 | 19.15 | 18.9 | 18.72 | 18.5 | 18.19 | 17.84 | 17.56 | 17.27 | 17.01 | 16.82 | 16.62 | 16.38 | 15.64 | 13.92 | 12.16
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LEOMINSTER 66 11kV S STN | Primary | 11 | -2.761 | 52.2288 | WPD Best View | Headroom (MW) | N/A | 19.61 | 19.42 | 19.16 | 18.99 | 18.46 | 18 | 17.51 | 16.97 | 16.41 | 15.86 | 15.31 | 14.77 | 14.29 | 13.79 | 13.21 | 10.16 | 6.79 | 3.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Consumer Transformation | Headroom (MW) | Thermal | 1.54 | 1.49 | 1.45 | 1.41 | 1.24 | 1.11 | 0.93 | 0.68 | 0.43 | 0.18 | -0.08 | -0.31 | -0.54 | -0.78 | -1.1 | -2.01 | -2.88 | -3.85
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Leading the Way | Headroom (MW) | Thermal | 1.54 | 1.48 | 1.44 | 1.4 | 1.21 | 1.07 | 0.88 | 0.64 | 0.4 | 0.13 | -0.15 | -0.42 | -0.68 | -0.91 | -1.17 | -2.24 | -3.48 | -4.93
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | Steady Progression | Headroom (MW) | N/A | 1.54 | 1.51 | 1.49 | 1.47 | 1.44 | 1.41 | 1.38 | 1.33 | 1.29 | 1.25 | 1.21 | 1.19 | 1.18 | 1.17 | 1.16 | 1.14 | 1.07 | 0.89
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | System Transformation | Headroom (MW) | Thermal | 1.54 | 1.5 | 1.47 | 1.45 | 1.36 | 1.29 | 1.19 | 1.05 | 0.92 | 0.78 | 0.64 | 0.55 | 0.48 | 0.4 | 0.24 | 0.04 | -0.33 | -0.71
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | LOWER CHADNOR 66 11kV S STN | Primary | 11 | -2.8424 | 52.1693 | WPD Best View | Headroom (MW) | Thermal | 1.54 | 1.49 | 1.45 | 1.41 | 1.24 | 1.11 | 0.93 | 0.68 | 0.43 | 0.18 | -0.08 | -0.31 | -0.54 | -0.78 | -1.1 | -2.01 | -2.88 | -3.85
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Consumer Transformation | Headroom (MW) | N/A | 5.425 | 5.365 | 5.325 | 5.285 | 5.145 | 5.055 | 4.965 | 4.875 | 4.785 | 4.695 | 4.615 | 4.545 | 4.465 | 4.395 | 4.305 | 3.785 | 3.165 | 2.505
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Leading the Way | Headroom (MW) | N/A | 5.425 | 5.365 | 5.325 | 5.275 | 5.105 | 5.015 | 4.925 | 4.825 | 4.745 | 4.655 | 4.565 | 4.485 | 4.405 | 4.325 | 4.235 | 3.685 | 3.005 | 2.145
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | Steady Progression | Headroom (MW) | N/A | 5.425 | 5.385 | 5.375 | 5.345 | 5.315 | 5.285 | 5.255 | 5.235 | 5.205 | 5.175 | 5.145 | 5.125 | 5.105 | 5.085 | 5.065 | 5.005 | 4.915 | 4.755
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | System Transformation | Headroom (MW) | N/A | 5.425 | 5.385 | 5.355 | 5.325 | 5.245 | 5.195 | 5.145 | 5.085 | 5.035 | 4.975 | 4.935 | 4.895 | 4.865 | 4.825 | 4.795 | 4.655 | 4.345 | 4.045
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | MADLEY 66 11kV S STN | Primary | 11 | -2.8486 | 52.0363 | WPD Best View | Headroom (MW) | N/A | 5.425 | 5.365 | 5.325 | 5.285 | 5.145 | 5.055 | 4.965 | 4.875 | 4.785 | 4.695 | 4.615 | 4.545 | 4.465 | 4.395 | 4.305 | 3.785 | 3.165 | 2.505
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Consumer Transformation | Headroom (MW) | Thermal | 2.47 | 2.32 | 2.22 | 2.1 | 1.7 | 1.42 | 1.04 | -0.29 | -1.81 | -3.56 | -5.47 | -7.61 | -9.86 | -11.9 | -14.38 | -19.95 | -27.92 | -35.37
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Leading the Way | Headroom (MW) | Thermal | 2.47 | 2.31 | 2.2 | 2.07 | 1.58 | 1.3 | 0.86 | 0.44 | 0.08 | -0.32 | -0.72 | -5.86 | -7.66 | -9.36 | -11.14 | -17.14 | -28 | -32.58
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | Steady Progression | Headroom (MW) | Thermal | 2.47 | 2.38 | 2.34 | 2.31 | 2.23 | 2.22 | 2.16 | 1.85 | 1.57 | 1.18 | 0.77 | 0.27 | -0.86 | -1.95 | -3.38 | -5.22 | -7.12 | -9.26
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | System Transformation | Headroom (MW) | Thermal | 2.47 | 2.36 | 2.29 | 2.22 | 2.03 | 1.97 | 1.81 | 0.66 | -0.8 | -2.37 | -4.08 | -6.02 | -8.05 | -9.85 | -12.07 | -15.5 | -21.76 | -27.28
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | NEWENT 66 11kV S STN | Primary | 11 | -2.3802 | 51.9289 | WPD Best View | Headroom (MW) | Thermal | 2.47 | 2.38 | 2.33 | 2.28 | 2.17 | 2.14 | 2.05 | 1.63 | 1.21 | 0.67 | 0.18 | -0.41 | -1.61 | -2.76 | -4.25 | -6.33 | -8.45 | -10.79
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Consumer Transformation | Headroom (MW) | Thermal | 3.41 | 3.35 | 3.3 | 3.25 | 3.09 | 2.96 | 2.79 | 2.58 | 2.38 | 2.18 | 1.99 | 1.81 | 1.64 | 1.45 | 1.21 | 0.3 | -0.63 | -1.68
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Leading the Way | Headroom (MW) | Thermal | 3.41 | 3.34 | 3.3 | 3.24 | 3.05 | 2.91 | 2.74 | 2.54 | 2.36 | 2.15 | 1.94 | 1.74 | 1.54 | 1.36 | 1.14 | 0.1 | -1.12 | -2.62
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | Steady Progression | Headroom (MW) | N/A | 3.41 | 3.37 | 3.35 | 3.33 | 3.3 | 3.27 | 3.24 | 3.2 | 3.16 | 3.13 | 3.1 | 3.08 | 3.07 | 3.06 | 3.05 | 3.07 | 3 | 2.8
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | System Transformation | Headroom (MW) | N/A | 3.41 | 3.36 | 3.33 | 3.3 | 3.22 | 3.15 | 3.06 | 2.95 | 2.85 | 2.74 | 2.63 | 2.56 | 2.51 | 2.45 | 2.33 | 2.15 | 1.73 | 1.31
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PETERCHURCH 66 11kV S STN | Primary | 11 | -2.9543 | 52.0422 | WPD Best View | Headroom (MW) | Thermal | 3.41 | 3.35 | 3.3 | 3.25 | 3.09 | 2.96 | 2.79 | 2.58 | 2.38 | 2.18 | 1.99 | 1.81 | 1.64 | 1.45 | 1.21 | 0.3 | -0.63 | -1.68
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Consumer Transformation | Headroom (MW) | Thermal | 6.57 | 6.51 | 6.48 | 6.44 | 6.31 | 6.23 | 6.11 | 5.24 | 4.18 | 2.93 | 1.51 | -0.12 | -1.85 | -3.39 | -5.25 | -8.29 | -11.7 | -15.93
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Leading the Way | Headroom (MW) | Thermal | 6.57 | 6.51 | 6.47 | 6.43 | 6.29 | 6.19 | 6.06 | 5.92 | 5.78 | 5.64 | 5.51 | 5.39 | 4.07 | 2.86 | 1.63 | -1.76 | -6.19 | -7.52
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | Steady Progression | Headroom (MW) | Thermal | 6.57 | 6.53 | 6.51 | 6.49 | 6.46 | 6.43 | 6.4 | 6.18 | 5.96 | 5.68 | 5.36 | 4.96 | 4.02 | 3.11 | 1.9 | 0.33 | -1.19 | -2.76
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | System Transformation | Headroom (MW) | Thermal | 6.57 | 6.52 | 6.49 | 6.47 | 6.4 | 6.35 | 6.29 | 5.47 | 4.42 | 3.22 | 1.84 | 0.27 | -1.4 | -2.87 | -4.7 | -7.27 | -10.35 | -14.22
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PONTRILAS 66 11kV S STN | Primary | 11 | -2.8729 | 51.9424 | WPD Best View | Headroom (MW) | Thermal | 6.57 | 6.51 | 6.48 | 6.44 | 6.31 | 6.23 | 6.11 | 5.24 | 4.18 | 2.93 | 1.51 | -0.12 | -1.85 | -3.39 | -5.25 | -8.29 | -11.7 | -15.93
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Consumer Transformation | Headroom (MW) | N/A | 4.91 | 4.82 | 4.77 | 4.72 | 4.58 | 4.48 | 4.37 | 4.24 | 4.11 | 3.99 | 3.87 | 3.75 | 3.64 | 3.52 | 3.45 | 2.89 | 2.23 | 1.51
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Leading the Way | Headroom (MW) | N/A | 4.91 | 4.82 | 4.76 | 4.71 | 4.55 | 4.44 | 4.32 | 4.19 | 4.07 | 3.94 | 3.81 | 3.68 | 3.56 | 3.44 | 3.35 | 2.78 | 2.06 | 1.16
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | Steady Progression | Headroom (MW) | N/A | 4.91 | 4.84 | 4.81 | 4.78 | 4.74 | 4.7 | 4.66 | 4.62 | 4.57 | 4.53 | 4.49 | 4.46 | 4.43 | 4.41 | 4.38 | 4.29 | 4.17 | 3.97
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | System Transformation | Headroom (MW) | N/A | 4.91 | 4.83 | 4.79 | 4.75 | 4.68 | 4.62 | 4.56 | 4.48 | 4.4 | 4.32 | 4.25 | 4.19 | 4.14 | 4.09 | 4.06 | 3.89 | 3.53 | 3.17
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | PRESTEIGNE 66 11kV S STN | Primary | 11 | -2.9883 | 52.2648 | WPD Best View | Headroom (MW) | N/A | 4.91 | 4.82 | 4.77 | 4.72 | 4.56 | 4.46 | 4.35 | 4.22 | 4.09 | 3.97 | 3.85 | 3.73 | 3.61 | 3.49 | 3.41 | 2.84 | 2.15 | 1.33
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Consumer Transformation | Headroom (MW) | Thermal | 10.06 | 9.84 | 9.71 | 9.54 | 9.05 | 8.55 | 8.03 | 7.38 | 6.7 | 6.03 | 5.45 | 4.89 | 4.34 | 3.76 | 3.08 | -0.3 | -4.04 | -8.16
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Leading the Way | Headroom (MW) | Thermal | 10.06 | 9.82 | 9.68 | 9.5 | 8.93 | 8.39 | 7.83 | 7.26 | 6.7 | 6.15 | 5.58 | 5.04 | 4.43 | 3.81 | 3.1 | -0.57 | -4.84 | -10.08
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | Steady Progression | Headroom (MW) | N/A | 10.06 | 9.91 | 9.86 | 9.81 | 9.73 | 9.64 | 9.54 | 9.4 | 9.28 | 9.14 | 9.03 | 8.93 | 8.82 | 8.72 | 8.62 | 8.49 | 8.12 | 7.37
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | System Transformation | Headroom (MW) | N/A | 10.06 | 9.88 | 9.79 | 9.7 | 9.48 | 9.3 | 9.08 | 8.66 | 8.14 | 7.73 | 7.4 | 7.11 | 6.84 | 6.58 | 6.26 | 5.34 | 3.42 | 1.43
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ROSS ON WYE 66 11kV S STN | Primary | 11 | -2.5896 | 51.9216 | WPD Best View | Headroom (MW) | Thermal | 10.06 | 9.84 | 9.71 | 9.54 | 9.05 | 8.55 | 8.03 | 7.38 | 6.7 | 6.03 | 5.45 | 4.89 | 4.34 | 3.76 | 3.08 | -0.3 | -4.04 | -8.16
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Consumer Transformation | Headroom (MW) | Thermal | 1.27 | 1.2 | 1.15 | 1.1 | 0.93 | 0.66 | 0.45 | -0.26 | -1.05 | -1.93 | -2.89 | -3.93 | -5.01 | -6.01 | -7.25 | -10.16 | -13.31 | -16.98
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Leading the Way | Headroom (MW) | Thermal | 1.27 | 1.19 | 1.15 | 1.09 | 0.9 | 0.59 | 0.34 | -0.05 | -0.44 | -0.84 | -1.25 | -1.65 | -2.57 | -3.4 | -4.21 | -7.56 | -11.61 | -14.44
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | Steady Progression | Headroom (MW) | Thermal | 1.27 | 1.22 | 1.2 | 1.18 | 1.15 | 1.1 | 1.07 | 0.96 | 0.85 | 0.7 | 0.5 | 0.28 | -0.17 | -0.61 | -1.19 | -2.01 | -2.88 | -3.83
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | System Transformation | Headroom (MW) | Thermal | 1.27 | 1.21 | 1.18 | 1.15 | 1.06 | 0.98 | 0.98 | 0.41 | -0.33 | -1 | -1.77 | -2.6 | -3.45 | -4.23 | -5.23 | -6.76 | -8.98 | -11.67
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | ST WEONARDS 66 11kV S STN | Primary | 11 | -2.7288 | 51.9096 | WPD Best View | Headroom (MW) | Thermal | 1.27 | 1.2 | 1.15 | 1.1 | 0.93 | 0.66 | 0.45 | -0.26 | -1.05 | -1.93 | -2.89 | -3.93 | -5.01 | -6.01 | -7.25 | -10.16 | -13.31 | -16.98
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Consumer Transformation | Headroom (MW) | N/A | 6.6 | 6.53 | 6.48 | 6.42 | 6.23 | 6.11 | 5.98 | 5.83 | 5.69 | 5.56 | 5.44 | 5.32 | 5.21 | 5.09 | 4.96 | 4.22 | 3.33 | 2.34
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Leading the Way | Headroom (MW) | N/A | 6.6 | 6.52 | 6.47 | 6.4 | 6.19 | 6.06 | 5.92 | 5.78 | 5.64 | 5.51 | 5.37 | 5.25 | 5.12 | 5 | 4.87 | 4.05 | 3.01 | 1.67
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | Steady Progression | Headroom (MW) | N/A | 6.6 | 6.55 | 6.53 | 6.51 | 6.46 | 6.43 | 6.4 | 6.36 | 6.32 | 6.29 | 6.25 | 6.23 | 6.22 | 6.2 | 6.19 | 6.18 | 6.1 | 5.9
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | System Transformation | Headroom (MW) | N/A | 6.6 | 6.54 | 6.51 | 6.47 | 6.38 | 6.31 | 6.23 | 6.15 | 6.07 | 6 | 5.93 | 5.88 | 5.83 | 5.79 | 5.75 | 5.6 | 5.19 | 4.76
Bishops Wood 132kV | Hereford (Bishops Wood) & Ludlow 132 66 | WOOFFERTON 66 11kV S STN | Primary | 11 | -2.7271 | 52.3073 | WPD Best View | Headroom (MW) | N/A | 6.6 | 6.53 | 6.48 | 6.42 | 6.25 | 6.13 | 6.01 | 5.89 | 5.78 | 5.67 | 5.57 | 5.48 | 5.4 | 5.31 | 5.21 | 4.55 | 3.71 | 2.77
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Consumer Transformation | Headroom (MW) | Thermal | 3.75 | 3.68 | 3.63 | 3.58 | 3.24 | 3.13 | 3.01 | 2.89 | 2.78 | 2.68 | 2.58 | 2.49 | 2.39 | 2.3 | 2.18 | 1.36 | 0.45 | -0.53
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Leading the Way | Headroom (MW) | Thermal | 3.75 | 3.67 | 3.63 | 3.57 | 3.37 | 3.08 | 2.96 | 2.84 | 2.73 | 2.63 | 2.52 | 2.42 | 2.32 | 2.21 | 2.06 | 1.18 | 0.18 | -1.08
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | Steady Progression | Headroom (MW) | N/A | 3.75 | 3.7 | 3.68 | 3.66 | 3.63 | 3.6 | 3.57 | 3.54 | 3.51 | 3.48 | 3.45 | 3.43 | 3.41 | 3.39 | 3.37 | 3.32 | 3.21 | 2.98
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | System Transformation | Headroom (MW) | N/A | 3.75 | 3.69 | 3.66 | 3.63 | 3.55 | 3.49 | 3.43 | 3.36 | 3.3 | 3.08 | 3.02 | 2.97 | 2.93 | 2.9 | 2.85 | 2.62 | 2.17 | 1.74
Bishops Wood 132kV | Ludlow 132 33 | BISHOPS CASTLE 33 11kV S STN | Primary | 11 | -2.9945 | 52.4916 | WPD Best View | Headroom (MW) | N/A | 3.75 | 3.69 | 3.66 | 3.63 | 3.55 | 3.49 | 3.43 | 3.36 | 3.3 | 3.08 | 3.02 | 2.97 | 2.93 | 2.9 | 2.85 | 2.62 | 2.17 | 1.74
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Consumer Transformation | Headroom (MW) | Thermal | 2.57 | 2.5 | 2.45 | 2.38 | 2.18 | 2.03 | 1.64 | 1.01 | 0.51 | 0.04 | -0.62 | -1.27 | -1.94 | -2.6 | -3.35 | -6.31 | -10.09 | -14.21
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Leading the Way | Headroom (MW) | Thermal | 2.57 | 2.5 | 2.44 | 2.37 | 2.15 | 2 | 1.58 | 1.22 | 0.93 | 0.54 | 0.17 | -0.17 | -0.72 | -1.26 | -1.85 | -4.53 | -8.15 | -11.49
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | Steady Progression | Headroom (MW) | Thermal | 2.57 | 2.53 | 2.51 | 2.49 | 2.46 | 2.43 | 2.4 | 2.36 | 2.28 | 1.99 | 1.88 | 1.75 | 1.52 | 1.34 | 1.13 | 0.85 | 0.34 | -0.27
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | System Transformation | Headroom (MW) | Thermal | 2.57 | 2.52 | 2.48 | 2.45 | 2.36 | 2.29 | 2.21 | 2.09 | 1.76 | 1.55 | 1.17 | 0.8 | 0.42 | 0.11 | -0.26 | -1.14 | -2.65 | -4.37
Bishops Wood 132kV | Ludlow 132 33 | CLEOBURY MORTIMER 33 11kV S STN | Primary | 11 | -2.4856 | 52.3763 | WPD Best View | Headroom (MW) | Thermal | 2.57 | 2.52 | 2.49 | 2.45 | 2.38 | 2.32 | 2.25 | 2.18 | 2.07 | 1.77 | 1.63 | 1.48 | 1.23 | 1.03 | 0.79 | 0.31 | -0.52 | -1.33
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Consumer Transformation | Headroom (MW) | Thermal | 4.185 | 3.305 | 3.235 | 3.145 | 2.855 | 2.655 | 2.415 | 2.105 | 1.795 | 1.535 | 1.275 | 1.035 | 0.825 | 0.605 | 0.325 | -1.035 | -2.515 | -4.075
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Leading the Way | Headroom (MW) | Thermal | 4.185 | 3.295 | 3.215 | 3.125 | 2.775 | 2.575 | 2.335 | 2.085 | 1.825 | 1.575 | 1.325 | 1.095 | 0.855 | 0.625 | 0.345 | -1.125 | -2.605 | -4.585
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | Steady Progression | Headroom (MW) | N/A | 4.185 | 4.105 | 3.315 | 3.285 | 3.245 | 3.205 | 3.165 | 3.045 | 2.935 | 2.845 | 2.745 | 2.675 | 2.635 | 2.605 | 2.585 | 2.605 | 2.435 | 2.075
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | System Transformation | Headroom (MW) | N/A | 4.185 | 3.325 | 3.275 | 3.225 | 3.095 | 3.005 | 2.875 | 2.695 | 2.525 | 2.365 | 2.225 | 2.125 | 2.055 | 1.985 | 1.875 | 1.585 | 0.925 | 0.245
Bishops Wood 132kV | Ludlow 132 33 | CRAVEN ARMS 33 11kV S STN | Primary | 11 | -2.8315 | 52.4411 | WPD Best View | Headroom (MW) | Thermal | 4.185 | 3.325 | 3.275 | 3.215 | 3.075 | 2.965 | 2.835 | 2.635 | 2.445 | 2.285 | 2.125 | 2.015 | 1.935 | 1.865 | 1.735 | 1.365 | 0.605 | -0.085
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Consumer Transformation | Headroom (MW) | Thermal | 7.18 | 7.04 | 6.88 | 6.74 | 6.35 | 6.04 | 5.74 | 5.27 | 4.77 | 4.26 | 3.65 | 2.99 | 2.31 | 1.64 | 0.84 | -1.85 | -6.04 | -9.92
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Leading the Way | Headroom (MW) | Thermal | 7.18 | 7.02 | 6.86 | 6.71 | 6.26 | 5.94 | 5.62 | 5.34 | 5.08 | 4.83 | 4.61 | 4.4 | 3.79 | 3.19 | 2.53 | -0.43 | -5.99 | -9.65
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | Steady Progression | Headroom (MW) | N/A | 7.18 | 7.1 | 7.07 | 7.04 | 6.99 | 6.93 | 6.87 | 6.77 | 6.66 | 6.54 | 6.41 | 6.25 | 5.95 | 5.67 | 5.29 | 4.89 | 4.14 | 3.11
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | System Transformation | Headroom (MW) | Thermal | 7.18 | 7.07 | 7.01 | 6.89 | 6.72 | 6.58 | 6.42 | 6.08 | 5.71 | 5.3 | 4.8 | 4.25 | 3.69 | 3.2 | 2.61 | 1.46 | -1.45 | -3.81
Bishops Wood 132kV | Ludlow 132 33 | Ludlow 132/66/33/11kV | Primary | 11 | -2.688 | 52.3668 | WPD Best View | Headroom (MW) | Thermal | 7.18 | 7.07 | 7.01 | 6.89 | 6.72 | 6.58 | 6.42 | 6.08 | 5.7 | 5.3 | 4.79 | 4.24 | 3.67 | 3.18 | 2.59 | 1.44 | -1.47 | -3.82
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Consumer Transformation | Headroom (MW) | Thermal | 4.14 | 3.35 | 3.3 | 3.24 | 3.09 | 2.88 | 2.67 | 2.15 | 1.56 | 0.9 | -0.08 | -1.18 | -2.34 | -3.39 | -4.65 | -7.43 | -10.95 | -15.16
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Leading the Way | Headroom (MW) | Thermal | 4.14 | 3.34 | 3.29 | 3.23 | 3.07 | 2.84 | 2.6 | 2.36 | 2.13 | 1.91 | 1.68 | 1.45 | 0.51 | -0.37 | -1.29 | -4.38 | -8.69 | -11.08
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | Steady Progression | Headroom (MW) | Thermal | 4.14 | 4.1 | 3.35 | 3.33 | 3.31 | 3.27 | 3.23 | 3.11 | 3 | 2.85 | 2.64 | 2.38 | 1.8 | 1.24 | 0.51 | -0.46 | -1.63 | -2.92
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | System Transformation | Headroom (MW) | Thermal | 4.14 | 4.09 | 3.33 | 3.29 | 3.23 | 3.17 | 3.09 | 2.66 | 2.09 | 1.54 | 0.66 | -0.34 | -1.38 | -2.31 | -3.46 | -5.24 | -8.04 | -11.43
Bishops Wood 132kV | Ludlow 132 33 | STOCKTON 33 11kV S STN | Primary | 11 | -2.4217 | 52.3007 | WPD Best View | Headroom (MW) | Thermal | 4.14 | 4.1 | 3.35 | 3.33 | 3.31 | 3.26 | 3.22 | 3.08 | 2.95 | 2.79 | 2.56 | 2.29 | 1.69 | 1.12 | 0.37 | -0.63 | -1.82 | -3.13
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Consumer Transformation | Headroom (MW) | Thermal | 11.19 | 11.09 | 10.95 | 10.87 | 10.64 | 10.45 | 10.26 | 9.61 | 8.85 | 8 | 6.87 | 5.59 | 4.24 | 3.03 | 1.54 | -1.4 | -5.03 | -9.4
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Leading the Way | Headroom (MW) | Thermal | 11.19 | 11.09 | 10.94 | 10.85 | 10.6 | 10.4 | 10.19 | 9.98 | 9.78 | 9.59 | 9.4 | 9.22 | 8.17 | 7.19 | 6.17 | 2.89 | -1.67 | -4.02
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | Steady Progression | Headroom (MW) | N/A | 11.19 | 11.13 | 11.09 | 11.06 | 11.02 | 10.97 | 10.93 | 10.77 | 10.62 | 10.43 | 10.16 | 9.85 | 9.15 | 8.47 | 7.57 | 6.41 | 5.11 | 3.66
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | System Transformation | Headroom (MW) | Thermal | 11.19 | 11.11 | 11.06 | 10.94 | 10.83 | 10.74 | 10.63 | 10.08 | 9.39 | 8.61 | 7.56 | 6.37 | 5.12 | 4.01 | 2.63 | 0.62 | -2.28 | -5.81
Bishops Wood 132kV | Ludlow 132 33 | TENBURY 33 11kV S STN | Primary | 11 | -2.5938 | 52.317 | WPD Best View | Headroom (MW) | Thermal | 11.19 | 11.12 | 11.08 | 11.03 | 10.94 | 10.87 | 10.79 | 10.45 | 10.06 | 9.61 | 9 | 8.31 | 7.36 | 6.49 | 5.37 | 3.76 | 1.73 | -0.67
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Consumer Transformation | Headroom (MW) | Thermal | 27.19 | 26.96 | 26.71 | 26.36 | 25.49 | 24.8 | 24.14 | 23.25 | 22.33 | 21.46 | 20.43 | 19.26 | 18.05 | 16.88 | 15.56 | 10.14 | 3.22 | -4.59
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Leading the Way | Headroom (MW) | Thermal | 27.19 | 26.93 | 26.67 | 26.29 | 25.32 | 24.6 | 23.92 | 23.25 | 22.62 | 22.1 | 21.46 | 20.8 | 19.68 | 18.57 | 17.38 | 11.34 | 3.47 | -5.07
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | Steady Progression | Headroom (MW) | N/A | 27.19 | 27.01 | 26.91 | 26.83 | 26.71 | 26.63 | 26.51 | 26.32 | 26.14 | 25.95 | 25.73 | 25.5 | 25.1 | 24.74 | 24.29 | 23.67 | 22.3 | 20.38
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | System Transformation | Headroom (MW) | N/A | 27.19 | 26.98 | 26.86 | 26.68 | 26.3 | 25.98 | 25.63 | 25.08 | 24.48 | 23.88 | 23.13 | 22.31 | 21.49 | 20.77 | 19.88 | 17.69 | 13.77 | 9.56
Bishops Wood 132kV | Malvern 132 11 (GT1) | Malvern 132/11kVDUMMY | Primary | 11 | -2.3053 | 52.1264 | WPD Best View | Headroom (MW) | N/A | 27.19 | 27.01 | 26.91 | 26.82 | 26.69 | 26.54 | 26.38 | 26.16 | 25.96 | 25.74 | 25.49 | 25.23 | 24.81 | 24.41 | 23.94 | 23.07 | 21.49 | 19.34
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Consumer Transformation | Headroom (MW) | Thermal | 7.51 | 7.42 | 7.36 | 7.3 | 7.15 | 6.96 | 6.63 | 5.69 | 4.7 | 3.61 | 2.32 | 0.88 | -0.62 | -1.99 | -3.65 | -6.48 | -11.19 | -16.67
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Leading the Way | Headroom (MW) | Thermal | 7.51 | 7.41 | 7.35 | 7.29 | 7.13 | 6.93 | 6.58 | 6.27 | 6.01 | 5.7 | 5.42 | 5.14 | 4.01 | 2.9 | 2.73 | -1.28 | -6.6 | -9.93
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | Steady Progression | Headroom (MW) | N/A | 7.51 | 7.43 | 7.39 | 7.35 | 7.31 | 7.27 | 7.23 | 7.19 | 7.01 | 6.66 | 6.38 | 6.03 | 5.27 | 4.56 | 3.64 | 2.44 | 3.55 | 2.02
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | System Transformation | Headroom (MW) | Thermal | 7.51 | 7.42 | 7.38 | 7.33 | 7.27 | 7.21 | 7.14 | 6.57 | 5.68 | 4.77 | 3.65 | 2.4 | 1.08 | -0.07 | -1.47 | -2.67 | -5.77 | -9.49
Bishops Wood 132kV | Stourport 132 33 | KINVER 33 11kV S STN | Primary | 11 | -2.2145 | 52.4408 | WPD Best View | Headroom (MW) | Thermal | 7.51 | 7.42 | 7.36 | 7.3 | 7.17 | 7 | 6.67 | 6.38 | 6.13 | 5.84 | 5.56 | 5.3 | 4.19 | 3.1 | 1.96 | -1.86 | -5.94 | -8.99
Bishops Wood 132kV | Stourport 132 33 | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Consumer Transformation | Headroom (MW) | N/A | 49.46 | 49.12 | 48.93 | 48.72 | 48.21 | 47.68 | 46.8 | 45.63 | 44.49 | 43.32 | 42.04 | 40.61 | 39.08 | 37.58 | 35.91 | 28.48 | 19.07 | 8.48
Bishops Wood 132kV | Stourport 132 33 | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Leading the Way | Headroom (MW) | N/A | 49.46 | 49.07 | 48.87 | 48.63 | 47.91 | 47.31 | 46.41 | 45.47 | 44.65 | 43.84 | 42.94 | 42.1 | 40.68 | 39.19 | 37.6 | 29.52 | 19.01 | 6.94
Bishops Wood 132kV | Stourport 132 33 | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | Steady Progression | Headroom (MW) | N/A | 49.46 | 49.2 | 49.08 | 43.33 | 43.13 | 43.04 | 42.95 | 42.48 | 41.93 | 41.82 | 41.56 | 41.13 | 40.85 | 40.62 | 40.13 | 39.54 | 37.77 | 35.35
Bishops Wood 132kV | Stourport 132 33 | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | System Transformation | Headroom (MW) | N/A | 49.46 | 49.16 | 49 | 48.85 | 48.53 | 48.39 | 48.27 | 48.11 | 47.37 | 46.56 | 45.66 | 44.74 | 43.81 | 42.98 | 41.91 | 39.24 | 34.78 | 29.31
Bishops Wood 132kV | Stourport 132 33 | Kidderminster 132/33/11kV | Primary | 11 | -2.2508 | 52.3828 | WPD Best View | Headroom (MW) | N/A | 49.46 | 49.2 | 49.08 | 43.33 | 43.13 | 43.03 | 42.94 | 42.47 | 41.91 | 41.8 | 41.53 | 41.1 | 40.82 | 40.58 | 40.1 | 39.5 | 37.73 | 35.31
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Consumer Transformation | Headroom (MW) | Thermal | -33.64 | -33.79 | -33.88 | -33.98 | -34.18 | -34.35 | -34.58 | -34.88 | -35.18 | -35.51 | -35.9 | -36.31 | -36.75 | -37.15 | -37.63 | -39.06 | -7.04 | -8.86
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Leading the Way | Headroom (MW) | Thermal | -33.64 | -33.79 | -33.89 | -33.99 | -34.22 | -34.39 | -34.56 | -34.72 | -34.88 | -35.03 | -35.18 | -35.33 | -35.7 | -36.06 | -36.43 | -4.97 | -3.86 | -3.6
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | Steady Progression | Headroom (MW) | Thermal | -33.64 | -33.76 | -33.82 | -33.87 | -33.94 | -34 | -34.17 | -34.27 | -34.36 | -34.46 | -34.57 | -34.68 | -34.89 | -35.09 | -35.34 | -35.76 | -36.2 | -4
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | System Transformation | Headroom (MW) | Thermal | -33.64 | -33.77 | -33.84 | -33.92 | -34.03 | -34.13 | -34.3 | -34.53 | -34.78 | -35.05 | -35.38 | -35.74 | -36.11 | -36.44 | -36.83 | -37.54 | -4.97 | -6.1
Bishops Wood 132kV | Stourport 132 33 | QUATT 33 11kV S STN | Primary | 11 | -2.373 | 52.4808 | WPD Best View | Headroom (MW) | Thermal | -33.64 | -33.77 | -33.84 | -33.92 | -34.03 | -34.13 | -34.29 | -34.52 | -34.77 | -35.03 | -35.36 | -35.71 | -36.08 | -36.4 | -36.78 | -37.49 | -4.91 | -6.04
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Consumer Transformation | Headroom (MW) | Thermal | 15.23 | 15.07 | 14.72 | 14.56 | 14.23 | 13.96 | 13.68 | 13.09 | 12.45 | 11.75 | 10.8 | 9.77 | 8.7 | 7.71 | 6.52 | 3.19 | -1.25 | -6.38
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Leading the Way | Headroom (MW) | Thermal | 15.23 | 15.05 | 14.7 | 14.54 | 14.17 | 13.89 | 13.59 | 13.32 | 13.07 | 12.84 | 12.56 | 12.28 | 11.43 | 10.6 | 9.72 | 6.03 | 0.92 | -3.2
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | Steady Progression | Headroom (MW) | N/A | 15.23 | 15.12 | 15.07 | 15.02 | 14.96 | 14.9 | 14.84 | 14.7 | 14.56 | 14.38 | 14.17 | 13.93 | 13.44 | 12.98 | 12.37 | 11.68 | 10.68 | 9.31
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | System Transformation | Headroom (MW) | N/A | 15.23 | 15.09 | 15.01 | 14.71 | 14.56 | 14.42 | 14.27 | 13.83 | 13.3 | 12.72 | 11.92 | 11.03 | 10.12 | 9.33 | 8.37 | 6.81 | 4.03 | 0.79
Bishops Wood 132kV | Stourport 132 33 | WRIBBENHALL 33 11kV S STN | Primary | 11 | -2.3076 | 52.3853 | WPD Best View | Headroom (MW) | N/A | 15.23 | 15.12 | 15.07 | 15.01 | 14.95 | 14.88 | 14.79 | 14.63 | 14.47 | 14.28 | 14.02 | 13.74 | 13.21 | 12.69 | 12.03 | 11.06 | 9.6 | 7.77
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Consumer Transformation | Headroom (MW) | Thermal | 35.25 | 34.87 | 34.61 | 29.44 | 28.71 | 28.04 | 27.32 | 25.87 | 24.39 | 22.95 | 21.23 | 19.44 | 17.74 | 16.26 | 15.11 | 9.82 | 3.04 | -6.85
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Leading the Way | Headroom (MW) | Thermal | 35.25 | 34.84 | 34.57 | 29.38 | 28.51 | 27.81 | 27.02 | 26.4 | 25.63 | 25.03 | 24.41 | 22.44 | 21.12 | 19.8 | 19.67 | 13.78 | 4.15 | -4.67
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | Steady Progression | Headroom (MW) | N/A | 35.25 | 34.98 | 34.85 | 29.85 | 29.68 | 29.55 | 29.38 | 28.7 | 28.05 | 27.4 | 26.72 | 26.06 | 25.1 | 24.21 | 23.16 | 22.04 | 20.25 | 17.63
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | System Transformation | Headroom (MW) | N/A | 35.25 | 34.93 | 34.74 | 29.68 | 29.31 | 29.11 | 28.84 | 27.71 | 26.34 | 25.22 | 23.79 | 22.29 | 20.87 | 19.63 | 18.58 | 16.56 | 12.08 | 5.52
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | DROITWICH 66 11kV S STN | Primary | 11 | -2.1706 | 52.274 | WPD Best View | Headroom (MW) | N/A | 35.25 | 34.98 | 34.85 | 29.85 | 29.68 | 29.55 | 29.38 | 28.7 | 28.05 | 27.4 | 26.72 | 26.06 | 25.1 | 24.21 | 23.16 | 22.04 | 20.25 | 17.63
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Consumer Transformation | Headroom (MW) | Thermal | 28.04 | 27.75 | 27.61 | 27.41 | 26.56 | 25.87 | 25.02 | 23.87 | 22.83 | 21.84 | 20.82 | 19.8 | 18.78 | 17.76 | 16.63 | 10.45 | 3.09 | -4.97
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Leading the Way | Headroom (MW) | Thermal | 28.04 | 27.71 | 27.56 | 27.34 | 26.31 | 25.57 | 24.65 | 23.76 | 22.98 | 22.17 | 21.39 | 20.62 | 19.62 | 18.59 | 17.5 | 11.37 | 3.7 | -4.92
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | Steady Progression | Headroom (MW) | N/A | 28.04 | 27.81 | 27.71 | 27.6 | 27.41 | 27.29 | 27.15 | 27.02 | 26.85 | 26.5 | 26.27 | 26.04 | 25.72 | 25.44 | 25.13 | 24.53 | 23.56 | 22.01
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | System Transformation | Headroom (MW) | N/A | 28.04 | 27.78 | 27.66 | 27.54 | 27.23 | 26.96 | 26.64 | 26.13 | 25.37 | 24.85 | 24.22 | 23.61 | 23.02 | 22.5 | 21.95 | 20.16 | 16.47 | 12.52
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132/66/33/11kV | Primary | 11 | -2.2691 | 52.3381 | WPD Best View | Headroom (MW) | N/A | 28.04 | 27.81 | 27.71 | 27.6 | 27.41 | 27.28 | 27.15 | 27.01 | 26.78 | 26.48 | 26.22 | 25.97 | 25.64 | 25.36 | 25.04 | 24.35 | 23.23 | 21.56
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Consumer Transformation | Headroom (MW) | Thermal | 32.58 | 32.14 | 31.81 | 31.42 | 30.27 | 29.37 | 28.37 | 26.39 | 24.28 | 22.11 | 19.41 | 16.5 | 13.36 | 10.43 | 7 | -3.49 | -15.95 | -30.19
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Leading the Way | Headroom (MW) | Thermal | 32.58 | 32.08 | 31.75 | 31.33 | 29.98 | 29.02 | 27.96 | 27 | 26.09 | 25.22 | 24.25 | 23.27 | 20.66 | 18.12 | 15.46 | 4.18 | -9.89 | -21.36
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | Steady Progression | Headroom (MW) | N/A | 32.58 | 32.3 | 32.17 | 32.05 | 31.85 | 31.66 | 31.5 | 31.14 | 30.74 | 30.16 | 29.6 | 28.95 | 27.59 | 26.29 | 24.62 | 22.53 | 19.59 | 15.93
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | System Transformation | Headroom (MW) | Thermal | 32.58 | 32.22 | 32.01 | 31.78 | 31.25 | 30.85 | 30.45 | 29.23 | 27.52 | 25.82 | 23.6 | 21.17 | 18.66 | 16.47 | 13.84 | 8.67 | 0.97 | -7.95
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Upton Warren 132/66/11kVDUMMY | Primary | 11 | -2.0962 | 52.3091 | WPD Best View | Headroom (MW) | N/A | 32.58 | 32.23 | 32.03 | 31.81 | 31.32 | 30.95 | 30.58 | 29.75 | 28.76 | 27.53 | 26.16 | 24.65 | 22.71 | 20.97 | 18.85 | 14.73 | 8.92 | 2.54
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Consumer Transformation | Headroom (MW) | Thermal | 24.91 | 24.74 | 24.76 | 24.66 | 24.19 | 23.72 | 23.25 | 22.39 | 21.43 | 20.38 | 19.11 | 17.66 | 16.14 | 14.69 | 13.1 | 7.6 | 1.56 | -5.39
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Leading the Way | Headroom (MW) | Thermal | 24.91 | 24.72 | 24.74 | 24.63 | 24.05 | 23.58 | 23.08 | 22.58 | 22.1 | 21.6 | 21.05 | 20.45 | 19.11 | 17.78 | 16.51 | 10.67 | 3.63 | -2.8
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | Steady Progression | Headroom (MW) | N/A | 24.91 | 24.78 | 24.83 | 24.78 | 24.68 | 24.65 | 24.61 | 24.57 | 24.53 | 24.48 | 24.24 | 23.96 | 23.38 | 22.81 | 22.09 | 21.12 | 19.68 | 17.73
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | System Transformation | Headroom (MW) | N/A | 24.91 | 24.76 | 24.8 | 24.73 | 24.56 | 24.51 | 24.35 | 23.74 | 23.02 | 22.21 | 21.16 | 20 | 18.8 | 17.73 | 16.48 | 13.73 | 9.88 | 5.53
Bishops Wood 132kV | Timberdine 132 11 (GT1) | Timberdine 132/11kVDUMMY | Primary | 11 | -2.2056 | 52.1676 | WPD Best View | Headroom (MW) | N/A | 24.91 | 24.78 | 24.83 | 24.78 | 24.68 | 24.65 | 24.61 | 24.57 | 24.53 | 24.48 | 24.24 | 23.96 | 23.38 | 22.81 | 22.09 | 21.12 | 19.68 | 17.73
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Consumer Transformation | Headroom (MW) | Fault level | -26.5383 | -26.7149 | -26.8706 | -28.2028 | -28.6932 | -29.1756 | -29.6592 | -30.1924 | -30.7256 | -31.2656 | -31.9495 | -32.6588 | -33.3765 | -34.0756 | -34.8046 | -37.8584 | -41.3037 | -44.8687
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Leading the Way | Headroom (MW) | Fault level | -36.3196 | -36.5621 | -36.7768 | -38.6015 | -39.271 | -39.9321 | -40.5985 | -41.2541 | -41.926 | -42.6009 | -43.333 | -44.0673 | -45.0025 | -45.9423 | -46.8891 | -51.3448 | -56.2546 | -60.4772
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | Steady Progression | Headroom (MW) | Fault level | -14.6401 | -14.6516 | -14.6591 | -15.3143 | -15.3212 | -15.3508 | -15.3859 | -15.446 | -15.5055 | -15.5724 | -15.6552 | -15.7374 | -15.8476 | -15.9543 | -16.0776 | -16.4259 | -16.8368 | -17.2489
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | System Transformation | Headroom (MW) | Fault level | -20.9206 | -20.9687 | -21.0585 | -22.01 | -22.1328 | -22.284 | -22.4633 | -22.6781 | -22.8947 | -23.1145 | -23.4334 | -23.7652 | -24.1073 | -24.4338 | -24.7932 | -26.0761 | -27.5582 | -29.1435
Bishops Wood 132kV | Warndon 132 11 (GT1A) | Warndon 132/11kVDUMMY | Primary | 11 | -2.1935 | 52.2176 | WPD Best View | Headroom (MW) | Fault level | -21.8126 | -21.8298 | -21.8409 | -22.8171 | -22.8273 | -22.8714 | -22.9238 | -23.0133 | -23.1019 | -23.2016 | -23.325 | -23.4474 | -23.6116 | -23.7707 | -23.9543 | -24.4733 | -25.0855 | -25.6995
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Consumer Transformation | Headroom (MW) | N/A | 45.93 | 45.56 | 45.28 | 44.97 | 44.19 | 43.6 | 43 | 42.16 | 41.28 | 40.43 | 39.49 | 38.49 | 37.36 | 36.25 | 35.07 | 30.02 | 23.54 | 16.61
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Leading the Way | Headroom (MW) | N/A | 45.93 | 45.53 | 45.24 | 44.91 | 44.03 | 43.45 | 42.85 | 42.23 | 41.62 | 41.06 | 40.47 | 39.82 | 38.75 | 37.65 | 36.58 | 31.51 | 23.15 | 15.51
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | Steady Progression | Headroom (MW) | N/A | 45.2055 | 45.1932 | 45.1835 | 45.1716 | 45.1562 | 45.1143 | 45.0571 | 44.9 | 44.75 | 44.56 | 44.36 | 44.15 | 43.81 | 43.48 | 43.07 | 42.57 | 41.45 | 40.11
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | System Transformation | Headroom (MW) | N/A | 45.93 | 45.62 | 45.43 | 45.23 | 44.88 | 44.62 | 44.31 | 43.81 | 43.23 | 42.61 | 41.89 | 41.15 | 40.4 | 39.74 | 39.03 | 37.03 | 33.27 | 29.51
Bishops Wood 132kV | Worcester 132 11 (GT1) | Worcester 132/11kVDUMMY | Primary | 11 | -2.2359 | 52.1919 | WPD Best View | Headroom (MW) | N/A | 45.93 | 45.67 | 45.54 | 45.43 | 45.3 | 45.18 | 45.07 | 44.9 | 44.75 | 44.56 | 44.36 | 44.15 | 43.81 | 43.48 | 43.07 | 42.57 | 41.45 | 40.11
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Consumer Transformation | Headroom (MW) | N/A | 45.7111 | 45.5152 | 45.2567 | 44.935 | 44.1781 | 43.3829 | 42.5457 | 41.5411 | 40.4816 | 39.3373 | 38.0103 | 36.6075 | 35.1769 | 33.8221 | 32.354 | 26.5872 | 16.51 | 5.47
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Leading the Way | Headroom (MW) | Thermal | 49.36 | 48.63 | 48.12 | 47.57 | 46.26 | 45.53 | 44.58 | 43.78 | 43.05 | 42.37 | 41.69 | 40.93 | 39.61 | 38.2 | 36.68 | 27.68 | 15.88 | -0.27
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | Steady Progression | Headroom (MW) | N/A | 28.9741 | 28.9561 | 28.9358 | 28.9199 | 28.9019 | 28.8393 | 28.7252 | 28.6096 | 28.4948 | 28.3486 | 28.1813 | 27.9972 | 27.7079 | 27.4238 | 27.0852 | 26.2752 | 25.4987 | 24.696
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | System Transformation | Headroom (MW) | N/A | 38.374 | 38.297 | 38.1967 | 38.0888 | 37.8838 | 37.6094 | 37.2504 | 36.7512 | 36.1968 | 35.5893 | 34.8646 | 34.0785 | 33.2685 | 32.5173 | 31.6675 | 28.8232 | 27.5994 | 21.4436
Bushbury 132kV | Bushbury 132 11 (GT1C) | Bushbury B-C 132/33/11kVDUMMY | Primary | 11 | -2.113 | 52.6337 | WPD Best View | Headroom (MW) | N/A | 39.5867 | 39.4164 | 39.1919 | 38.9133 | 38.2572 | 37.5601 | 36.8643 | 36.1736 | 35.4732 | 34.7422 | 33.9269 | 33.1014 | 31.9684 | 30.8806 | 29.7859 | 24.6217 | 18.53 | 4.79
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Consumer Transformation | Headroom (MW) | Thermal | 11.54 | 12.2 | 12.07 | 11.9 | 11.51 | 11.32 | 11.12 | 10.45 | 9.64 | 8.74 | 7.58 | 6.28 | 4.91 | 3.63 | 2.07 | -2 | -8.24 | -14.61
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Leading the Way | Headroom (MW) | Thermal | 11.54 | 12.3 | 12.15 | 11.97 | 11.5 | 11.33 | 11.18 | 11.07 | 10.89 | 10.73 | 10.45 | 10.18 | 8.98 | 7.85 | 6.65 | 1.84 | -6.29 | -11.64
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | Steady Progression | Headroom (MW) | N/A | 11.54 | 12.19 | 12.18 | 12.17 | 12.19 | 12.3 | 12.38 | 12.36 | 12.28 | 12.16 | 11.96 | 11.72 | 11.1 | 10.52 | 9.74 | 9.1 | 7.65 | 5.75
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | System Transformation | Headroom (MW) | Thermal | 11.54 | 12.25 | 12.19 | 12.11 | 12.01 | 12.03 | 12 | 11.51 | 10.83 | 10.07 | 9.05 | 7.9 | 6.69 | 5.66 | 4.39 | 2.35 | -2.14 | -6.4
Bushbury 132kV | Bushbury 132 33 | ALBRIGHTON 33 11kV S STN | Primary | 11 | -2.2497 | 52.6372 | WPD Best View | Headroom (MW) | Thermal | 11.54 | 12.21 | 12.08 | 11.93 | 11.61 | 11.56 | 11.48 | 11.27 | 10.95 | 10.62 | 10.11 | 9.55 | 8.38 | 7.27 | 6.03 | 1.96 | -4.53 | -9.63
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Consumer Transformation | Headroom (MW) | Thermal | 8.9 | 8.73 | 8.61 | 8.48 | 8.04 | 7.74 | 7.48 | 6.76 | 5.95 | 5.04 | 3.9 | 2.62 | 1.28 | 0.09 | -1.36 | -8.19 | -12.64 | -17.96
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Leading the Way | Headroom (MW) | Thermal | 8.9 | 8.71 | 8.58 | 8.45 | 7.92 | 7.59 | 7.32 | 7.07 | 6.83 | 6.6 | 6.38 | 6.16 | 5.14 | 4.2 | 3.19 | -3.89 | -9.35 | -13.24
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | Steady Progression | Headroom (MW) | N/A | 8.9 | 8.79 | 8.75 | 8.71 | 8.63 | 8.57 | 8.52 | 8.37 | 8.23 | 8.05 | 7.84 | 7.58 | 6.99 | 6.42 | 5.65 | 5 | 3.75 | 2.11
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | System Transformation | Headroom (MW) | Thermal | 8.9 | 8.76 | 8.69 | 8.62 | 8.41 | 8.26 | 8.13 | 7.56 | 6.85 | 6.06 | 5.06 | 3.91 | 2.71 | 1.67 | 0.39 | -3.07 | -6.23 | -10.08
Bushbury 132kV | Bushbury 132 33 | FOUR ASHES 33 11kV S STN | Primary | 11 | -2.117 | 52.6763 | WPD Best View | Headroom (MW) | Thermal | 8.9 | 8.71 | 8.58 | 8.45 | 7.92 | 7.6 | 7.33 | 7.09 | 6.87 | 6.66 | 6.45 | 6.25 | 5.24 | 4.33 | 3.32 | -3.72 | -9.15 | -13.01
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Consumer Transformation | Headroom (MW) | N/A | 40.74 | 40.43 | 40.33 | 40.22 | 40.08 | 39.94 | 39.81 | 39.68 | 39.55 | 39.44 | 39.34 | 39.24 | 39.15 | 39.06 | 38.97 | 37.08 | 36.01 | 35.08
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Leading the Way | Headroom (MW) | N/A | 40.74 | 40.43 | 40.33 | 40.22 | 40.07 | 39.92 | 39.77 | 39.63 | 39.49 | 39.37 | 39.26 | 39.16 | 39.05 | 38.95 | 38.84 | 35.7 | 34.34 | 33.17
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | Steady Progression | Headroom (MW) | N/A | 40.74 | 40.57 | 40.36 | 40.28 | 40.19 | 40.11 | 40.02 | 39.94 | 39.85 | 39.78 | 39.7 | 39.63 | 39.56 | 39.49 | 39.43 | 39.2 | 38.92 | 38.53
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | System Transformation | Headroom (MW) | N/A | 40.74 | 40.44 | 40.35 | 40.25 | 40.15 | 40.04 | 39.93 | 39.82 | 39.71 | 39.61 | 39.52 | 39.44 | 39.36 | 39.29 | 39.23 | 37.73 | 36.97 | 36.4
Bushbury 132kV | Bushbury 132 33 | I54 Busines Park 33/11kv | Primary | 11 | -2.1418 | 52.6301 | WPD Best View | Headroom (MW) | N/A | 40.74 | 40.43 | 40.33 | 40.22 | 40.08 | 39.93 | 39.79 | 39.65 | 39.51 | 39.38 | 39.27 | 39.17 | 39.08 | 38.98 | 38.89 | 35.83 | 34.55 | 33.63
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Consumer Transformation | Headroom (MW) | Thermal | 46.1 | 45.81 | 45.54 | 45.21 | 44.28 | 43.74 | 43.13 | 41.44 | 39.43 | 37.21 | 34.69 | 31.88 | 28.91 | 26.19 | 22.84 | 14.17 | 4.07 | -7.27
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Leading the Way | Headroom (MW) | N/A | 46.1 | 45.77 | 45.49 | 45.14 | 44 | 43.51 | 42.91 | 42.23 | 41.42 | 40.64 | 40.05 | 39.47 | 37.05 | 34.69 | 32.25 | 23.01 | 10.89 | 2.69
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | Steady Progression | Headroom (MW) | N/A | 46.1 | 45.93 | 45.83 | 45.75 | 45.66 | 45.69 | 45.68 | 45.38 | 45.04 | 44.6 | 44.06 | 43.41 | 41.97 | 40.59 | 38.77 | 36.61 | 33.68 | 30.14
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | System Transformation | Headroom (MW) | N/A | 46.1 | 45.88 | 45.72 | 45.54 | 45.16 | 45.01 | 44.76 | 43.44 | 41.72 | 39.81 | 37.55 | 34.99 | 32.32 | 29.95 | 27.08 | 22.22 | 15.05 | 6.89
Bushbury 132kV | Stafford 132 11 (GT1B1) | Stafford 132/25/11kVDUMMY | Primary | 11 | -2.1221 | 52.8104 | WPD Best View | Headroom (MW) | N/A | 46.1 | 45.93 | 45.83 | 45.75 | 45.66 | 45.69 | 45.67 | 45.37 | 45.02 | 44.57 | 44.02 | 43.37 | 41.93 | 40.53 | 38.71 | 36.54 | 33.61 | 30.06
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Consumer Transformation | Headroom (MW) | Thermal | 39.0567 | 38.8878 | 38.6655 | 38.3827 | 37.7057 | 37.0308 | 36.3405 | 35.0947 | 33.7178 | 32.2082 | 30.3395 | 28.2981 | 26.1611 | 24.1824 | 21.9085 | 15.437 | 6.49 | -5.68
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Leading the Way | Headroom (MW) | Thermal | 44.22 | 43.91 | 43.74 | 43.46 | 42.38 | 41.47 | 40.69 | 39.94 | 39.26 | 38.63 | 37.87 | 37.13 | 35.14 | 33.18 | 31.1 | 21.4 | 9.81 | -1.65
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | Steady Progression | Headroom (MW) | N/A | 24.7562 | 24.7416 | 24.7258 | 24.7126 | 24.6973 | 24.6454 | 24.5834 | 24.4223 | 24.2642 | 24.0644 | 23.813 | 23.5245 | 22.9458 | 22.3821 | 21.6585 | 20.419 | 19.1469 | 17.8743
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | System Transformation | Headroom (MW) | N/A | 32.7877 | 32.7229 | 32.6384 | 32.5444 | 32.3613 | 32.1322 | 31.8527 | 31.1121 | 30.2401 | 29.2768 | 28.0328 | 26.6486 | 25.189 | 23.862 | 22.2745 | 18.7396 | 14.9525 | 10.564
Bushbury 132kV | Stafford South 132 11 (GT1A) | STAFFORD SOUTH 11kV S STN | Primary | 11 | -2.1066 | 52.7943 | WPD Best View | Headroom (MW) | N/A | 33.8238 | 33.7979 | 33.7678 | 33.7389 | 33.6871 | 33.5811 | 33.4534 | 33.2177 | 32.9838 | 32.6947 | 32.3569 | 31.9955 | 31.1105 | 30.2604 | 29.2443 | 27.1818 | 24.8359 | 23.1519
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Consumer Transformation | Headroom (MW) | N/A | 51.47 | 51.09 | 50.88 | 50.63 | 50.11 | 49.7 | 48.82 | 47.93 | 47.12 | 46.37 | 45.63 | 44.9 | 44.1 | 43.13 | 42.12 | 35.06 | 26.1 | 16.05
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Leading the Way | Headroom (MW) | N/A | 51.47 | 51.05 | 50.82 | 50.55 | 49.85 | 49.42 | 48.51 | 47.61 | 46.82 | 46.05 | 45.2 | 44.36 | 43.44 | 42.3 | 41.02 | 33.29 | 23.26 | 9.98
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | Steady Progression | Headroom (MW) | N/A | 37.3952 | 37.3754 | 37.3502 | 37.33 | 37.3106 | 37.2534 | 37.1851 | 37.0938 | 37.0026 | 36.8912 | 36.7703 | 36.647 | 36.5162 | 36.377 | 36.237 | 35.5852 | 35.1914 | 34.837
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | System Transformation | Headroom (MW) | N/A | 49.5271 | 49.4466 | 49.3352 | 49.2168 | 48.9985 | 48.7336 | 48.4195 | 48.0655 | 47.7039 | 47.3155 | 46.8851 | 46.441 | 45.9793 | 45.499 | 45.0009 | 42.8007 | 40.8753 | 37.48
Bushbury 132kV | Wednesfield 132 11 (GT2A) | Wednesfield 132/11kVDUMMY | Primary | 11 | -2.0706 | 52.599 | WPD Best View | Headroom (MW) | N/A | 51.0921 | 50.979 | 50.8226 | 50.6366 | 50.2326 | 49.8057 | 49.377 | 48.8536 | 48.3141 | 47.7304 | 47.0874 | 46.4232 | 45.7379 | 45.0392 | 44.34 | 41.07 | 35.59 | 28.75
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Consumer Transformation | Headroom (MW) | N/A | 49.36 | 49.05 | 48.85 | 48.63 | 48.25 | 47.9 | 47.18 | 46.27 | 45.42 | 44.64 | 43.9 | 43.14 | 42.3 | 41.4 | 40.41 | 33.52 | 24.15 | 13.61
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Leading the Way | Headroom (MW) | N/A | 49.36 | 49.02 | 48.8 | 48.55 | 48.06 | 47.65 | 46.88 | 45.95 | 45.08 | 44.27 | 43.41 | 42.56 | 41.58 | 40.44 | 39.22 | 31.39 | 21.01 | 7.25
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | Steady Progression | Headroom (MW) | N/A | 37.0808 | 37.0619 | 37.0456 | 37.0293 | 37.0112 | 36.9531 | 36.8848 | 36.8039 | 36.7226 | 36.6235 | 36.524 | 36.4276 | 36.3316 | 36.2356 | 36.1422 | 35.663 | 35.1332 | 34.599
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | System Transformation | Headroom (MW) | N/A | 49.1107 | 49.0285 | 48.93 | 48.76 | 48.53 | 48.3499 | 48.0368 | 47.7169 | 47.3952 | 47.0683 | 46.7263 | 46.3817 | 46.0284 | 45.6704 | 45.3058 | 43.416 | 39.53 | 35.32
Bustleholm 132kV | Bustleholm 132 11 (GT1) | BUSTLEHOLM 11kV S STN | Primary | 11 | -1.962 | 52.5538 | WPD Best View | Headroom (MW) | N/A | 49.36 | 49.1 | 48.95 | 48.81 | 48.61 | 48.48 | 48.35 | 48.12 | 47.82 | 47.67 | 47.47 | 47.26 | 47.05 | 46.85 | 46.64 | 45.46 | 41.93 | 38.38
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Consumer Transformation | Headroom (MW) | N/A | 52.26 | 51.83 | 51.55 | 51.22 | 50.7 | 50.37 | 49.39 | 48.18 | 47.03 | 45.97 | 44.76 | 43.45 | 42.1 | 40.74 | 39.2 | 30.3 | 18.47 | 4.48
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Leading the Way | Headroom (MW) | Thermal | 52.26 | 51.8 | 51.48 | 51.11 | 50.47 | 50.1 | 49.09 | 48.04 | 47.1 | 46.26 | 45.28 | 44.2 | 42.75 | 41.16 | 39.43 | 29.09 | 15.77 | -2
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | Steady Progression | Headroom (MW) | N/A | 52.26 | 51.93 | 51.76 | 51.59 | 51.4 | 51.24 | 51.08 | 50.92 | 50.76 | 50.6 | 50.43 | 50.27 | 50.1 | 49.93 | 49.75 | 48.96 | 47.87 | 45.48
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | System Transformation | Headroom (MW) | N/A | 52.26 | 51.88 | 51.66 | 51.42 | 51.11 | 50.91 | 50.7 | 50.49 | 50.26 | 50.03 | 49.43 | 48.78 | 48.18 | 47.64 | 46.93 | 43.54 | 38.42 | 32.41
Bustleholm 132kV | Kingstanding 132 11 (GT1A) | Kingstanding 132/11kVDummy | Primary | 11 | -1.8798 | 52.5557 | WPD Best View | Headroom (MW) | N/A | 52.26 | 51.85 | 51.59 | 51.3 | 50.82 | 50.54 | 50.26 | 49.95 | 49.36 | 48.71 | 47.98 | 47.26 | 46.42 | 45.34 | 44.07 | 37.38 | 29.07 | 16.51
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Consumer Transformation | Headroom (MW) | N/A | 44.18 | 44.04 | 44 | 43.96 | 43.79 | 43.68 | 43.56 | 43.2 | 42.87 | 42.61 | 42.42 | 42.27 | 42.15 | 42.03 | 43.09 | 39.04 | 38.23 | 37.36
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Leading the Way | Headroom (MW) | N/A | 44.18 | 44.04 | 44.01 | 43.98 | 43.75 | 43.63 | 43.5 | 43.37 | 43.31 | 38.26 | 38.12 | 37.99 | 37.86 | 37.72 | 37.58 | 36.83 | 38.22 | 39.25
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | Steady Progression | Headroom (MW) | N/A | 37.4397 | 37.4138 | 37.3891 | 37.3631 | 37.3495 | 37.3266 | 37.3006 | 36.8343 | 36.383 | 35.9602 | 35.5797 | 35.2631 | 35.0934 | 34.962 | 34.881 | 34.7581 | 34.6603 | 34.57
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | System Transformation | Headroom (MW) | N/A | 44.18 | 44.05 | 44.02 | 43.98 | 43.85 | 43.75 | 43.65 | 43.3 | 42.98 | 39.45 | 39.27 | 39.13 | 39.03 | 38.92 | 38.81 | 38.29 | 38.09 | 37.91
Bustleholm 132kV | Ladywood 132 11 (GT1A) | Ladywood 132/11kVDUMMY | Primary | 11 | -1.9159 | 52.4768 | WPD Best View | Headroom (MW) | N/A | 44.18 | 44.04 | 44.01 | 43.98 | 43.75 | 43.63 | 43.5 | 43.37 | 43.31 | 38.26 | 38.12 | 37.99 | 37.86 | 37.72 | 37.58 | 36.83 | 38.22 | 39.25
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Consumer Transformation | Headroom (MW) | N/A | 54.0968 | 53.8751 | 53.5958 | 53.2276 | 52.3863 | 51.5284 | 50.6568 | 49.7715 | 48.8711 | 48.0269 | 47.0932 | 46.1495 | 45.1956 | 44.2312 | 43.2724 | 38.3795 | 29.74 | 19.02
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Leading the Way | Headroom (MW) | N/A | 54.62 | 54.23 | 54.03 | 53.8 | 53.19 | 52.83 | 52.45 | 52.04 | 51.45 | 50.59 | 49.68 | 48.79 | 47.86 | 46.83 | 45.68 | 37.52 | 26.85 | 12.97
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | Steady Progression | Headroom (MW) | N/A | 34.2894 | 34.2616 | 34.2347 | 34.2079 | 34.1819 | 34.1123 | 34.0304 | 33.9361 | 33.8407 | 33.7328 | 33.6218 | 33.513 | 33.4034 | 33.2933 | 33.1854 | 32.6428 | 32.0945 | 31.547
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | System Transformation | Headroom (MW) | N/A | 45.4137 | 45.3192 | 45.2049 | 45.0695 | 44.8335 | 44.535 | 44.1752 | 43.8075 | 43.4328 | 43.0872 | 42.702 | 42.3107 | 41.9148 | 41.5119 | 41.1077 | 39.0639 | 36.9605 | 34.8514
Bustleholm 132kV | Perry Barr 132 11 (GT1) | Perry Barr 132/11kVDUMMY | Primary | 11 | -1.8956 | 52.5272 | WPD Best View | Headroom (MW) | N/A | 46.8487 | 46.652 | 46.4023 | 46.0749 | 45.3493 | 44.6025 | 43.8438 | 43.0705 | 42.2825 | 41.558 | 40.7529 | 39.9333 | 39.1036 | 38.2581 | 37.4049 | 33.0021 | 26.92 | 13.07
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Consumer Transformation | Headroom (MW) | N/A | 60.63 | 60.13 | 59.85 | 59.44 | 57.84 | 56.74 | 55.66 | 54.6 | 53.62 | 52.77 | 52 | 51.3 | 50.54 | 49.56 | 48.5 | 40.75 | 30.68 | 19.57
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Leading the Way | Headroom (MW) | N/A | 60.63 | 60.06 | 59.76 | 59.3 | 57.37 | 56.23 | 55.12 | 54.07 | 53.12 | 52.29 | 51.47 | 50.7 | 49.73 | 48.54 | 47.24 | 38.91 | 27.81 | 13.35
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | Steady Progression | Headroom (MW) | N/A | 60.63 | 60.24 | 60.04 | 59.85 | 59.53 | 59.35 | 59.17 | 58.98 | 58.82 | 58.64 | 58.45 | 58.27 | 58.09 | 57.91 | 57.72 | 56.84 | 55.74 | 54.09
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | System Transformation | Headroom (MW) | N/A | 60.63 | 60.18 | 59.95 | 59.72 | 59.14 | 58.61 | 58.06 | 57.52 | 57.03 | 56.58 | 56.17 | 55.81 | 55.53 | 55.3 | 55.08 | 52.85 | 48.13 | 43.46
Bustleholm 132kV | Rushall 132 11 (GT1) | Rushall 132/11kVDUMMY | Primary | 11 | -1.9706 | 52.5983 | WPD Best View | Headroom (MW) | N/A | 60.63 | 60.24 | 60.04 | 59.85 | 59.53 | 59.34 | 59.17 | 58.98 | 58.81 | 58.62 | 58.44 | 58.25 | 58.07 | 57.88 | 57.69 | 56.81 | 55.71 | 54.06
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Consumer Transformation | Headroom (MW) | N/A | 46.97 | 46.71 | 46.6 | 46.39 | 45.63 | 45.21 | 44.79 | 44.37 | 43.96 | 43.59 | 43.28 | 42.99 | 42.7 | 42.38 | 42.04 | 38.96 | 35.57 | 31.86
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Leading the Way | Headroom (MW) | N/A | 46.97 | 46.66 | 46.54 | 46.32 | 45.29 | 44.83 | 44.39 | 43.92 | 43.49 | 43.1 | 42.75 | 42.43 | 42.08 | 41.71 | 41.3 | 38.54 | 34.84 | 30.22
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | Steady Progression | Headroom (MW) | N/A | 37.7151 | 37.7107 | 37.7067 | 37.7001 | 37.6896 | 37.6623 | 37.6284 | 37.587 | 37.5478 | 37.5015 | 37.4535 | 37.4042 | 37.354 | 37.3046 | 37.2571 | 37.04 | 36.8383 | 36.6418
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | System Transformation | Headroom (MW) | N/A | 46.97 | 46.74 | 46.64 | 46.55 | 46.23 | 46.12 | 45.99 | 45.74 | 45.51 | 45.29 | 45.11 | 44.93 | 44.77 | 44.64 | 44.52 | 43.82 | 42.17 | 40.47
Bustleholm 132kV | Smethwick 132 11 (GT2B) | Smethwick 132/11kVDUMMY | Primary | 11 | -1.9688 | 52.5075 | WPD Best View | Headroom (MW) | N/A | 46.97 | 46.73 | 46.63 | 46.53 | 46.16 | 46.03 | 45.8 | 45.53 | 45.28 | 45.05 | 44.85 | 44.66 | 44.48 | 44.31 | 44.13 | 42.99 | 40.92 | 38.59
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Consumer Transformation | Headroom (MW) | N/A | 47.12 | 46.99 | 46.99 | 46.97 | 46.66 | 46.37 | 45.93 | 45.5 | 45.11 | 44.76 | 44.44 | 44.1 | 43.75 | 43.33 | 42.81 | 39.87 | 35.36 | 30.37
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Leading the Way | Headroom (MW) | N/A | 47.12 | 46.96 | 46.97 | 46.96 | 46.47 | 46.17 | 45.71 | 45.28 | 44.88 | 44.49 | 44.11 | 43.74 | 43.32 | 43.87 | 43.26 | 39.06 | 34.04 | 27.3
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | Steady Progression | Headroom (MW) | N/A | 36.4504 | 36.4367 | 36.4227 | 36.4064 | 36.3821 | 36.3328 | 36.2778 | 36.2143 | 36.1496 | 36.0774 | 36.0007 | 35.9215 | 35.8382 | 35.7506 | 35.6616 | 35.2463 | 36.159 | 35.8776
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | System Transformation | Headroom (MW) | N/A | 47.12 | 47.01 | 47.03 | 47.03 | 46.84 | 46.79 | 46.73 | 46.66 | 46.56 | 46.37 | 46.21 | 46.07 | 45.98 | 45.6948 | 45.395 | 45.5474 | 43.74 | 41.68
Bustleholm 132kV | Winson Green 132 11 (GT1) | Winson Green 132/11kVDUMMY | Primary | 11 | -1.9279 | 52.487 | WPD Best View | Headroom (MW) | N/A | 47.12 | 46.97 | 46.97 | 46.97 | 46.5 | 46.23 | 45.78 | 45.36 | 44.97 | 44.6 | 44.22 | 43.84 | 43.42 | 43.97 | 43.37 | 39.22 | 34.24 | 27.6
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Consumer Transformation | Headroom (MW) | N/A | 35.52 | 35.18 | 35.09 | 34.89 | 34.46 | 33.89 | 33.11 | 31.84 | 30.75 | 29.91 | 29.15 | 28.46 | 27.8 | 27.09 | 27.65 | 16.1 | 9.07 | 1.4
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Leading the Way | Headroom (MW) | N/A | 35.52 | 35.15 | 35.06 | 34.85 | 34.26 | 33.68 | 32.89 | 32 | 31.35 | 21.5 | 20.85 | 20.18 | 19.47 | 18.69 | 17.32 | 11.72 | 7.32 | 0.77
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | Steady Progression | Headroom (MW) | N/A | 35.52 | 35.23 | 35.18 | 35.05 | 34.86 | 34.81 | 34.75 | 34.15 | 33.56 | 32.97 | 32.46 | 32.01 | 31.72 | 31.49 | 31.31 | 30.76 | 29.9 | 28.9
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | System Transformation | Headroom (MW) | N/A | 35.52 | 35.21 | 35.15 | 34.99 | 34.7 | 34.64 | 34.58 | 33.94 | 33.19 | 26.53 | 26.1 | 25.75 | 25.47 | 25.22 | 24.72 | 23.45 | 20.71 | 17.72
Cellarhead 132kV | Boothen 132 11 (GT1B) | Boothen 132/33/11kVDUMMY | Primary | 11 | -2.181 | 52.9964 | WPD Best View | Headroom (MW) | N/A | 35.52 | 35.16 | 35.1 | 34.92 | 34.39 | 34.25 | 33.69 | 33.01 | 32.51 | 22.76 | 22.31 | 21.82 | 21.3 | 20.77 | 19.68 | 16.17 | 14.18 | 10.52
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Consumer Transformation | Headroom (MW) | N/A | 42.29 | 41.8 | 41.49 | 37.8 | 36.6 | 35.83 | 35.08 | 34.37 | 33.73 | 33.1 | 32.58 | 32.1 | 31.64 | 31 | 30.32 | 24.92 | 18.09 | 10.56
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Leading the Way | Headroom (MW) | N/A | 42.29 | 41.74 | 41.41 | 37.69 | 36.21 | 35.44 | 34.67 | 33.98 | 33.36 | 32.71 | 32.14 | 31.63 | 31.02 | 30.28 | 29.45 | 23.77 | 16.26 | 6.58
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | Steady Progression | Headroom (MW) | N/A | 42.29 | 41.96 | 41.81 | 41.66 | 41.4 | 41.26 | 41.1 | 37.62 | 37.49 | 37.34 | 37.21 | 37.11 | 37.02 | 36.94 | 36.89 | 36.85 | 35.98 | 34.42
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | System Transformation | Headroom (MW) | N/A | 42.29 | 41.88 | 41.66 | 41.44 | 40.85 | 37.19 | 36.81 | 36.45 | 36.12 | 35.77 | 35.48 | 35.24 | 35.05 | 34.91 | 34.81 | 33.39 | 30.12 | 26.89
Cellarhead 132kV | Burslem 132 11 (GT3A) | Burslem 132/33/11kVDUMMY | Primary | 11 | -2.2026 | 53.0509 | WPD Best View | Headroom (MW) | N/A | 42.29 | 41.75 | 41.44 | 37.74 | 36.35 | 35.62 | 34.9 | 34.24 | 33.65 | 33.02 | 32.48 | 31.99 | 31.45 | 30.74 | 29.96 | 24.65 | 17.59 | 8.44
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Consumer Transformation | Headroom (MW) | Thermal | 5.835 | 5.785 | 5.745 | 5.705 | 5.555 | 5.515 | 5.425 | 5.275 | 5.135 | 4.995 | 4.825 | 4.655 | 4.495 | 4.325 | 4.125 | 2.815 | 1.405 | -0.105
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Leading the Way | Headroom (MW) | Thermal | 5.835 | 5.775 | 5.745 | 5.695 | 5.525 | 5.515 | 5.455 | 5.315 | 5.195 | 5.065 | 4.895 | 4.735 | 4.565 | 4.405 | 4.215 | 2.885 | 1.475 | -0.175
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | Steady Progression | Headroom (MW) | N/A | 5.835 | 5.805 | 5.785 | 5.765 | 5.745 | 5.775 | 5.785 | 5.765 | 5.755 | 5.725 | 5.695 | 5.685 | 5.665 | 5.645 | 5.645 | 5.655 | 5.515 | 5.295
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | System Transformation | Headroom (MW) | N/A | 5.835 | 5.795 | 5.765 | 5.745 | 5.675 | 5.695 | 5.695 | 5.635 | 5.565 | 5.495 | 5.415 | 5.365 | 5.315 | 5.275 | 5.225 | 4.875 | 4.365 | 3.845
Cellarhead 132kV | Forsbrook 132 33 | CAULDON | Primary | 11 | -1.8862 | 53.0412 | WPD Best View | Headroom (MW) | N/A | 5.835 | 5.805 | 5.785 | 5.765 | 5.735 | 5.775 | 5.795 | 5.755 | 5.715 | 5.665 | 5.615 | 5.575 | 5.535 | 5.495 | 5.455 | 5.405 | 5.215 | 4.955
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Consumer Transformation | Headroom (MW) | N/A | 6.18 | 6.1 | 6.06 | 6.02 | 5.98 | 5.93 | 5.89 | 5.85 | 5.81 | 5.77 | 5.74 | 5.7 | 5.66 | 5.62 | 5.59 | 5.41 | 5.24 | 5.08
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Leading the Way | Headroom (MW) | N/A | 6.18 | 6.1 | 6.06 | 6.02 | 5.98 | 5.93 | 5.89 | 5.85 | 5.81 | 5.77 | 5.74 | 5.7 | 5.66 | 5.62 | 5.59 | 5.41 | 5.24 | 5.08
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | Steady Progression | Headroom (MW) | N/A | 6.18 | 6.1 | 6.06 | 6.02 | 5.98 | 5.93 | 5.89 | 5.85 | 5.81 | 5.77 | 5.74 | 5.7 | 5.66 | 5.62 | 5.59 | 5.41 | 5.24 | 5.08
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | System Transformation | Headroom (MW) | N/A | 6.18 | 6.1 | 6.06 | 6.02 | 5.98 | 5.93 | 5.89 | 5.85 | 5.81 | 5.77 | 5.74 | 5.7 | 5.66 | 5.62 | 5.59 | 5.41 | 5.24 | 5.08
Cellarhead 132kV | Forsbrook 132 33 | FROGHALL 33 11kV S STN | Primary | 11 | -1.9636 | 53.0224 | WPD Best View | Headroom (MW) | N/A | 6.18 | 6.1 | 6.06 | 6.02 | 5.98 | 5.93 | 5.89 | 5.85 | 5.81 | 5.77 | 5.74 | 5.7 | 5.66 | 5.62 | 5.59 | 5.41 | 5.24 | 5.08
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Consumer Transformation | Headroom (MW) | Thermal | 4.975 | 4.895 | 4.845 | 4.775 | 4.625 | 4.485 | 4.355 | 4.025 | 3.645 | 3.225 | 2.745 | 2.195 | 1.625 | 1.105 | 0.475 | -1.095 | -2.975 | -5.255
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Leading the Way | Headroom (MW) | Thermal | 4.975 | 4.895 | 4.835 | 4.755 | 4.595 | 4.445 | 4.315 | 4.175 | 4.045 | 3.925 | 3.815 | 3.715 | 3.265 | 2.815 | 2.335 | 0.625 | -1.405 | -3.005
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | Steady Progression | Headroom (MW) | N/A | 4.975 | 4.925 | 4.905 | 4.885 | 4.875 | 4.845 | 4.825 | 4.745 | 4.675 | 4.585 | 4.475 | 4.345 | 4.055 | 3.775 | 3.415 | 3.235 | 2.695 | 2.015
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | System Transformation | Headroom (MW) | Thermal | 4.975 | 4.915 | 4.875 | 4.835 | 4.785 | 4.715 | 4.645 | 4.385 | 4.055 | 3.695 | 3.245 | 2.745 | 2.225 | 1.775 | 1.215 | 0.445 | -0.845 | -2.425
Cellarhead 132kV | Forsbrook 132 33 | KINGSLEY HOLT 33 11kV S STN | Primary | 11 | -1.9694 | 53.0091 | WPD Best View | Headroom (MW) | N/A | 4.975 | 4.925 | 4.905 | 4.885 | 4.875 | 4.845 | 4.825 | 4.745 | 4.665 | 4.575 | 4.465 | 4.335 | 4.045 | 3.765 | 3.405 | 3.225 | 2.685 | 2.005
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Consumer Transformation | Headroom (MW) | Thermal | 10.44 | 10.41 | 10.41 | 10.4 | 10.12 | 9.86 | 9.6 | 9.31 | 9.03 | 8.79 | 8.36 | 7.92 | 7.47 | 7.01 | 6.49 | 4.11 | 0.79 | -3.02
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Leading the Way | Headroom (MW) | Thermal | 10.44 | 10.4 | 10.41 | 10.4 | 10.09 | 9.82 | 9.56 | 9.31 | 9.08 | 8.87 | 8.62 | 8.39 | 7.97 | 7.51 | 7.02 | 4.25 | 0.41 | -3.83
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | Steady Progression | Headroom (MW) | N/A | 10.44 | 10.42 | 10.45 | 10.47 | 10.48 | 10.48 | 10.48 | 10.48 | 10.47 | 10.47 | 10.46 | 10.45 | 10.39 | 10.28 | 10.13 | 9.92 | 9.25 | 8.39
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | System Transformation | Headroom (MW) | N/A | 10.44 | 10.42 | 10.44 | 10.45 | 10.44 | 10.43 | 10.32 | 10.17 | 10.04 | 9.91 | 9.65 | 9.37 | 9.11 | 8.83 | 8.5 | 7.68 | 5.84 | 3.81
Cellarhead 132kV | Forsbrook 132 33 | SIMPLEX 33 11kV S STN | Primary | 11 | -2.078 | 52.9662 | WPD Best View | Headroom (MW) | N/A | 10.44 | 10.42 | 10.43 | 10.44 | 10.42 | 10.41 | 10.39 | 10.3 | 10.23 | 10.16 | 10.06 | 9.97 | 9.81 | 9.62 | 9.36 | 8.54 | 7.19 | 5.32
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Consumer Transformation | Headroom (MW) | N/A | 49.05 | 48.45 | 48.03 | 47.52 | 46.03 | 44.92 | 43.85 | 42.43 | 40.97 | 39.59 | 38.2 | 36.74 | 35.15 | 33.61 | 31.87 | 23.38 | 15.64 | 0.26
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Leading the Way | Headroom (MW) | Thermal | 49.05 | 48.39 | 47.96 | 47.43 | 45.69 | 44.51 | 43.39 | 42.36 | 41.37 | 40.44 | 39.5 | 38.51 | 36.97 | 35.42 | 36.89 | 22.86 | 10.61 | -3.59
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | Steady Progression | Headroom (MW) | N/A | 49.05 | 48.67 | 48.52 | 48.38 | 48.1 | 47.86 | 47.62 | 47.05 | 46.51 | 45.95 | 45.4 | 44.9 | 44.32 | 43.79 | 43.22 | 42.45 | 40.63 | 37.79
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | System Transformation | Headroom (MW) | N/A | 49.05 | 48.57 | 48.32 | 48.03 | 47.35 | 46.82 | 46.24 | 45.3 | 44.34 | 43.41 | 42.41 | 41.4 | 40.42 | 39.6 | 39.11 | 32.91 | 27.04 | 20.84
Cellarhead 132kV | Longton 132 11 (GT3A) | Longton 132/33/11kV | Primary | 11 | -2.1333 | 52.9741 | WPD Best View | Headroom (MW) | Thermal | 49.05 | 48.41 | 47.99 | 47.47 | 45.79 | 44.67 | 43.61 | 42.31 | 41.06 | 39.86 | 38.65 | 37.41 | 35.95 | 34.47 | 32.79 | 24.45 | 13.66 | -0.35
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Consumer Transformation | Headroom (MW) | Thermal | 4.1 | 4.06 | 4.01 | 3.96 | 3.85 | 3.75 | 3.17 | 2.15 | 1.41 | 0.72 | 0.03 | -0.62 | -1.25 | -1.94 | -2.7 | -6.29 | -10.63 | -15.15
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Leading the Way | Headroom (MW) | Thermal | 4.1 | 4.06 | 4.02 | 3.97 | 3.87 | 3.77 | 3.15 | 2.63 | 2.22 | 1.63 | 1.11 | 0.63 | 0.11 | -0.43 | -1.03 | -3.88 | -7.43 | -11.25
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | Steady Progression | Headroom (MW) | N/A | 4.1 | 4.07 | 4.06 | 4.04 | 4.02 | 4 | 3.98 | 3.95 | 3.85 | 3.34 | 3.24 | 3.13 | 2.98 | 2.9 | 2.84 | 2.69 | 2.46 | 2.18
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | System Transformation | Headroom (MW) | Thermal | 4.1 | 4.07 | 4.04 | 4.02 | 3.97 | 3.92 | 3.87 | 3.8 | 3.32 | 3.09 | 2.83 | 2.61 | 2.43 | 2.3 | 2.14 | 1.47 | 0.41 | -0.71
Cellarhead 132kV | Meaford 'C' 132 33 | BEARSTONE | Primary | 11 | -2.4119 | 52.9473 | WPD Best View | Headroom (MW) | Thermal | 4.1 | 4.07 | 4.05 | 4.02 | 3.99 | 3.95 | 3.91 | 3.86 | 3.4 | 3.18 | 2.94 | 2.74 | 2.57 | 2.46 | 2.32 | 1.7 | 0.71 | -0.37
Cellarhead 132kV | Meaford 'C' 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Consumer Transformation | Headroom (MW) | Thermal | 13.81 | 13.7 | 13.61 | 13.5 | 13.16 | 12.91 | 12.67 | 12.25 | 11.79 | 11.31 | 10.71 | 10.04 | 9.32 | 8.66 | 7.87 | 5.51 | 2.56 | -0.86
Cellarhead 132kV | Meaford 'C' 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Leading the Way | Headroom (MW) | N/A | 13.81 | 13.68 | 13.59 | 13.48 | 13.07 | 12.81 | 12.56 | 12.32 | 12.11 | 11.91 | 11.7 | 11.47 | 10.86 | 10.27 | 9.65 | 7.04 | 3.55 | 0.51
Cellarhead 132kV | Meaford 'C' 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | Steady Progression | Headroom (MW) | N/A | 13.81 | 13.75 | 13.73 | 13.71 | 13.67 | 13.63 | 13.59 | 13.49 | 13.41 | 13.3 | 13.17 | 13.02 | 12.71 | 12.41 | 12.03 | 11.55 | 10.85 | 9.94
Cellarhead 132kV | Meaford 'C' 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | System Transformation | Headroom (MW) | N/A | 13.81 | 13.73 | 13.68 | 13.62 | 13.48 | 13.37 | 13.24 | 12.93 | 12.57 | 12.18 | 11.68 | 11.12 | 10.55 | 10.05 | 9.43 | 8.28 | 6.39 | 4.24
Cellarhead 132kV | Meaford 'C' 132 33 | CHEADLE 33 11kV S STN | Primary | 11 | -2.0048 | 52.9813 | WPD Best View | Headroom (MW) | N/A | 13.81 | 13.75 | 13.72 | 13.7 | 13.64 | 13.59 | 13.53 | 13.42 | 13.32 | 13.2 | 13.05 | 12.89 | 12.57 | 12.26 | 11.85 | 11.26 | 10.43 | 9.36
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Consumer Transformation | Headroom (MW) | Thermal | 5.38 | 5.32 | 5.28 | 5.24 | 5.12 | 5.04 | 4.94 | 4.63 | 4.26 | 3.85 | 3.29 | 2.66 | 1.99 | 1.4 | 0.66 | -0.77 | -2.46 | -4.48
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Leading the Way | Headroom (MW) | Thermal | 5.38 | 5.31 | 5.28 | 5.23 | 5.08 | 4.99 | 4.89 | 4.79 | 4.68 | 4.58 | 4.48 | 4.38 | 3.87 | 3.39 | 2.88 | 1.3 | -0.83 | -1.84
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | Steady Progression | Headroom (MW) | N/A | 5.38 | 5.34 | 5.32 | 5.3 | 5.27 | 5.24 | 5.21 | 5.14 | 5.06 | 4.96 | 4.83 | 4.68 | 4.34 | 4 | 3.56 | 2.99 | 2.34 | 1.63
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | System Transformation | Headroom (MW) | Thermal | 5.38 | 5.33 | 5.3 | 5.27 | 5.21 | 5.16 | 5.11 | 4.84 | 4.5 | 4.12 | 3.6 | 3.01 | 2.4 | 1.86 | 1.17 | 0.18 | -1.2 | -2.89
Cellarhead 132kV | Meaford 'C' 132 33 | COTES HEATH 33 11kV S STN | Primary | 11 | -2.2481 | 52.9116 | WPD Best View | Headroom (MW) | N/A | 5.38 | 5.34 | 5.32 | 5.3 | 5.27 | 5.24 | 5.21 | 5.14 | 5.06 | 4.96 | 4.83 | 4.68 | 4.34 | 4 | 3.56 | 2.99 | 2.34 | 1.63
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Consumer Transformation | Headroom (MW) | Thermal | 0.6 | 0.54 | 0.51 | 0.46 | 0.32 | 0.25 | 0.18 | 0.1 | 0.03 | -0.04 | -0.11 | -0.17 | -0.24 | -0.31 | -0.38 | -1.17 | -1.9 | -2.69
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Leading the Way | Headroom (MW) | Thermal | 0.6 | 0.54 | 0.5 | 0.45 | 0.29 | 0.22 | 0.16 | 0.08 | 0 | -0.06 | -0.14 | -0.21 | -0.29 | -0.38 | -0.47 | -1.3 | -2.09 | -3.12
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | Steady Progression | Headroom (MW) | N/A | 0.6 | 0.56 | 0.55 | 0.53 | 0.5 | 0.5 | 0.48 | 0.47 | 0.45 | 0.43 | 0.41 | 0.4 | 0.39 | 0.38 | 0.37 | 0.38 | 0.29 | 0.13
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | System Transformation | Headroom (MW) | Thermal | 0.6 | 0.56 | 0.53 | 0.5 | 0.44 | 0.41 | 0.38 | 0.34 | 0.3 | 0.26 | 0.23 | 0.2 | 0.18 | 0.16 | 0.14 | -0.11 | -0.44 | -0.78
Cellarhead 132kV | Meaford 'C' 132 33 | ECCLESHALL PRIMARY 33 11kV S STN | Primary | 11 | -2.2551 | 52.8527 | WPD Best View | Headroom (MW) | N/A | 0.6 | 0.56 | 0.55 | 0.53 | 0.5 | 0.5 | 0.48 | 0.47 | 0.45 | 0.43 | 0.41 | 0.4 | 0.39 | 0.38 | 0.37 | 0.38 | 0.29 | 0.13
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Consumer Transformation | Headroom (MW) | Thermal | 1.63 | 1.56 | 1.51 | 1.45 | 1.31 | 1.19 | 1.07 | 0.93 | 0.79 | 0.67 | 0.54 | 0.43 | 0.32 | 0.2 | 0.05 | -0.69 | -1.61 | -2.64
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Leading the Way | Headroom (MW) | Thermal | 1.63 | 1.56 | 1.5 | 1.44 | 1.29 | 1.17 | 1.05 | 0.91 | 0.78 | 0.65 | 0.52 | 0.4 | 0.28 | 0.15 | 0 | -0.87 | -1.98 | -3.43
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | Steady Progression | Headroom (MW) | N/A | 1.63 | 1.59 | 1.56 | 1.54 | 1.52 | 1.49 | 1.47 | 1.44 | 1.41 | 1.39 | 1.36 | 1.35 | 1.34 | 1.34 | 1.33 | 1.39 | 1.31 | 1.09
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | System Transformation | Headroom (MW) | Thermal | 1.63 | 1.57 | 1.54 | 1.5 | 1.44 | 1.38 | 1.31 | 1.24 | 1.17 | 1.1 | 1.03 | 0.99 | 0.95 | 0.92 | 0.87 | 0.73 | 0.3 | -0.12
Cellarhead 132kV | Meaford 'C' 132 33 | GNOSALL 33 11kV S STN | Primary | 11 | -2.2577 | 52.7821 | WPD Best View | Headroom (MW) | N/A | 1.63 | 1.59 | 1.56 | 1.54 | 1.51 | 1.48 | 1.43 | 1.38 | 1.32 | 1.26 | 1.2 | 1.16 | 1.11 | 1.08 | 1.04 | 1.03 | 0.88 | 0.6
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Consumer Transformation | Headroom (MW) | N/A | 2.5 | 2.47 | 2.45 | 2.42 | 2.35 | 2.3 | 2.23 | 2.16 | 2.09 | 2.03 | 1.97 | 1.92 | 1.86 | 1.79 | 1.72 | 1.37 | 0.95 | 0.49
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Leading the Way | Headroom (MW) | N/A | 2.5 | 2.47 | 2.45 | 2.42 | 2.34 | 2.28 | 2.22 | 2.15 | 2.09 | 2.03 | 1.96 | 1.89 | 1.82 | 1.75 | 1.68 | 1.28 | 0.78 | 0.13
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | Steady Progression | Headroom (MW) | N/A | 2.5 | 2.48 | 2.48 | 2.47 | 2.46 | 2.45 | 2.43 | 2.42 | 2.41 | 2.39 | 2.38 | 2.37 | 2.37 | 2.36 | 2.36 | 2.37 | 2.33 | 2.23
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | System Transformation | Headroom (MW) | N/A | 2.5 | 2.48 | 2.46 | 2.45 | 2.42 | 2.39 | 2.36 | 2.32 | 2.28 | 2.25 | 2.22 | 2.19 | 2.18 | 2.16 | 2.14 | 2.06 | 1.87 | 1.68
Cellarhead 132kV | Meaford 'C' 132 33 | HIGH OFFLEY 33 11kV S STN | Primary | 11 | -2.3205 | 52.832 | WPD Best View | Headroom (MW) | N/A | 2.5 | 2.48 | 2.48 | 2.47 | 2.46 | 2.44 | 2.42 | 2.4 | 2.39 | 2.37 | 2.34 | 2.33 | 2.32 | 2.31 | 2.3 | 2.3 | 2.25 | 2.14
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Consumer Transformation | Headroom (MW) | Thermal | 1.41 | 1.39 | 1.37 | 1.34 | 1.27 | 1.21 | 1.06 | 0.54 | 0.01 | -0.57 | -1.28 | -2.07 | -2.89 | -3.65 | -4.56 | -6.51 | -8.85 | -11.58
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Leading the Way | Headroom (MW) | Thermal | 1.41 | 1.39 | 1.37 | 1.34 | 1.26 | 1.2 | 1.03 | 0.88 | 0.75 | 0.59 | 0.44 | 0.29 | -0.34 | -0.93 | -1.56 | -3.53 | -6.15 | -7.54
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | Steady Progression | Headroom (MW) | Thermal | 1.41 | 1.4 | 1.4 | 1.39 | 1.38 | 1.37 | 1.36 | 1.28 | 1.18 | 0.99 | 0.84 | 0.66 | 0.26 | -0.12 | -0.62 | -1.26 | -1.95 | -2.66
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | System Transformation | Headroom (MW) | Thermal | 1.41 | 1.39 | 1.38 | 1.37 | 1.34 | 1.31 | 1.27 | 0.96 | 0.48 | 0 | -0.61 | -1.29 | -1.99 | -2.61 | -3.38 | -4.54 | -6.05 | -7.91
Cellarhead 132kV | Meaford 'C' 132 33 | HILL CHORLTON 33 11kV S STN | Primary | 11 | -2.2974 | 52.9521 | WPD Best View | Headroom (MW) | Thermal | 1.41 | 1.4 | 1.4 | 1.39 | 1.38 | 1.37 | 1.36 | 1.28 | 1.18 | 0.99 | 0.84 | 0.66 | 0.26 | -0.12 | -0.62 | -1.26 | -1.95 | -2.66
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Consumer Transformation | Headroom (MW) | N/A | 3.85 | 3.8 | 3.77 | 3.74 | 3.64 | 3.57 | 3.5 | 3.42 | 3.35 | 3.28 | 3.21 | 3.15 | 3.08 | 3.01 | 2.95 | 2.53 | 2.06 | 1.54
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Leading the Way | Headroom (MW) | N/A | 3.85 | 3.8 | 3.77 | 3.73 | 3.61 | 3.54 | 3.46 | 3.39 | 3.32 | 3.25 | 3.17 | 3.11 | 3.03 | 2.97 | 2.89 | 2.46 | 1.92 | 1.23
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | Steady Progression | Headroom (MW) | N/A | 3.85 | 3.82 | 3.8 | 3.79 | 3.77 | 3.75 | 3.73 | 3.7 | 3.68 | 3.66 | 3.64 | 3.63 | 3.61 | 3.6 | 3.59 | 3.56 | 3.49 | 3.36
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | System Transformation | Headroom (MW) | N/A | 3.85 | 3.81 | 3.79 | 3.77 | 3.72 | 3.68 | 3.64 | 3.59 | 3.55 | 3.51 | 3.47 | 3.44 | 3.41 | 3.38 | 3.35 | 3.25 | 3.01 | 2.78
Cellarhead 132kV | Meaford 'C' 132 33 | HINSTOCK 33 11kV S STN | Primary | 11 | -2.4509 | 52.8368 | WPD Best View | Headroom (MW) | N/A | 3.85 | 3.81 | 3.79 | 3.77 | 3.72 | 3.68 | 3.64 | 3.6 | 3.56 | 3.52 | 3.48 | 3.45 | 3.42 | 3.39 | 3.36 | 3.26 | 3.03 | 2.79
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Consumer Transformation | Headroom (MW) | Thermal | 4.13 | 4.08 | 4.04 | 3.99 | 3.86 | 3.75 | 3.64 | 3.28 | 2.88 | 2.41 | 1.66 | 0.81 | -0.07 | -0.87 | -1.86 | -3.72 | -6.11 | -9.03
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Leading the Way | Headroom (MW) | Thermal | 4.13 | 4.08 | 4.04 | 3.98 | 3.84 | 3.73 | 3.6 | 3.48 | 3.36 | 3.23 | 3.09 | 2.95 | 2.25 | 1.59 | 0.91 | -1.18 | -4.24 | -5.69
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | Steady Progression | Headroom (MW) | Thermal | 4.13 | 4.11 | 4.09 | 4.08 | 4.06 | 4.04 | 4.02 | 3.94 | 3.86 | 3.76 | 3.59 | 3.4 | 2.95 | 2.52 | 1.94 | 1.22 | 0.31 | -0.68
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | System Transformation | Headroom (MW) | Thermal | 4.13 | 4.1 | 4.07 | 4.04 | 3.99 | 3.93 | 3.87 | 3.57 | 3.2 | 2.78 | 2.09 | 1.31 | 0.5 | -0.23 | -1.13 | -2.44 | -4.39 | -6.81
Cellarhead 132kV | Meaford 'C' 132 33 | HOOKGATE 33 11kV S STN | Primary | 11 | -2.3799 | 52.9129 | WPD Best View | Headroom (MW) | Thermal | 4.13 | 4.11 | 4.09 | 4.08 | 4.06 | 4.04 | 4.01 | 3.93 | 3.84 | 3.74 | 3.56 | 3.36 | 2.91 | 2.47 | 1.89 | 1.16 | 0.24 | -0.75
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Consumer Transformation | Headroom (MW) | N/A | 20.58 | 20.33 | 20.18 | 13.34 | 12.89 | 12.57 | 12.23 | 11.9 | 11.59 | 11.35 | 11.12 | 10.91 | 10.66 | 10.4 | 10.1 | 8.02 | 5.24 | 2.16
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Leading the Way | Headroom (MW) | N/A | 20.58 | 20.31 | 20.15 | 13.3 | 12.76 | 12.44 | 12.1 | 11.77 | 11.49 | 11.28 | 11.07 | 10.88 | 10.61 | 10.32 | 9.98 | 7.69 | 4.55 | 0.48
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | Steady Progression | Headroom (MW) | N/A | 20.58 | 20.4 | 20.33 | 13.59 | 13.53 | 13.46 | 13.39 | 13.31 | 13.24 | 13.2 | 13.17 | 13.16 | 13.14 | 13.11 | 13.1 | 13.19 | 12.83 | 12.16
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | System Transformation | Headroom (MW) | N/A | 20.58 | 20.37 | 20.26 | 13.49 | 13.3 | 13.15 | 12.98 | 12.81 | 12.65 | 12.54 | 12.45 | 12.39 | 12.29 | 12.21 | 12.13 | 11.76 | 10.45 | 9.04
Cellarhead 132kV | Meaford 'C' 132 33 | MARKET DRAYTON 33 11kV S STN | Primary | 11 | -2.4819 | 52.9019 | WPD Best View | Headroom (MW) | N/A | 20.58 | 20.37 | 20.26 | 13.49 | 13.3 | 13.16 | 13 | 12.85 | 12.71 | 12.62 | 12.55 | 12.5 | 12.42 | 12.35 | 12.3 | 11.96 | 10.68 | 9.3
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Consumer Transformation | Headroom (MW) | Thermal | 17.84 | 17.66 | 17.82 | 17.94 | 17.89 | 17.73 | 17.39 | 16.41 | 15.35 | 14.25 | 12.88 | 11.41 | 9.86 | 8.34 | 6.59 | 0.31 | -7.55 | -16.22
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Leading the Way | Headroom (MW) | Thermal | 17.84 | 17.64 | 17.83 | 17.99 | 17.9 | 17.7 | 17.27 | 16.78 | 16.18 | 15.52 | 14.85 | 14.2 | 12.91 | 11.62 | 10.19 | 3.78 | -4.61 | -12.09
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | Steady Progression | Headroom (MW) | N/A | 17.84 | 17.7 | 17.86 | 17.99 | 18.08 | 18.07 | 18.04 | 18.01 | 17.94 | 17.7 | 17.61 | 17.51 | 17.24 | 16.68 | 15.96 | 14.92 | 13.3 | 11.32
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | System Transformation | Headroom (MW) | Thermal | 17.84 | 17.68 | 17.86 | 18 | 18.05 | 18.05 | 18.04 | 17.92 | 17.34 | 16.64 | 15.63 | 14.53 | 13.37 | 12.37 | 11.18 | 8.53 | 4.06 | -0.94
Cellarhead 132kV | Meaford 'C' 132 33 | Meaford C 132/33/11kVDUMMY | Primary | 11 | -2.1673 | 52.9315 | WPD Best View | Headroom (MW) | N/A | 17.84 | 17.7 | 17.86 | 17.99 | 18.08 | 18.07 | 18.04 | 18.01 | 17.94 | 17.71 | 17.61 | 17.51 | 17.21 | 16.65 | 15.93 | 14.89 | 13.28 | 11.29
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Consumer Transformation | Headroom (MW) | Thermal | 12.41 | 12.37 | 12.31 | 12.25 | 12.04 | 11.89 | 11.71 | 10.78 | 9.65 | 8.35 | 6.67 | 4.75 | 2.7 | 0.89 | -1.35 | -5.35 | -9.91 | -15.51
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Leading the Way | Headroom (MW) | Thermal | 12.41 | 12.36 | 12.31 | 12.24 | 11.99 | 11.82 | 11.62 | 11.41 | 11.19 | 10.97 | 10.75 | 10.54 | 8.95 | 7.52 | 6.01 | 1.66 | -4.22 | -6.42
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | Steady Progression | Headroom (MW) | N/A | 12.41 | 12.39 | 12.37 | 12.35 | 12.31 | 12.29 | 12.25 | 12.04 | 11.83 | 11.55 | 11.17 | 10.7 | 9.62 | 8.58 | 7.19 | 5.42 | 3.53 | 1.53
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | System Transformation | Headroom (MW) | Thermal | 12.41 | 12.38 | 12.35 | 12.31 | 12.21 | 12.14 | 12.04 | 11.2 | 10.13 | 8.9 | 7.3 | 5.47 | 3.53 | 1.83 | -0.29 | -3.38 | -7.33 | -12.23
Cellarhead 132kV | Meaford 'C' 132 33 | TEAN 33 11kV S STN | Primary | 11 | -1.9903 | 52.9585 | WPD Best View | Headroom (MW) | Thermal | 12.41 | 12.39 | 12.37 | 12.35 | 12.3 | 12.26 | 12.21 | 11.68 | 11 | 10.22 | 9.21 | 8.04 | 6.52 | 5.14 | 3.38 | 1.02 | -1.8 | -5.21
Cellarhead 132kV | Newcastle 132 11 (GT5) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Consumer Transformation | Headroom (MW) | Thermal | 60.47 | 54.92 | 51.17 | 50.58 | 49.05 | 47.93 | 46.81 | 45.52 | 44.25 | 43.11 | 41.92 | 40.71 | 39.46 | 38.07 | 39.52 | 22.52 | 10.77 | -0.89
Cellarhead 132kV | Newcastle 132 11 (GT5) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Leading the Way | Headroom (MW) | N/A | 60.47 | 54.85 | 51.09 | 50.46 | 48.7 | 47.55 | 46.54 | 45.65 | 45.19 | 29.98 | 29.12 | 28.68 | 25.37 | 23.95 | 22.4 | 13.54 | 9.33 | 1.38
Cellarhead 132kV | Newcastle 132 11 (GT5) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | Steady Progression | Headroom (MW) | N/A | 60.47 | 55.15 | 51.74 | 51.55 | 51.28 | 44.66 | 44.29 | 43.27 | 42.29 | 41.36 | 40.5 | 39.74 | 39.12 | 38.62 | 38.15 | 38 | 36.37 | 33.66
Cellarhead 132kV | Newcastle 132 11 (GT5) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | System Transformation | Headroom (MW) | N/A | 60.47 | 55.04 | 51.51 | 51.11 | 50.42 | 49.9 | 49.28 | 48.46 | 47.63 | 37.28 | 36.46 | 35.73 | 33.63 | 32.96 | 32.24 | 29.78 | 26.19 | 21.07
Cellarhead 132kV | Newcastle 132 11 (GT5) | Newcastle 132/11kVDUMMY | Primary | 11 | -2.2423 | 53.029 | WPD Best View | Headroom (MW) | N/A | 60.47 | 55.12 | 51.69 | 51.47 | 51.05 | 44.38 | 43.96 | 42.93 | 41.9 | 40.96 | 40.06 | 39.65 | 37.02 | 36.48 | 35.94 | 35.11 | 33.26 | 30.28
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Consumer Transformation | Headroom (MW) | Thermal | 4.59 | 4.5 | 4.43 | 4.33 | 4.11 | 3.91 | 3.72 | 3.2 | 2.62 | 1.99 | 1.15 | 0.2 | -0.79 | -1.73 | -2.87 | -5.86 | -9.1 | -12.96
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Leading the Way | Headroom (MW) | Thermal | 4.59 | 4.5 | 4.41 | 4.31 | 4.06 | 3.86 | 3.65 | 3.46 | 3.28 | 3.13 | 2.98 | 2.83 | 2.01 | 1.23 | 0.41 | -2.91 | -6.9 | -9.54
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | Steady Progression | Headroom (MW) | Thermal | 4.59 | 4.54 | 4.52 | 4.5 | 4.47 | 4.44 | 4.41 | 4.3 | 4.19 | 4.05 | 3.87 | 3.65 | 3.14 | 2.66 | 2.02 | 1.29 | 0.3 | -0.88
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | System Transformation | Headroom (MW) | Thermal | 4.59 | 4.52 | 4.48 | 4.43 | 4.34 | 4.25 | 4.15 | 3.74 | 3.22 | 2.65 | 1.88 | 1 | 0.08 | -0.72 | -1.71 | -3.46 | -5.83 | -8.65
Cellarhead 132kV | Newcastle 132 33 | SCOT HAY 33 11kV S STN | Primary | 11 | -2.2915 | 53.0213 | WPD Best View | Headroom (MW) | Thermal | 4.59 | 4.54 | 4.52 | 4.5 | 4.47 | 4.44 | 4.41 | 4.3 | 4.19 | 4.05 | 3.87 | 3.65 | 3.14 | 2.66 | 2.02 | 1.29 | 0.3 | -0.88
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Consumer Transformation | Headroom (MW) | N/A | 14.57 | 14.47 | 14.41 | 14.35 | 14.22 | 14.03 | 13.77 | 13.37 | 12.95 | 12.47 | 11.94 | 11.34 | 10.7 | 10.1 | 9.4 | 6.93 | 3.79 | 0.19
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Leading the Way | Headroom (MW) | N/A | 14.57 | 14.46 | 14.4 | 14.33 | 14.15 | 13.96 | 13.69 | 13.45 | 13.22 | 13 | 12.77 | 12.56 | 12 | 11.44 | 10.84 | 8.08 | 4.45 | 0.87
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | Steady Progression | Headroom (MW) | N/A | 14.57 | 14.49 | 14.46 | 14.42 | 14.38 | 14.36 | 14.33 | 14.3 | 14.27 | 14.24 | 14.2 | 14.15 | 13.9 | 13.66 | 13.36 | 12.93 | 12.27 | 11.36
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | System Transformation | Headroom (MW) | N/A | 14.57 | 14.48 | 14.43 | 14.39 | 14.31 | 14.29 | 14.25 | 14.07 | 13.74 | 13.39 | 12.96 | 12.49 | 12 | 11.58 | 11.05 | 9.93 | 8.04 | 5.95
Cellarhead 132kV | Newcastle 132 33 | TALKE 33 11kV S STN | Primary | 11 | -2.2633 | 53.0823 | WPD Best View | Headroom (MW) | N/A | 14.57 | 14.49 | 14.46 | 14.42 | 14.38 | 14.36 | 14.33 | 14.3 | 14.27 | 14.24 | 14.2 | 14.15 | 13.9 | 13.66 | 13.36 | 12.93 | 12.27 | 11.36
Cellarhead 132kV | Stagefields 132 11 (GT3A) | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Consumer Transformation | Headroom (MW) | Thermal | 14.57 | 14.23 | 14.11 | 13.87 | 12.97 | 11.92 | 10.86 | 9.71 | 8.63 | 7.55 | 6.53 | 5.53 | 4.49 | 3.45 | 2.31 | -5.48 | -14.82 | -25.02
Cellarhead 132kV | Stagefields 132 11 (GT3A) | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Leading the Way | Headroom (MW) | Thermal | 14.57 | 14.19 | 14.06 | 13.8 | 12.58 | 11.49 | 10.41 | 9.18 | 8.05 | 6.89 | 5.74 | 4.61 | 3.41 | 2.29 | 1.03 | -6.86 | -17.05 | -30.18
Cellarhead 132kV | Stagefields 132 11 (GT3A) | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | Steady Progression | Headroom (MW) | N/A | 14.57 | 14.31 | 14.25 | 14.09 | 13.83 | 13.73 | 13.64 | 13.53 | 13.42 | 13.29 | 13.16 | 13.03 | 12.9 | 12.76 | 12.62 | 11.88 | 10.85 | 9.13
Cellarhead 132kV | Stagefields 132 11 (GT3A) | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | System Transformation | Headroom (MW) | Thermal | 14.57 | 14.28 | 14.19 | 14.01 | 13.57 | 13.46 | 13.16 | 12.54 | 11.96 | 11.35 | 10.8 | 10.28 | 9.79 | 9.41 | 9.05 | 6.89 | 2.32 | -2.31
Cellarhead 132kV | Stagefields 132 11 (GT3A) | Stagefields 132/33/11kV | Primary | 11 | -2.1695 | 53.0136 | WPD Best View | Headroom (MW) | Thermal | 14.57 | 14.2 | 14.08 | 13.83 | 12.79 | 11.78 | 10.76 | 9.6 | 8.53 | 7.42 | 6.32 | 5.25 | 4.11 | 3.1 | 1.97 | -5.19 | -14.49 | -26.52
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Consumer Transformation | Headroom (MW) | Thermal | 6.975 | 6.935 | 6.925 | 4.835 | 4.775 | 4.745 | 4.445 | 3.855 | 3.325 | 2.795 | 2.215 | 1.585 | 0.945 | 0.295 | -0.435 | -2.925 | -5.685 | -9.085
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Leading the Way | Headroom (MW) | Thermal | 6.975 | 6.935 | 6.925 | 4.845 | 4.755 | 4.725 | 4.425 | 4.155 | 3.945 | 3.685 | 3.435 | 3.205 | 2.725 | 2.185 | 1.635 | -0.675 | -2.635 | -4.645
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | Steady Progression | Headroom (MW) | N/A | 6.975 | 6.945 | 6.945 | 4.875 | 4.855 | 4.855 | 4.805 | 4.795 | 4.755 | 4.585 | 4.535 | 4.405 | 4.165 | 3.925 | 3.635 | 3.265 | 2.725 | 2.035
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | System Transformation | Headroom (MW) | Thermal | 6.975 | 6.945 | 6.945 | 4.865 | 4.835 | 4.825 | 4.785 | 4.715 | 4.325 | 3.995 | 3.575 | 3.135 | 2.685 | 2.285 | 1.815 | 0.905 | -0.245 | -1.855
Cellarhead 132kV | Whitfield 132 33 | CHEDDLETON 33 11kV S STN | Primary | 11 | -2.0361 | 53.0712 | WPD Best View | Headroom (MW) | N/A | 6.975 | 6.945 | 6.945 | 4.875 | 4.855 | 4.855 | 4.805 | 4.795 | 4.755 | 4.585 | 4.535 | 4.405 | 4.165 | 3.925 | 3.635 | 3.265 | 2.725 | 2.035
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Consumer Transformation | Headroom (MW) | N/A | 26.44 | 26.22 | 26.11 | 25.92 | 25.45 | 25.07 | 24.4 | 23.64 | 22.97 | 22.2 | 21.59 | 20.98 | 20.32 | 19.63 | 18.87 | 14.3 | 9.05 | 3.29
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Leading the Way | Headroom (MW) | N/A | 26.44 | 26.18 | 26.05 | 25.93 | 25.17 | 24.76 | 24.05 | 23.66 | 23.35 | 22.8 | 22.28 | 21.77 | 21.15 | 20.47 | 19.68 | 14.99 | 9.38 | 2.3
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | Steady Progression | Headroom (MW) | N/A | 26.44 | 26.28 | 26.21 | 26.15 | 25.98 | 25.9 | 25.82 | 25.8 | 25.77 | 25.59 | 25.52 | 25.45 | 25.37 | 25.3 | 25.24 | 24.93 | 24.41 | 23.66
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | System Transformation | Headroom (MW) | N/A | 26.44 | 26.25 | 26.16 | 26.08 | 25.78 | 25.68 | 25.56 | 25.55 | 25.22 | 24.75 | 24.42 | 24.11 | 23.82 | 23.57 | 23.3 | 22.12 | 19.77 | 17.33
Cellarhead 132kV | Whitfield 132 33 | CONGLETON 33 11kV S STN | Primary | 11 | -2.2039 | 53.1633 | WPD Best View | Headroom (MW) | N/A | 26.44 | 26.28 | 26.21 | 26.15 | 25.98 | 25.9 | 25.82 | 25.8 | 25.77 | 25.59 | 25.52 | 25.45 | 25.37 | 25.3 | 25.24 | 24.93 | 24.41 | 23.66
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Consumer Transformation | Headroom (MW) | Thermal | 14.04 | 13.96 | 13.91 | 13.85 | 13.69 | 13.43 | 13.18 | 12.57 | 11.87 | 11.12 | 10.11 | 9 | 7.82 | 6.74 | 5.43 | 2.2 | -2.01 | -6.99
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Leading the Way | Headroom (MW) | Thermal | 14.04 | 13.96 | 13.89 | 13.82 | 13.64 | 13.37 | 13.1 | 12.84 | 12.6 | 12.37 | 12.11 | 11.86 | 10.9 | 9.98 | 9 | 5.29 | 0.19 | -3.7
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | Steady Progression | Headroom (MW) | N/A | 14.04 | 13.98 | 13.95 | 13.92 | 13.89 | 13.86 | 13.83 | 13.8 | 13.77 | 13.7 | 13.49 | 13.24 | 12.69 | 12.15 | 11.44 | 10.53 | 9.39 | 7.94
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | System Transformation | Headroom (MW) | Thermal | 14.04 | 13.97 | 13.93 | 13.88 | 13.83 | 13.78 | 13.74 | 13.3 | 12.72 | 12.06 | 11.18 | 10.2 | 9.17 | 8.25 | 7.12 | 5.27 | 2.34 | -1.08
Cellarhead 132kV | Whitfield 132 33 | ENDON 33 11kV S STN | Primary | 11 | -2.1041 | 53.0703 | WPD Best View | Headroom (MW) | N/A | 14.04 | 13.97 | 13.92 | 13.87 | 13.79 | 13.74 | 13.6 | 13.36 | 13.13 | 12.9 | 12.6 | 12.24 | 11.55 | 10.88 | 10.01 | 8.02 | 5.54 | 2.44
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Consumer Transformation | Headroom (MW) | Thermal | 4.91 | 4.84 | 4.76 | 4.66 | 4.46 | 4.29 | 4.13 | 3.97 | 3.83 | 3.7 | 3.56 | 3.43 | 3.29 | 3.15 | 3 | 1.86 | 0.23 | -1.59
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Leading the Way | Headroom (MW) | Thermal | 4.91 | 4.83 | 4.75 | 4.65 | 4.44 | 4.26 | 4.1 | 3.94 | 3.8 | 3.68 | 3.52 | 3.37 | 3.22 | 3.05 | 2.85 | 1.5 | -0.3 | -2.74
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | Steady Progression | Headroom (MW) | N/A | 4.91 | 4.87 | 4.85 | 4.83 | 4.8 | 4.77 | 4.74 | 4.71 | 4.68 | 4.65 | 4.62 | 4.6 | 4.58 | 4.58 | 4.57 | 4.49 | 4.26 | 3.92
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | System Transformation | Headroom (MW) | N/A | 4.91 | 4.86 | 4.81 | 4.75 | 4.68 | 4.6 | 4.52 | 4.44 | 4.37 | 4.3 | 4.25 | 4.2 | 4.16 | 4.12 | 4.07 | 3.7 | 2.99 | 2.28
Cellarhead 132kV | Whitfield 132 33 | GOLDENHILL BANK 33 11kV S STN | Primary | 11 | -2.2268 | 53.0829 | WPD Best View | Headroom (MW) | N/A | 4.91 | 4.87 | 4.84 | 4.81 | 4.78 | 4.73 | 4.69 | 4.65 | 4.62 | 4.58 | 4.55 | 4.52 | 4.5 | 4.48 | 4.46 | 4.28 | 3.94 | 3.46
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Consumer Transformation | Headroom (MW) | Thermal | 6.11 | 6.03 | 5.98 | -1.33 | -1.75 | -2.07 | -2.39 | -3.77 | -5.09 | -6.18 | -7.24 | -8.21 | -9.15 | -9.99 | -11 | -14.35 | -17.22 | -19.5
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Leading the Way | Headroom (MW) | Thermal | 6.11 | 6.02 | 5.96 | -1.36 | -1.84 | -2.18 | -2.51 | -2.82 | -3.1 | -3.37 | -3.69 | -4.01 | -4.82 | -5.59 | -6.41 | -1.84 | -15.51 | -16.68
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | Steady Progression | Headroom (MW) | Thermal | 6.11 | 6.06 | 6.04 | -1.18 | -1.22 | -1.24 | -1.26 | -2.56 | -3.9 | -5.16 | -6.32 | -7.32 | -8.09 | -8.75 | -9.38 | -9.97 | -10.87 | -12.11
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | System Transformation | Headroom (MW) | Thermal | 6.11 | 6.04 | 6.01 | -1.21 | -1.33 | -1.47 | -1.62 | -2.83 | -4.01 | -4.98 | -5.88 | -6.68 | -7.42 | -8.07 | -8.87 | -4.89 | -15.08 | -17.52
Cellarhead 132kV | Whitfield 132 33 | KNYPERSLEY 33 11kV S STN | Primary | 11 | -2.1785 | 53.0987 | WPD Best View | Headroom (MW) | Thermal | 6.11 | 6.06 | 6.04 | -1.18 | -1.22 | -1.24 | -1.26 | -2.56 | -3.9 | -5.16 | -6.32 | -7.32 | -8.09 | -8.75 | -9.38 | -9.97 | -10.87 | -12.11
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Consumer Transformation | Headroom (MW) | Thermal | 10.81 | 10.62 | 10.49 | 10.34 | 9.78 | 9.35 | 8.94 | 8.32 | 7.66 | 6.95 | 6.13 | 5.26 | 4.35 | 3.49 | 2.42 | -1.42 | -6.08 | -11.45
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Leading the Way | Headroom (MW) | Thermal | 10.81 | 10.59 | 10.46 | 10.26 | 9.55 | 9.1 | 8.68 | 8.28 | 7.91 | 7.56 | 7.24 | 6.93 | 6.15 | 5.38 | 4.51 | 0.42 | -4.83 | -9.9
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | Steady Progression | Headroom (MW) | N/A | 10.81 | 10.69 | 10.66 | 10.63 | 10.57 | 10.51 | 10.46 | 10.31 | 10.17 | 10.01 | 9.82 | 9.62 | 9.22 | 8.83 | 8.35 | 8.02 | 7.75 | 6.33
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | System Transformation | Headroom (MW) | Thermal | 10.81 | 10.66 | 10.59 | 10.51 | 10.27 | 10.07 | 9.85 | 9.41 | 8.9 | 8.37 | 7.68 | 6.94 | 6.17 | 5.51 | 4.73 | 3.28 | 0.47 | -2.78
Cellarhead 132kV | Whitfield 132 33 | LEEK 33 11kV S STN | Primary | 11 | -2.0327 | 53.102 | WPD Best View | Headroom (MW) | N/A | 10.81 | 10.69 | 10.66 | 10.63 | 10.57 | 10.51 | 10.46 | 10.31 | 10.17 | 10.01 | 9.82 | 9.62 | 9.22 | 8.83 | 8.35 | 8.02 | 7.75 | 6.33
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Consumer Transformation | Headroom (MW) | N/A | 14.08 | 13.93 | 13.7 | 13.55 | 13.23 | 12.96 | 12.7 | 12.45 | 12.22 | 12.01 | 11.82 | 11.62 | 11.41 | 11.18 | 10.94 | 9.15 | 6.65 | 3.85
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Leading the Way | Headroom (MW) | N/A | 14.08 | 13.91 | 13.68 | 13.53 | 13.17 | 12.89 | 12.61 | 12.37 | 12.15 | 11.94 | 11.71 | 11.48 | 11.24 | 10.98 | 10.68 | 8.63 | 5.86 | 2.13
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | Steady Progression | Headroom (MW) | N/A | 14.08 | 13.99 | 13.94 | 13.9 | 13.85 | 13.79 | 13.74 | 13.69 | 13.64 | 13.59 | 13.55 | 13.51 | 13.48 | 13.46 | 13.45 | 13.44 | 13.06 | 12.52
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | System Transformation | Headroom (MW) | N/A | 14.08 | 13.96 | 13.88 | 13.69 | 13.55 | 13.43 | 13.3 | 13.17 | 13.06 | 12.94 | 12.84 | 12.76 | 12.7 | 12.64 | 12.56 | 12.07 | 10.89 | 9.73
Cellarhead 132kV | Whitfield 132 33 | Whitfield 132/33/11kVDUMMY | Primary | 11 | -2.178 | 53.0794 | WPD Best View | Headroom (MW) | N/A | 14.08 | 13.91 | 13.68 | 13.53 | 13.17 | 12.89 | 12.61 | 12.37 | 12.15 | 11.94 | 11.71 | 11.48 | 11.24 | 10.98 | 10.68 | 8.63 | 5.86 | 2.13
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Consumer Transformation | Headroom (MW) | N/A | 77.64 | 77.02 | 76.6 | 75.88 | 74.79 | 74.17 | 73.48 | 71.97 | 70.56 | 69.61 | 68.65 | 67.66 | 66.65 | 65.66 | 64.51 | 58.24 | 51.58 | 44.62
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Leading the Way | Headroom (MW) | N/A | 77.64 | 76.97 | 76.54 | 75.78 | 74.52 | 74.03 | 73.44 | 72.92 | 72.44 | 72.37 | 71.87 | 71.35 | 70.38 | 69.35 | 68.19 | 65.79 | 63.73 | 34.77
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | Steady Progression | Headroom (MW) | N/A | 77.64 | 77.29 | 76.99 | 76.8 | 76.61 | 76.62 | 76.48 | 75.32 | 74.22 | 73.31 | 72.67 | 71.84 | 71.22 | 70.7 | 70.2 | 69.99 | 68.55 | 66.06
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | System Transformation | Headroom (MW) | N/A | 77.64 | 77.21 | 76.82 | 76.51 | 76.02 | 75.87 | 75.59 | 74.48 | 73.38 | 72.68 | 71.95 | 71.21 | 70.49 | 69.88 | 69.19 | 70.41 | 75.09 | 57.75
East Claydon 132kV | Banbury 132 11 (GT1A) | Banbury 132/11kVDUMMY | Primary | 11 | -1.335 | 52.0698 | WPD Best View | Headroom (MW) | N/A | 77.64 | 76.98 | 76.55 | 75.8 | 74.54 | 74.07 | 73.49 | 72.97 | 72.5 | 72.44 | 71.94 | 71.43 | 70.47 | 69.44 | 68.3 | 65.97 | 63.99 | 35.13
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Consumer Transformation | Headroom (MW) | Thermal | 5.57 | 5.41 | 5.28 | 5.13 | 4.7 | 4.24 | 3.79 | 2.74 | 1.58 | 0.29 | -1.38 | -3.23 | -5.17 | -6.96 | -9.11 | -15.51 | -22.9 | -30.57
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Leading the Way | Headroom (MW) | Thermal | 5.57 | 5.39 | 5.25 | 5.09 | 4.59 | 4.06 | 3.53 | 3.02 | 2.54 | 2.06 | 1.6 | 1.15 | -0.45 | -1.99 | -3.63 | -11.54 | -21.16 | -26.43
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | Steady Progression | Headroom (MW) | Thermal | 5.57 | 5.48 | 5.43 | 5.4 | 5.33 | 5.25 | 5.16 | 4.93 | 4.7 | 4.42 | 4.05 | 3.62 | 2.68 | 1.77 | 0.58 | -0.91 | -2.79 | -4.98
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | System Transformation | Headroom (MW) | Thermal | 5.57 | 5.44 | 5.37 | 5.28 | 5.09 | 4.94 | 4.77 | 3.9 | 2.78 | 1.72 | 0.25 | -1.4 | -3.12 | -4.65 | -6.51 | -10.57 | -16.29 | -22.03
Feckenham 66kV | Bevington 66 11 (T1) | BEVINGTON 66 11kV S STN | Primary | 11 | -1.9437 | 52.1734 | WPD Best View | Headroom (MW) | Thermal | 5.57 | 5.48 | 5.43 | 5.4 | 5.33 | 5.25 | 5.16 | 4.93 | 4.7 | 4.42 | 4.05 | 3.62 | 2.68 | 1.77 | 0.58 | -0.91 | -2.79 | -4.98
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Consumer Transformation | Headroom (MW) | Thermal | 3 | 2.94 | 2.86 | 2.76 | 2.46 | 2.25 | 1.55 | 0.44 | -0.39 | -1.14 | -1.88 | -2.57 | -3.25 | -3.98 | -4.79 | -9.22 | -14.46 | -19.97
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Leading the Way | Headroom (MW) | Thermal | 3 | 2.93 | 2.85 | 2.75 | 2.42 | 2.2 | 1.46 | 0.85 | 0.35 | -0.32 | -0.88 | -1.41 | -1.98 | -2.58 | -3.23 | -7.07 | -11.54 | -16.68
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | Steady Progression | Headroom (MW) | N/A | 3 | 2.99 | 2.99 | 3 | 2.98 | 2.97 | 2.96 | 2.95 | 2.85 | 2.35 | 2.26 | 2.16 | 2.03 | 1.96 | 1.91 | 1.87 | 1.63 | 1.21
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | System Transformation | Headroom (MW) | Thermal | 3 | 2.97 | 2.94 | 2.91 | 2.8 | 2.72 | 2.63 | 2.54 | 2.02 | 1.75 | 1.48 | 1.25 | 1.04 | 0.88 | 0.73 | -0.23 | -1.65 | -3.14
Feckenham 66kV | Bloxham 66 11 | BLOXHAM 66 11kV S STN | Primary | 11 | -1.3865 | 52.0314 | WPD Best View | Headroom (MW) | Thermal | 3 | 2.93 | 2.85 | 2.75 | 2.42 | 2.21 | 1.47 | 0.86 | 0.37 | -0.29 | -0.86 | -1.39 | -1.95 | -2.55 | -3.2 | -7.03 | -11.49 | -16.63
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Consumer Transformation | Headroom (MW) | Thermal | 4.26 | 4.11 | 4 | 3.86 | 3.43 | 3.13 | 2.8 | 2.29 | 1.74 | 1.16 | 0.45 | -0.32 | -1.13 | -1.88 | -2.78 | -6.25 | -9.21 | -12.97
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Leading the Way | Headroom (MW) | Thermal | 4.26 | 4.09 | 3.97 | 3.83 | 3.32 | 3 | 2.66 | 2.37 | 2.08 | 1.81 | 1.56 | 1.33 | 0.65 | -0.02 | -0.75 | -3.13 | -10.07 | -13.4
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | Steady Progression | Headroom (MW) | Thermal | 4.26 | 4.17 | 4.13 | 4.09 | 4.02 | 3.96 | 3.87 | 3.74 | 3.63 | 3.5 | 3.33 | 3.15 | 2.78 | 2.42 | 1.96 | 1.44 | 0.67 | -0.39
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | System Transformation | Headroom (MW) | Thermal | 4.26 | 4.14 | 4.07 | 4 | 3.8 | 3.66 | 3.47 | 3.09 | 2.65 | 2.17 | 1.57 | 0.91 | 0.22 | -0.38 | -1.1 | -2.03 | -6.19 | -8.65
Feckenham 66kV | Broadway 66 11 (T1) | BROADWAY 66 11kV S STN | Primary | 11 | -1.8557 | 52.0545 | WPD Best View | Headroom (MW) | Thermal | 4.26 | 4.17 | 4.13 | 4.09 | 4.02 | 3.96 | 3.87 | 3.74 | 3.63 | 3.5 | 3.33 | 3.15 | 2.78 | 2.42 | 1.96 | 1.44 | 0.67 | -0.39
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Consumer Transformation | Headroom (MW) | Thermal | 6.27 | 6.17 | 6.09 | 6 | 5.76 | 5.56 | 5.36 | 4.71 | 3.93 | 3.09 | 1.94 | 0.66 | -0.69 | -1.91 | -3.4 | -6.41 | -10.15 | -14.64
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Leading the Way | Headroom (MW) | Thermal | 6.27 | 6.16 | 6.08 | 5.99 | 5.72 | 5.51 | 5.3 | 5.06 | 4.83 | 4.63 | 4.41 | 4.19 | 3.15 | 2.15 | 1.1 | -2.33 | -7.04 | -9.64
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | Steady Progression | Headroom (MW) | Thermal | 6.27 | 6.2 | 6.17 | 6.14 | 6.09 | 6.05 | 6.01 | 5.86 | 5.71 | 5.53 | 5.28 | 5 | 4.32 | 3.66 | 2.79 | 1.71 | 0.43 | -1.05
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | System Transformation | Headroom (MW) | Thermal | 6.27 | 6.18 | 6.13 | 6.08 | 5.98 | 5.88 | 5.77 | 5.22 | 4.55 | 3.79 | 2.73 | 1.56 | 0.32 | -0.77 | -2.13 | -4.12 | -7.03 | -10.58
Feckenham 66kV | Brotheridge Green 66 11 (T1) | BROTHERIDGE GRN 66 11kV S STN | Primary | 11 | -2.2622 | 52.0715 | WPD Best View | Headroom (MW) | Thermal | 6.27 | 6.2 | 6.17 | 6.14 | 6.09 | 6.05 | 6.01 | 5.85 | 5.7 | 5.52 | 5.27 | 4.97 | 4.29 | 3.63 | 2.76 | 1.68 | 0.4 | -1.08
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Consumer Transformation | Headroom (MW) | Thermal | 2.09 | 1.93 | 1.84 | 1.71 | 1.41 | 1.11 | 0.82 | 0.01 | -0.91 | -1.92 | -3.17 | -4.57 | -6.05 | -7.39 | -9.01 | -14.69 | -19.17 | -24.52
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Leading the Way | Headroom (MW) | Thermal | 2.09 | 1.92 | 1.83 | 1.69 | 1.33 | 0.99 | 0.65 | 0.34 | 0.03 | -0.2 | -0.47 | -0.73 | -1.92 | -3.04 | -4.23 | -12.17 | -17.63 | -21.03
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | Steady Progression | Headroom (MW) | Thermal | 2.09 | 1.98 | 1.93 | 1.88 | 1.81 | 1.73 | 1.65 | 1.44 | 1.23 | 1 | 0.7 | 0.34 | -0.43 | -1.17 | -2.15 | -3.41 | -4.88 | -6.57
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | System Transformation | Headroom (MW) | Thermal | 2.09 | 1.96 | 1.9 | 1.81 | 1.66 | 1.53 | 1.39 | 0.68 | -0.22 | -1.12 | -2.27 | -3.58 | -4.95 | -6.16 | -7.64 | -11.89 | -15.35 | -19.49
Feckenham 66kV | Epwell 66 11 (T1) | EPWELL 66 11kV S STN | Primary | 11 | -1.4747 | 52.0701 | WPD Best View | Headroom (MW) | Thermal | 2.09 | 1.94 | 1.87 | 1.76 | 1.51 | 1.23 | 0.96 | 0.63 | 0.31 | 0.03 | -0.3 | -0.66 | -1.71 | -2.71 | -3.85 | -10.77 | -14.71 | -17.66
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Consumer Transformation | Headroom (MW) | Thermal | 17.3 | 16.84 | 16.54 | 16.18 | 15.21 | 14.41 | 13.58 | 12.19 | 10.69 | 9.2 | 7.44 | 5.51 | 3.38 | 1.37 | -1.03 | -9.96 | -19.35 | -30.36
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Leading the Way | Headroom (MW) | Thermal | 17.3 | 16.8 | 16.48 | 16.1 | 14.95 | 14.09 | 13.2 | 12.37 | 11.65 | 11.18 | 10.76 | 10.4 | 8.62 | 6.89 | 5.9 | -5.7 | -19.28 | -28.7
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | Steady Progression | Headroom (MW) | N/A | 17.3 | 16.98 | 16.83 | 16.69 | 16.49 | 16.32 | 16.12 | 15.76 | 15.43 | 15.09 | 14.67 | 14.22 | 13.2 | 12.24 | 10.99 | 9.45 | 7.09 | 4.04
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | System Transformation | Headroom (MW) | Thermal | 17.3 | 16.91 | 16.7 | 16.47 | 16 | 15.69 | 15.29 | 14.2 | 12.89 | 11.72 | 10.23 | 8.56 | 6.75 | 5.17 | 3.39 | -1.39 | -8.65 | -16.01
Feckenham 66kV | Evesham 66 11 (T1) | EVESHAM 66 11kV S STN | Primary | 11 | -1.9329 | 52.1102 | WPD Best View | Headroom (MW) | N/A | 17.3 | 16.98 | 16.83 | 16.69 | 16.49 | 16.32 | 16.12 | 15.76 | 15.43 | 15.09 | 14.67 | 14.22 | 13.2 | 12.24 | 10.99 | 9.45 | 7.09 | 4.04
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Consumer Transformation | Headroom (MW) | Thermal | 7.33 | 7.32 | 7.3 | 7.28 | 7.22 | 7.16 | 6.83 | 6.12 | 5.53 | 4.95 | 4.48 | 4.02 | 3.57 | 3.1 | 2.56 | 0.46 | -1.82 | -4.21
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Leading the Way | Headroom (MW) | Thermal | 7.33 | 7.31 | 7.3 | 7.29 | 7.22 | 7.17 | 6.81 | 6.5 | 6.26 | 5.9 | 5.6 | 5.32 | 4.95 | 4.58 | 4.18 | 2.46 | 0.59 | -1.41
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | Steady Progression | Headroom (MW) | N/A | 7.33 | 7.32 | 7.32 | 7.31 | 7.3 | 7.3 | 7.28 | 7.24 | 7.15 | 6.82 | 6.75 | 6.67 | 6.54 | 6.44 | 6.34 | 6.18 | 6.07 | 5.94
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | System Transformation | Headroom (MW) | N/A | 7.33 | 7.32 | 7.31 | 7.3 | 7.28 | 7.25 | 7.22 | 7.06 | 6.63 | 6.31 | 6.08 | 5.87 | 5.67 | 5.51 | 5.31 | 4.81 | 4.28 | 3.7
Feckenham 66kV | Feckenham 66 11 (T1) | Feckenham 66/11kVDUMMY | Primary | 11 | -1.9717 | 52.253 | WPD Best View | Headroom (MW) | N/A | 7.33 | 7.32 | 7.32 | 7.31 | 7.3 | 7.3 | 7.28 | 7.24 | 7.15 | 6.82 | 6.75 | 6.67 | 6.54 | 6.44 | 6.34 | 6.18 | 6.07 | 5.94
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Consumer Transformation | Headroom (MW) | Thermal | 6.18 | 6.06 | 5.98 | 5.89 | 5.54 | 5.3 | 5.05 | 4.27 | 3.36 | 2.33 | 1.13 | -0.2 | -1.6 | -2.88 | -4.43 | -8.13 | -12.5 | -17.62
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Leading the Way | Headroom (MW) | Thermal | 6.18 | 6.04 | 5.96 | 5.86 | 5.42 | 5.16 | 4.88 | 4.62 | 4.38 | 4.15 | 3.88 | 3.62 | 2.56 | 1.52 | 0.39 | -3.51 | -8.62 | -12.01
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | Steady Progression | Headroom (MW) | Thermal | 6.18 | 6.11 | 6.08 | 6.05 | 5.98 | 5.94 | 5.89 | 5.72 | 5.54 | 5.31 | 5.05 | 4.75 | 4.06 | 3.39 | 2.51 | 1.45 | 0.24 | -1.2
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | System Transformation | Headroom (MW) | Thermal | 6.18 | 6.09 | 6.04 | 5.99 | 5.81 | 5.7 | 5.58 | 4.93 | 4.12 | 3.19 | 2.12 | 0.93 | -0.33 | -1.43 | -2.78 | -4.86 | -7.82 | -11.36
Feckenham 66kV | Great Alne 66 11 (T1) | GREAT ALNE 66 11kV S STN | Primary | 11 | -1.8112 | 52.2342 | WPD Best View | Headroom (MW) | Thermal | 6.18 | 6.11 | 6.08 | 6.05 | 5.98 | 5.94 | 5.89 | 5.72 | 5.54 | 5.31 | 5.05 | 4.75 | 4.06 | 3.39 | 2.51 | 1.45 | 0.24 | -1.2
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Consumer Transformation | Headroom (MW) | N/A | 47.91 | 47.77 | 47.52 | 40.29 | 39.86 | 39.48 | 39.09 | 38.05 | 37.02 | 36.08 | 35.2 | 34.33 | 33.47 | 32.67 | 31.72 | 28.03 | 24.31 | 20.62
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Leading the Way | Headroom (MW) | N/A | 47.91 | 47.76 | 47.51 | 40.28 | 39.72 | 39.3 | 38.88 | 38.47 | 38.08 | 37.73 | 37.4 | 37.09 | 36.36 | 35.63 | 34.84 | 31.02 | 29.58 | 28.25
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | Steady Progression | Headroom (MW) | N/A | 47.91 | 47.83 | 47.77 | 40.64 | 40.65 | 40.55 | 40.44 | 39.68 | 38.94 | 38.22 | 37.55 | 36.94 | 36.35 | 35.8 | 35.22 | 34.47 | 33.54 | 32.09
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | System Transformation | Headroom (MW) | N/A | 47.91 | 47.81 | 47.72 | 40.44 | 40.3 | 40.1 | 39.87 | 39.03 | 38.13 | 37.3 | 36.52 | 35.76 | 35.03 | 34.39 | 33.65 | 32.15 | 30.05 | 27.55
Feckenham 66kV | Ipsley 66 11 (T1A) | IPSLEY 66 11kV S STN | Primary | 11 | -1.9144 | 52.2962 | WPD Best View | Headroom (MW) | N/A | 47.91 | 47.83 | 47.77 | 40.64 | 40.67 | 40.57 | 40.46 | 39.7 | 38.95 | 38.23 | 37.55 | 36.94 | 36.33 | 35.78 | 35.2 | 34.45 | 33.51 | 32.06
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Consumer Transformation | Headroom (MW) | Thermal | 3.18 | 3.09 | 3.03 | 2.95 | 2.74 | 2.57 | 2.37 | 1.65 | 0.79 | -0.19 | -1.43 | -2.84 | -4.32 | -5.65 | -7.27 | -11.5 | -15.11 | -19.47
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Leading the Way | Headroom (MW) | Thermal | 3.18 | 3.08 | 3.02 | 2.93 | 2.69 | 2.49 | 2.27 | 2.04 | 1.79 | 1.56 | 1.34 | 1.12 | -0.04 | -1.12 | -2.23 | -7.69 | -12.24 | -14.32
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | Steady Progression | Headroom (MW) | Thermal | 3.18 | 3.13 | 3.12 | 3.1 | 3.07 | 3.04 | 3.01 | 2.84 | 2.67 | 2.46 | 2.18 | 1.83 | 1.06 | 0.3 | -0.69 | -1.99 | -3.37 | -4.9
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | System Transformation | Headroom (MW) | Thermal | 3.18 | 3.11 | 3.08 | 3.03 | 2.95 | 2.86 | 2.74 | 2.11 | 1.31 | 0.42 | -0.74 | -2.07 | -3.47 | -4.71 | -6.22 | -9.54 | -12.53 | -16.18
Feckenham 66kV | Long Marston 66 11 (T1) | LONG MARSTON 66 11kV S STN | Primary | 11 | -1.7822 | 52.1024 | WPD Best View | Headroom (MW) | Thermal | 3.18 | 3.13 | 3.12 | 3.1 | 3.07 | 3.04 | 3.01 | 2.84 | 2.67 | 2.46 | 2.18 | 1.83 | 1.06 | 0.3 | -0.69 | -1.99 | -3.37 | -4.9
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Consumer Transformation | Headroom (MW) | N/A | 7.49 | 7.37 | 7.29 | 7.2 | 6.9 | 6.66 | 6.44 | 6.24 | 6.06 | 5.9 | 5.74 | 5.59 | 5.45 | 5.29 | 5.13 | 3.79 | 2.08 | 0.21
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Leading the Way | Headroom (MW) | Thermal | 7.49 | 7.36 | 7.28 | 7.18 | 6.82 | 6.57 | 6.34 | 6.15 | 5.97 | 5.82 | 5.65 | 5.5 | 5.34 | 5.17 | 4.97 | 3.5 | 1.63 | -0.78
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | Steady Progression | Headroom (MW) | N/A | 7.49 | 7.42 | 7.38 | 7.36 | 7.31 | 7.26 | 7.21 | 7.16 | 7.11 | 7.06 | 7.02 | 6.98 | 6.95 | 6.93 | 6.91 | 6.92 | 6.72 | 6.34
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | System Transformation | Headroom (MW) | N/A | 7.49 | 7.4 | 7.34 | 7.3 | 7.16 | 7.05 | 6.93 | 6.81 | 6.71 | 6.62 | 6.53 | 6.45 | 6.39 | 6.34 | 6.3 | 6.02 | 5.2 | 4.37
Feckenham 66kV | Moreton 66 11 (T1) | MORETON 66 11kV S STN | Primary | 11 | -1.7017 | 51.9944 | WPD Best View | Headroom (MW) | N/A | 7.49 | 7.42 | 7.38 | 7.36 | 7.31 | 7.26 | 7.21 | 7.16 | 7.11 | 7.06 | 7.02 | 6.98 | 6.95 | 6.93 | 6.91 | 6.92 | 6.72 | 6.34
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Consumer Transformation | Headroom (MW) | Thermal | 3.66 | 3.48 | 3.2 | 3.05 | 2.59 | 2.37 | 2.12 | 1.86 | 1.62 | 1.41 | 1.2 | 1.01 | 0.83 | 0.63 | 0.38 | -1.39 | -3.58 | -5.99
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Leading the Way | Headroom (MW) | Thermal | 3.66 | 3.46 | 3.17 | 3.02 | 2.45 | 2.25 | 1.99 | 1.74 | 1.5 | 1.29 | 1.07 | 0.87 | 0.66 | 0.4 | 0.11 | -1.72 | -4.01 | -7.05
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | Steady Progression | Headroom (MW) | N/A | 3.66 | 3.55 | 3.49 | 3.44 | 3.34 | 3.33 | 3.27 | 3.21 | 3.15 | 3.1 | 3.04 | 3 | 2.96 | 2.94 | 2.92 | 3.09 | 2.8 | 2.25
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | System Transformation | Headroom (MW) | Thermal | 3.66 | 3.52 | 3.43 | 3.18 | 2.95 | 2.87 | 2.74 | 2.6 | 2.47 | 2.35 | 2.23 | 2.14 | 2.06 | 2 | 1.94 | 1.63 | 0.61 | -0.46
Feckenham 66kV | Pershore 66 11 (T1) | PERSHORE 66 11kV S STN | Primary | 11 | -2.0978 | 52.1346 | WPD Best View | Headroom (MW) | N/A | 3.66 | 3.55 | 3.49 | 3.44 | 3.34 | 3.33 | 3.27 | 3.21 | 3.15 | 3.1 | 3.04 | 3 | 2.96 | 2.94 | 2.92 | 3.09 | 2.8 | 2.25
Bishops Wood 132kV | Redditch North 66 11 (T1) | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Consumer Transformation | Headroom (MW) | N/A | 32.07 | 31.8 | 31.62 | 31.4 | 30.86 | 30.42 | 29.96 | 29.5 | 29.07 | 28.68 | 28.3 | 27.92 | 27.54 | 27.06 | 26.56 | 23.33 | 19.63 | 15.59
Bishops Wood 132kV | Redditch North 66 11 (T1) | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Leading the Way | Headroom (MW) | N/A | 32.07 | 31.77 | 31.58 | 31.35 | 30.7 | 30.27 | 29.79 | 29.31 | 28.86 | 28.46 | 28.04 | 27.63 | 27.14 | 26.58 | 25.98 | 22.68 | 18.65 | 13.44
Bishops Wood 132kV | Redditch North 66 11 (T1) | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | Steady Progression | Headroom (MW) | N/A | 32.07 | 31.89 | 31.81 | 31.72 | 24.37 | 24.3 | 24.2 | 23.5 | 22.82 | 22.19 | 21.62 | 21.14 | 20.88 | 20.68 | 20.55 | 20.44 | 19.88 | 18.97
Bishops Wood 132kV | Redditch North 66 11 (T1) | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | System Transformation | Headroom (MW) | N/A | 32.07 | 31.85 | 31.72 | 31.59 | 31.37 | 31.19 | 30.96 | 30.71 | 30.46 | 30.24 | 30.01 | 29.81 | 29.62 | 29.44 | 29.28 | 28.31 | 26.51 | 24.73
Bishops Wood 132kV | Redditch North 66 11 (T1) | REDDITCH NORTH 66 11kV S STN | Primary | 11 | -1.9508 | 52.3132 | WPD Best View | Headroom (MW) | N/A | 32.07 | 31.88 | 31.78 | 31.68 | 24.27 | 24.16 | 24.02 | 23.28 | 22.56 | 21.88 | 21.26 | 20.73 | 20.43 | 20.18 | 20 | 19.64 | 18.72 | 17.58
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Consumer Transformation | Headroom (MW) | Thermal | 25.02 | 24.71 | 24.42 | 24.06 | 23.09 | 22.32 | 21.39 | 20.34 | 19.39 | 18.42 | 17.39 | 16.38 | 15.41 | 14.37 | 13.31 | 7.05 | -0.45 | -8.64
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Leading the Way | Headroom (MW) | Thermal | 25.02 | 24.66 | 24.37 | 23.99 | 22.87 | 22.06 | 21.1 | 20.17 | 19.27 | 18.25 | 17.17 | 16.1 | 15.06 | 13.97 | 12.82 | 6.57 | -1.34 | -11.6
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | Steady Progression | Headroom (MW) | N/A | 25.02 | 24.87 | 24.79 | 24.73 | 24.62 | 24.51 | 24.4 | 24.28 | 24.16 | 23.92 | 23.8 | 23.69 | 23.58 | 23.5 | 23.44 | 23.11 | 22.17 | 20.79
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | System Transformation | Headroom (MW) | N/A | 25.02 | 24.79 | 24.63 | 24.45 | 24.04 | 23.72 | 23.33 | 22.94 | 22.43 | 21.99 | 21.53 | 21.09 | 20.65 | 20.25 | 19.86 | 18.05 | 14.86 | 11.68
Feckenham 66kV | Redditch South 66 11 (T1A) | REDDITCH SOUTH 66 11kV S STN | Primary | 11 | -1.9476 | 52.2884 | WPD Best View | Headroom (MW) | N/A | 25.02 | 24.87 | 24.78 | 24.71 | 24.58 | 24.44 | 24.29 | 24.13 | 23.85 | 23.62 | 23.39 | 23.19 | 23.03 | 22.9 | 22.8 | 22.33 | 21.2 | 19.62
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Consumer Transformation | Headroom (MW) | Thermal | 5.23 | 5.09 | 4.99 | 4.88 | 4.52 | 4.14 | 3.78 | 2.45 | 0.89 | -0.89 | -3.06 | -5.53 | -8.15 | -10.5 | -13.39 | -19.44 | -27.43 | -36.03
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Leading the Way | Headroom (MW) | Thermal | 5.23 | 5.07 | 4.96 | 4.85 | 4.43 | 4 | 3.58 | 3.18 | 2.8 | 2.44 | 2.09 | 1.75 | -0.31 | -2.24 | -4.29 | -10.98 | -21.43 | -26.17
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | Steady Progression | Headroom (MW) | Thermal | 5.23 | 5.16 | 5.12 | 5.11 | 5.07 | 5 | 4.93 | 4.61 | 4.3 | 3.9 | 3.41 | 2.81 | 1.43 | 0.11 | -1.64 | -3.87 | -6.32 | -9.04
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | System Transformation | Headroom (MW) | Thermal | 5.23 | 5.13 | 5.07 | 5.02 | 4.87 | 4.74 | 4.59 | 3.4 | 1.86 | 0.25 | -1.79 | -4.12 | -6.58 | -8.74 | -11.41 | -15.47 | -22.01 | -28.96
Feckenham 66kV | Shipston 66 11 (T1) | SHIPSTON 66 11kV S STN | Primary | 11 | -1.6427 | 52.0798 | WPD Best View | Headroom (MW) | Thermal | 5.23 | 5.16 | 5.12 | 5.11 | 5.07 | 5 | 4.93 | 4.61 | 4.3 | 3.9 | 3.41 | 2.81 | 1.43 | 0.11 | -1.64 | -3.87 | -6.32 | -9.04
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Consumer Transformation | Headroom (MW) | Thermal | 4.44 | 4.42 | 4.38 | 4.32 | 4.13 | 3.98 | 3.84 | 3.7 | 3.57 | 3.45 | 3.33 | 3.22 | 3.1 | 2.99 | 2.87 | 2 | 0.93 | -0.22
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Leading the Way | Headroom (MW) | Thermal | 4.44 | 4.42 | 4.37 | 4.32 | 4.09 | 3.94 | 3.79 | 3.65 | 3.53 | 3.41 | 3.28 | 3.16 | 3.04 | 2.91 | 2.77 | 1.85 | 0.69 | -0.74
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | Steady Progression | Headroom (MW) | N/A | 4.44 | 4.44 | 4.41 | 4.39 | 4.36 | 4.32 | 4.29 | 4.26 | 4.22 | 4.18 | 4.15 | 4.12 | 4.09 | 4.07 | 4.04 | 3.99 | 3.84 | 3.6
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | System Transformation | Headroom (MW) | N/A | 4.44 | 4.43 | 4.4 | 4.37 | 4.28 | 4.21 | 4.14 | 4.06 | 3.99 | 3.93 | 3.87 | 3.81 | 3.76 | 3.71 | 3.67 | 3.43 | 2.93 | 2.4
Feckenham 66kV | Stow 66 11 (T1) | STOW 66 11kV S STN | Primary | 11 | -1.77 | 51.9243 | WPD Best View | Headroom (MW) | N/A | 4.44 | 4.44 | 4.41 | 4.39 | 4.36 | 4.32 | 4.29 | 4.26 | 4.22 | 4.18 | 4.15 | 4.12 | 4.09 | 4.07 | 4.04 | 3.99 | 3.84 | 3.6
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Consumer Transformation | Headroom (MW) | Thermal | 24.91 | 24.56 | 24.35 | 24.14 | 23.38 | 22.79 | 22.19 | 20.96 | 19.61 | 18.15 | 16.54 | 14.74 | 12.81 | 10.96 | 8.77 | 1.4 | -6.23 | -14.97
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Leading the Way | Headroom (MW) | Thermal | 24.91 | 24.53 | 24.31 | 24.13 | 23.24 | 22.63 | 22.01 | 21.42 | 20.87 | 20.36 | 19.84 | 19.27 | 17.62 | 15.97 | 14.22 | 5.54 | -3.39 | -11.12
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | Steady Progression | Headroom (MW) | N/A | 24.91 | 24.67 | 24.6 | 24.57 | 24.48 | 24.37 | 24.25 | 23.98 | 23.73 | 23.42 | 23.08 | 22.69 | 21.81 | 20.97 | 19.89 | 18.61 | 16.68 | 14.1
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | System Transformation | Headroom (MW) | Thermal | 24.91 | 24.62 | 24.49 | 24.4 | 24.09 | 23.82 | 23.51 | 22.61 | 21.48 | 20.23 | 18.83 | 17.25 | 15.61 | 14.17 | 12.45 | 8.41 | 3.43 | -2.26
Feckenham 66kV | Stratford 66 11 (T1) | STRATFORD 66 11kV S STN | Primary | 11 | -1.7413 | 52.1945 | WPD Best View | Headroom (MW) | N/A | 24.91 | 24.67 | 24.6 | 24.57 | 24.48 | 24.37 | 24.25 | 23.98 | 23.73 | 23.42 | 23.08 | 22.69 | 21.81 | 20.97 | 19.89 | 18.61 | 16.68 | 14.1
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Consumer Transformation | Headroom (MW) | N/A | 8.28 | 8.16 | 8.08 | 7.99 | 7.81 | 7.66 | 7.5 | 7.34 | 7.18 | 7.04 | 6.9 | 6.76 | 6.62 | 6.47 | 6.32 | 5.44 | 4.35 | 3.11
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Leading the Way | Headroom (MW) | N/A | 8.28 | 8.15 | 8.07 | 7.98 | 7.77 | 7.62 | 7.46 | 7.3 | 7.15 | 7 | 6.85 | 6.69 | 6.54 | 6.38 | 6.21 | 5.21 | 3.98 | 2.3
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | Steady Progression | Headroom (MW) | N/A | 8.28 | 8.18 | 8.14 | 8.1 | 8.06 | 8.01 | 7.96 | 7.92 | 7.87 | 7.83 | 7.78 | 7.75 | 7.72 | 7.69 | 7.67 | 7.6 | 7.42 | 7.12
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | System Transformation | Headroom (MW) | N/A | 8.28 | 8.17 | 8.11 | 8.05 | 7.96 | 7.88 | 7.79 | 7.69 | 7.6 | 7.51 | 7.43 | 7.36 | 7.3 | 7.25 | 7.18 | 6.93 | 6.38 | 5.84
Feckenham 66kV | Strensham 66 11 (T1) | STRENSHAM 66 11kV S STN | Primary | 11 | -2.1403 | 52.0677 | WPD Best View | Headroom (MW) | N/A | 8.28 | 8.18 | 8.14 | 8.1 | 8.06 | 8.01 | 7.96 | 7.92 | 7.87 | 7.83 | 7.78 | 7.75 | 7.72 | 7.69 | 7.67 | 7.6 | 7.42 | 7.12
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Consumer Transformation | Headroom (MW) | N/A | 28.95 | 28.91 | 28.87 | 28.82 | 28.7 | 28.6 | 28.5 | 28.1 | 27.62 | 27.09 | 26.37 | 25.56 | 24.71 | 23.94 | 22.98 | 21.19 | 19.01 | 16.36
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Leading the Way | Headroom (MW) | N/A | 28.95 | 28.9 | 28.86 | 28.82 | 28.69 | 28.58 | 28.49 | 28.36 | 28.24 | 28.12 | 28 | 27.87 | 27.2 | 26.57 | 25.91 | 23.89 | 21.11 | 19.75
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | Steady Progression | Headroom (MW) | N/A | 28.95 | 28.93 | 28.92 | 28.9 | 28.89 | 28.87 | 28.86 | 28.77 | 28.68 | 28.57 | 28.41 | 28.23 | 27.8 | 27.38 | 26.83 | 26.14 | 25.32 | 24.43
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | System Transformation | Headroom (MW) | N/A | 28.95 | 28.92 | 28.89 | 28.87 | 28.82 | 28.77 | 28.73 | 28.38 | 27.95 | 27.47 | 26.81 | 26.06 | 25.28 | 24.59 | 23.72 | 22.47 | 20.7 | 18.54
Feckenham 66kV | Tewkesbury 66 11 (T1) | TEWKESBURY 66 11kV S STN | Primary | 11 | -2.13 | 52.0012 | WPD Best View | Headroom (MW) | N/A | 28.95 | 28.93 | 28.92 | 28.9 | 28.89 | 28.87 | 28.86 | 28.77 | 28.68 | 28.57 | 28.41 | 28.23 | 27.8 | 27.38 | 26.83 | 26.14 | 25.32 | 24.43
Iron Acton 132kV | Bradley Stoke 33kV | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Consumer Transformation | Headroom (MW) | Thermal | 12.49 | 12.31 | 12.18 | 12.03 | 11.62 | 11.32 | 11.04 | 10.27 | 9.37 | 8.4 | 7.19 | 5.83 | 4.4 | 3.1 | 1.52 | -2.26 | -7.85 | -13.38
Iron Acton 132kV | Bradley Stoke 33kV | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Leading the Way | Headroom (MW) | Thermal | 12.49 | 12.29 | 12.16 | 12 | 11.52 | 11.21 | 10.91 | 10.64 | 10.38 | 10.16 | 9.94 | 9.74 | 8.61 | 7.54 | 6.39 | 2.16 | -4.42 | -8.25
Iron Acton 132kV | Bradley Stoke 33kV | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | Steady Progression | Headroom (MW) | N/A | 12.49 | 12.38 | 12.33 | 12.28 | 12.21 | 12.15 | 12.09 | 11.9 | 11.71 | 11.48 | 11.2 | 10.86 | 10.11 | 9.4 | 8.46 | 7.4 | 6.04 | 4.3
Iron Acton 132kV | Bradley Stoke 33kV | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | System Transformation | Headroom (MW) | Thermal | 12.49 | 12.35 | 12.26 | 12.17 | 11.99 | 11.85 | 11.69 | 11.03 | 10.23 | 9.33 | 8.2 | 6.94 | 5.6 | 4.43 | 3 | 0.81 | -3.06 | -7.12
Iron Acton 132kV | Bradley Stoke 33kV | HAMMERLEY DOWN 33 11kV S STN | Primary | 11 | -2.4201 | 51.6257 | WPD Best View | Headroom (MW) | Thermal | 12.49 | 12.37 | 12.3 | 12.24 | 12.13 | 12.04 | 11.94 | 11.42 | 10.8 | 10.09 | 9.22 | 8.23 | 7.07 | 6.04 | 4.76 | 3.04 | 0.58 | -2.6
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Consumer Transformation | Headroom (MW) | N/A | 33.66 | 33.4 | 33.24 | 32.87 | 32.29 | 31.72 | 31.14 | 30.15 | 29.08 | 27.91 | 26.57 | 25.05 | 23.43 | 21.9 | 20.12 | 19.21 | 11.8 | 3.29
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Leading the Way | Headroom (MW) | Thermal | 33.66 | 33.37 | 33.19 | 32.79 | 32.16 | 31.61 | 31.01 | 30.42 | 29.86 | 29.33 | 28.77 | 28.23 | 26.92 | 25.55 | 24.08 | 22.64 | 6.3 | -1.91
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | Steady Progression | Headroom (MW) | N/A | 33.66 | 33.45 | 33.35 | 33.25 | 33.29 | 33.25 | 33.18 | 33.07 | 32.84 | 32.57 | 32.27 | 31.94 | 31.28 | 30.64 | 29.83 | 33.92 | 32.19 | 29.77
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | System Transformation | Headroom (MW) | N/A | 33.66 | 33.42 | 33.3 | 33.18 | 33.07 | 32.84 | 32.52 | 31.78 | 30.93 | 30 | 28.88 | 27.6 | 26.3 | 25.18 | 23.84 | 26.16 | 16.36 | 11.09
Iron Acton 132kV | Chipping Sodbury 132 11 (GT1) | Chipping Sodbury 132/33/11kVDUMMY | Primary | 11 | -2.4123 | 51.5531 | WPD Best View | Headroom (MW) | N/A | 33.66 | 33.42 | 33.3 | 33.18 | 33.07 | 32.84 | 32.52 | 31.78 | 30.93 | 30 | 28.88 | 27.6 | 26.3 | 25.18 | 23.84 | 26.16 | 16.36 | 11.09
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Consumer Transformation | Headroom (MW) | Thermal | 12.79 | 12.45 | 12.27 | 12.06 | 11.6 | 11.15 | 10.72 | 9.78 | 8.74 | 7.59 | 6.18 | 4.59 | 2.94 | 1.43 | -0.38 | -5.47 | -11.27 | -18.07
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Leading the Way | Headroom (MW) | Thermal | 12.79 | 12.44 | 12.25 | 12.03 | 11.5 | 11.02 | 10.54 | 10.11 | 9.71 | 9.33 | 8.92 | 8.5 | 7.19 | 5.93 | 4.59 | -0.97 | -7.91 | -13.11
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | Steady Progression | Headroom (MW) | N/A | 12.79 | 12.58 | 12.43 | 12.34 | 12.23 | 12.11 | 11.99 | 11.75 | 11.5 | 11.21 | 10.86 | 10.47 | 9.67 | 8.9 | 7.9 | 6.53 | 4.89 | 2.84
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | System Transformation | Headroom (MW) | Thermal | 12.79 | 12.49 | 12.36 | 12.22 | 12 | 11.81 | 11.59 | 10.8 | 9.82 | 8.84 | 7.6 | 6.16 | 4.67 | 3.35 | 1.76 | -1.1 | -5.26 | -10.18
Iron Acton 132kV | Chipping Sodbury 132 33 | ALVESTON 33 11kV S STN | Primary | 11 | -2.521 | 51.5941 | WPD Best View | Headroom (MW) | Thermal | 12.79 | 12.49 | 12.36 | 12.22 | 12 | 11.81 | 11.59 | 10.8 | 9.82 | 8.84 | 7.6 | 6.16 | 4.67 | 3.35 | 1.76 | -1.1 | -5.26 | -10.18
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Consumer Transformation | Headroom (MW) | Thermal | 16.04 | 15.77 | 15.57 | 15.32 | 14.77 | 14.34 | 13.93 | 13.55 | 13.21 | 12.92 | 12.59 | 12.25 | 11.92 | 11.56 | 11.18 | 8.26 | 4.05 | -0.32
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Leading the Way | Headroom (MW) | Thermal | 16.04 | 15.75 | 15.53 | 15.28 | 14.65 | 14.2 | 13.78 | 13.41 | 13.08 | 12.79 | 12.4 | 12.03 | 11.65 | 11.23 | 10.75 | 7.41 | 2.49 | -3.32
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | Steady Progression | Headroom (MW) | N/A | 16.04 | 15.87 | 15.79 | 15.72 | 15.64 | 15.54 | 15.45 | 15.36 | 15.28 | 15.2 | 15.13 | 15.08 | 15.04 | 15.01 | 15 | 14.92 | 14.29 | 13.39
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | System Transformation | Headroom (MW) | N/A | 16.04 | 15.83 | 15.69 | 15.55 | 15.32 | 15.12 | 14.91 | 14.71 | 14.53 | 14.36 | 14.22 | 14.09 | 14 | 13.89 | 13.77 | 12.97 | 10.85 | 9.05
Iron Acton 132kV | Chipping Sodbury 132 33 | COWHORN 33 11kV S STN | Primary | 11 | -2.4773 | 51.4461 | WPD Best View | Headroom (MW) | N/A | 16.04 | 15.83 | 15.69 | 15.55 | 15.32 | 15.12 | 14.91 | 14.71 | 14.53 | 14.36 | 14.22 | 14.09 | 14 | 13.89 | 13.77 | 12.97 | 10.85 | 9.05
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Consumer Transformation | Headroom (MW) | Thermal | 3.78 | 3.65 | 3.65 | 3.25 | 2.97 | 2.78 | 2.61 | 2.21 | 1.76 | 1.28 | 0.65 | -0.06 | -0.81 | -1.5 | -2.34 | -5.03 | -8.16 | -11.32
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Leading the Way | Headroom (MW) | Thermal | 3.78 | 3.63 | 3.64 | 3.23 | 2.89 | 2.68 | 2.49 | 2.31 | 2.15 | 2 | 1.86 | 1.72 | 1.1 | 0.5 | -0.14 | -3 | -7.13 | -9.48
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | Steady Progression | Headroom (MW) | Thermal | 3.78 | 3.69 | 3.74 | 3.71 | 3.69 | 3.65 | 3.62 | 3.52 | 3.43 | 3.32 | 3.17 | 3 | 2.63 | 2.27 | 1.81 | 1.28 | 0.5 | -0.46
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | System Transformation | Headroom (MW) | Thermal | 3.78 | 3.67 | 3.71 | 3.66 | 3.54 | 3.46 | 3.36 | 3.03 | 2.64 | 2.21 | 1.64 | 0.99 | 0.32 | -0.27 | -0.99 | -2.4 | -4.74 | -6.96
Iron Acton 132kV | Chipping Sodbury 132 33 | NAISHCOMBE HILL 33 11kV S STN | Primary | 11 | -2.4273 | 51.4632 | WPD Best View | Headroom (MW) | Thermal | 3.78 | 3.67 | 3.71 | 3.66 | 3.55 | 3.46 | 3.36 | 3.04 | 2.65 | 2.22 | 1.65 | 1 | 0.33 | -0.26 | -0.98 | -2.39 | -4.72 | -6.94
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Consumer Transformation | Headroom (MW) | Thermal | 10.41 | 10.3 | 10.25 | 10.18 | 10.01 | 9.59 | 9.19 | 8.47 | 7.65 | 6.75 | 5.69 | 4.52 | 3.27 | 2.12 | 0.77 | -3.43 | -8.39 | -14.12
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Leading the Way | Headroom (MW) | Thermal | 10.41 | 10.29 | 10.23 | 10.16 | 9.92 | 9.45 | 8.99 | 8.56 | 8.14 | 7.73 | 7.29 | 6.85 | 5.8 | 4.73 | 3.62 | -0.97 | -6.71 | -11.48
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | Steady Progression | Headroom (MW) | N/A | 10.41 | 10.33 | 10.29 | 10.25 | 10.19 | 10.12 | 10.05 | 9.98 | 9.91 | 9.76 | 9.53 | 9.27 | 8.74 | 8.21 | 7.52 | 6.52 | 5.28 | 3.81
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | System Transformation | Headroom (MW) | Thermal | 10.41 | 10.31 | 10.27 | 10.22 | 10.12 | 10.07 | 10.01 | 9.46 | 8.68 | 8.01 | 7.12 | 6.14 | 5.11 | 4.21 | 3.13 | 0.97 | -2.48 | -6.42
Iron Acton 132kV | Chipping Sodbury 132 33 | OXBRIDGE 33 11kV S STN | Primary | 11 | -2.4592 | 51.5319 | WPD Best View | Headroom (MW) | Thermal | 10.41 | 10.31 | 10.27 | 10.22 | 10.12 | 10.07 | 10.01 | 9.46 | 8.68 | 8.01 | 7.12 | 6.14 | 5.11 | 4.21 | 3.13 | 0.97 | -2.48 | -6.42
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Consumer Transformation | Headroom (MW) | Thermal | 10.15 | 10.12 | 10.13 | 10.06 | 9.96 | 9.81 | 9.62 | 8.91 | 8.06 | 7.07 | 5.75 | 4.24 | 2.65 | 1.22 | -0.52 | -4.43 | -8.6 | -13.66
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Leading the Way | Headroom (MW) | Thermal | 10.15 | 10.12 | 10.13 | 10.07 | 9.96 | 9.78 | 9.56 | 9.38 | 9.2 | 8.99 | 8.79 | 5.43 | 4.18 | 3.01 | 1.79 | -2.49 | -7.69 | -10.04
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | Steady Progression | Headroom (MW) | N/A | 10.15 | 10.13 | 10.16 | 10.13 | 10.13 | 10.11 | 10.07 | 9.91 | 9.74 | 9.51 | 9.21 | 8.83 | 7.98 | 7.16 | 6.07 | 4.59 | 2.97 | 1.25
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | System Transformation | Headroom (MW) | Thermal | 10.15 | 10.13 | 10.15 | 10.11 | 10.08 | 10.05 | 9.98 | 9.33 | 8.47 | 7.56 | 6.31 | 4.88 | 3.37 | 2.03 | 0.38 | -2.36 | -5.9 | -10.24
Iron Acton 132kV | Ryeford 132 33 | BERKELEY 33 11kV S STN | Primary | 11 | -2.4681 | 51.7018 | WPD Best View | Headroom (MW) | Thermal | 10.15 | 10.13 | 10.16 | 10.13 | 10.13 | 10.11 | 10.07 | 9.81 | 9.51 | 9.14 | 8.65 | 8.07 | 7.09 | 6.17 | 4.97 | 3.34 | 1.45 | -0.67
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Consumer Transformation | Headroom (MW) | Thermal | 5.2 | 5.08 | 4.99 | 4.88 | 4.57 | 4.35 | 4.14 | 3.94 | 3.77 | 3.62 | 3.47 | 3.33 | 3.16 | 2.98 | 2.79 | 1.36 | -0.45 | -2.46
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Leading the Way | Headroom (MW) | Thermal | 5.2 | 5.07 | 4.97 | 4.86 | 4.49 | 4.26 | 4.05 | 3.85 | 3.69 | 3.54 | 3.38 | 3.21 | 3.01 | 2.8 | 2.57 | 0.99 | -1.01 | -3.67
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | Steady Progression | Headroom (MW) | N/A | 5.2 | 5.13 | 5.11 | 5.08 | 5.04 | 5 | 4.97 | 4.93 | 4.9 | 4.87 | 4.84 | 4.81 | 4.8 | 4.79 | 4.79 | 4.87 | 4.65 | 4.25
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | System Transformation | Headroom (MW) | N/A | 5.2 | 5.11 | 5.06 | 5 | 4.87 | 4.77 | 4.67 | 4.57 | 4.48 | 4.39 | 4.32 | 4.25 | 4.21 | 4.17 | 4.14 | 3.81 | 2.98 | 2.15
Iron Acton 132kV | Ryeford 132 33 | CAMP 33 11kV S STN | Primary | 11 | -2.1303 | 51.7865 | WPD Best View | Headroom (MW) | N/A | 5.2 | 5.13 | 5.11 | 5.08 | 5.04 | 5 | 4.97 | 4.93 | 4.9 | 4.87 | 4.84 | 4.81 | 4.8 | 4.79 | 4.79 | 4.87 | 4.65 | 4.25
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Consumer Transformation | Headroom (MW) | Thermal | 2.6 | 2.57 | 2.52 | 2.5 | 2.3 | 2.16 | 1.94 | 1.48 | 1.06 | 0.62 | 0.15 | -0.34 | -0.85 | -1.33 | -1.9 | -3.91 | -6.02 | -8.39
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Leading the Way | Headroom (MW) | Thermal | 2.6 | 2.56 | 2.51 | 2.5 | 2.24 | 2.11 | 1.87 | 1.66 | 1.49 | 1.3 | 1.12 | 0.96 | 0.55 | 0.15 | -0.28 | -2.18 | -4.37 | -6.22
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | Steady Progression | Headroom (MW) | N/A | 2.6 | 2.59 | 2.58 | 2.59 | 2.55 | 2.53 | 2.5 | 2.44 | 2.36 | 2.19 | 2.09 | 1.98 | 1.76 | 1.56 | 1.31 | 1 | 0.58 | 0.08
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | System Transformation | Headroom (MW) | Thermal | 2.6 | 2.58 | 2.56 | 2.56 | 2.46 | 2.4 | 2.34 | 2.13 | 1.8 | 1.49 | 1.14 | 0.77 | 0.39 | 0.06 | -0.33 | -1.15 | -2.25 | -3.51
Iron Acton 132kV | Ryeford 132 33 | CHERINGTON 33 11kV S STN | Primary | 11 | -2.1465 | 51.675 | WPD Best View | Headroom (MW) | N/A | 2.6 | 2.59 | 2.58 | 2.59 | 2.55 | 2.53 | 2.5 | 2.44 | 2.36 | 2.19 | 2.09 | 1.98 | 1.76 | 1.56 | 1.31 | 1 | 0.58 | 0.08
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Consumer Transformation | Headroom (MW) | Thermal | 28.49 | 28.07 | 27.75 | 27.36 | 26.19 | 25.4 | 24.63 | 23.9 | 23.23 | 22.65 | 22.03 | 21.37 | 20.71 | 20.02 | 19.3 | 13.93 | 7.28 | -0.06
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Leading the Way | Headroom (MW) | Thermal | 28.49 | 28.02 | 27.69 | 27.27 | 25.86 | 25.03 | 24.23 | 23.5 | 22.86 | 22.29 | 21.57 | 20.86 | 20.12 | 19.33 | 18.46 | 12.71 | 5.45 | -4.12
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | Steady Progression | Headroom (MW) | N/A | 28.49 | 28.25 | 28.18 | 28.06 | 27.85 | 27.69 | 27.53 | 27.38 | 27.24 | 27.08 | 26.94 | 26.83 | 26.74 | 26.68 | 26.64 | 26.57 | 25.46 | 23.93
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | System Transformation | Headroom (MW) | N/A | 28.49 | 28.17 | 28.02 | 27.74 | 27.2 | 26.83 | 26.43 | 26.06 | 25.71 | 25.39 | 25.09 | 24.82 | 24.59 | 24.39 | 24.14 | 22.65 | 19.54 | 16.44
Iron Acton 132kV | Ryeford 132 33 | DUDBRIDGE 33 11kV S STN | Primary | 11 | -2.2382 | 51.7403 | WPD Best View | Headroom (MW) | N/A | 28.49 | 28.25 | 28.18 | 28.06 | 27.85 | 27.69 | 27.53 | 27.38 | 27.24 | 27.08 | 26.94 | 26.83 | 26.74 | 26.68 | 26.64 | 26.57 | 25.46 | 23.93
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Consumer Transformation | Headroom (MW) | Thermal | 12.92 | 12.83 | 12.69 | 12.61 | 12.2 | 11.89 | 11.6 | 11.16 | 10.72 | 10.26 | 9.7 | 9.08 | 8.4 | 7.77 | 7.02 | 4.3 | 0.04 | -3.96
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Leading the Way | Headroom (MW) | Thermal | 12.92 | 12.83 | 12.68 | 12.62 | 12.14 | 11.82 | 11.51 | 11.23 | 10.98 | 10.75 | 10.52 | 10.23 | 9.64 | 9.04 | 8.39 | 5.34 | 0.25 | -3.8
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | Steady Progression | Headroom (MW) | N/A | 12.92 | 12.89 | 12.84 | 12.87 | 12.81 | 12.76 | 12.7 | 12.59 | 12.49 | 12.38 | 12.24 | 12.1 | 11.82 | 11.55 | 11.22 | 10.83 | 10.09 | 9.02
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | System Transformation | Headroom (MW) | N/A | 12.92 | 12.87 | 12.78 | 12.78 | 12.61 | 12.47 | 12.31 | 12 | 11.65 | 11.28 | 10.82 | 10.31 | 9.8 | 9.37 | 8.83 | 7.66 | 5.03 | 2.71
Iron Acton 132kV | Ryeford 132 33 | DURSLEY 33 11kV S STN | Primary | 11 | -2.3478 | 51.6907 | WPD Best View | Headroom (MW) | N/A | 12.92 | 12.89 | 12.84 | 12.87 | 12.81 | 12.76 | 12.7 | 12.59 | 12.49 | 12.38 | 12.24 | 12.1 | 11.82 | 11.55 | 11.22 | 10.83 | 10.09 | 9.02
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Consumer Transformation | Headroom (MW) | Thermal | 9.17 | 9.2 | 9.15 | 9.1 | 8.9 | 8.64 | 8.35 | 7.55 | 6.64 | 5.63 | 4.41 | 3.05 | 1.63 | 0.33 | -1.23 | -4.72 | -8.67 | -13.38
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Leading the Way | Headroom (MW) | Thermal | 9.17 | 9.21 | 9.16 | 9.11 | 8.85 | 8.53 | 8.19 | 7.83 | 7.5 | 7.17 | 6.86 | 6.55 | 5.39 | 4.31 | 3.19 | -0.54 | -5.36 | -8.11
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | Steady Progression | Headroom (MW) | N/A | 9.17 | 9.27 | 9.2 | 9.2 | 9.17 | 9.13 | 9.08 | 8.91 | 8.74 | 8.53 | 8.26 | 7.94 | 7.22 | 6.53 | 5.63 | 4.35 | 3.02 | 1.58
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | System Transformation | Headroom (MW) | Thermal | 9.17 | 9.22 | 9.19 | 9.17 | 9.07 | 9 | 8.89 | 8.23 | 7.33 | 6.48 | 5.39 | 4.16 | 2.86 | 1.71 | 0.29 | -1.96 | -5.11 | -8.91
Iron Acton 132kV | Ryeford 132 33 | NETHERHILLS 33 11kV S STN | Primary | 11 | -2.3406 | 51.7621 | WPD Best View | Headroom (MW) | N/A | 9.17 | 9.27 | 9.2 | 9.2 | 9.17 | 9.13 | 9.08 | 8.91 | 8.74 | 8.53 | 8.26 | 7.94 | 7.22 | 6.53 | 5.63 | 4.35 | 3.02 | 1.58
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Consumer Transformation | Headroom (MW) | N/A | 29.42 | 29.26 | 29.26 | 25.61 | 25.26 | 25 | 24.75 | 24.49 | 24.25 | 24.03 | 23.8 | 23.57 | 23.35 | 23.13 | 22.88 | 21.17 | 19.09 | 16.8
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Leading the Way | Headroom (MW) | N/A | 29.42 | 29.24 | 29.25 | 25.63 | 25.2 | 24.92 | 24.65 | 24.38 | 24.12 | 23.89 | 23.64 | 23.39 | 23.15 | 22.89 | 22.6 | 20.83 | 18.59 | 15.68
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | Steady Progression | Headroom (MW) | N/A | 28.0423 | 28.0388 | 28.0353 | 23.7331 | 23.7291 | 23.7155 | 23.6992 | 23.6789 | 23.6582 | 23.634 | 23.6093 | 23.5838 | 23.5591 | 23.5345 | 23.5107 | 23.3962 | 23.2795 | 23.1636
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | System Transformation | Headroom (MW) | N/A | 29.42 | 29.27 | 29.28 | 25.65 | 25.52 | 25.39 | 25.23 | 25.07 | 24.92 | 24.78 | 24.63 | 24.49 | 24.37 | 24.26 | 24.15 | 23.54 | 22.46 | 21.39
Iron Acton 132kV | Ryeford 132 33 | Ryeford 132/33/11kVDUMMY | Primary | 11 | -2.2725 | 51.7391 | WPD Best View | Headroom (MW) | N/A | 29.42 | 29.28 | 29.29 | 25.65 | 25.57 | 25.51 | 25.45 | 25.39 | 25.32 | 25.23 | 25.14 | 25.06 | 24.97 | 24.9 | 24.82 | 24.56 | 24.13 | 23.51
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Consumer Transformation | Headroom (MW) | N/A | 34.99 | 34.73 | 34.62 | 34.56 | 34.05 | 33.63 | 33.25 | 32.73 | 32.28 | 31.86 | 31.49 | 31.16 | 30.83 | 30.48 | 30.11 | 26.19 | 22.38 | 18.37
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Leading the Way | Headroom (MW) | N/A | 34.99 | 34.71 | 34.62 | 34.61 | 34.01 | 33.57 | 33.17 | 32.72 | 32.36 | 31.99 | 31.61 | 31.26 | 30.89 | 30.47 | 29.97 | 24.98 | 22.65 | 13.95
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | Steady Progression | Headroom (MW) | N/A | 34.99 | 34.81 | 34.86 | 34.93 | 34.9 | 33.79 | 33.72 | 33.37 | 33.05 | 32.71 | 32.41 | 32.16 | 31.99 | 31.84 | 31.74 | 31.61 | 31.1 | 30
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | System Transformation | Headroom (MW) | N/A | 34.99 | 34.78 | 34.81 | 34.78 | 34.59 | 34.4 | 34.21 | 33.87 | 33.58 | 33.31 | 33.07 | 32.87 | 32.7 | 32.55 | 32.41 | 30.84 | 30.83 | 26.73
Ironbridge & Shrewsbury 132kV | Hortonwood 132 11 (GT1) | HORTONWOOD 132 11kV S STN | Primary | 11 | -2.4889 | 52.7191 | WPD Best View | Headroom (MW) | N/A | 34.99 | 34.71 | 34.62 | 34.61 | 34.01 | 33.57 | 33.17 | 32.72 | 32.36 | 31.99 | 31.61 | 31.26 | 30.89 | 30.47 | 29.97 | 24.98 | 22.65 | 13.95
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Consumer Transformation | Headroom (MW) | Thermal | 6.69 | 6.6 | 6.52 | 6.43 | 6.15 | 5.92 | 5.71 | 5.1 | 4.38 | 3.59 | 2.53 | 1.34 | 0.08 | -1.07 | -2.48 | -5.65 | -9.58 | -14.27
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Leading the Way | Headroom (MW) | Thermal | 6.69 | 6.59 | 6.51 | 6.41 | 6.09 | 5.86 | 5.64 | 5.43 | 5.25 | 5.08 | 4.9 | 4.72 | 3.75 | 2.79 | 1.78 | -1.72 | -6.51 | -9.46
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | Steady Progression | Headroom (MW) | Thermal | 6.69 | 6.64 | 6.62 | 6.6 | 6.57 | 6.53 | 6.49 | 6.36 | 6.22 | 6.05 | 5.82 | 5.54 | 4.9 | 4.27 | 3.45 | 2.48 | 1.19 | -0.28
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | System Transformation | Headroom (MW) | Thermal | 6.69 | 6.62 | 6.58 | 6.53 | 6.41 | 6.32 | 6.21 | 5.71 | 5.08 | 4.36 | 3.38 | 2.27 | 1.1 | 0.08 | -1.18 | -3.13 | -6.09 | -9.6
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | BROSELEY 33 11kV S STN | Primary | 11 | -2.4845 | 52.6106 | WPD Best View | Headroom (MW) | Thermal | 6.69 | 6.62 | 6.56 | 6.5 | 6.34 | 6.22 | 6.08 | 5.56 | 4.91 | 4.18 | 3.18 | 2.05 | 0.86 | -0.19 | -1.49 | -3.73 | -6.92 | -10.8
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Consumer Transformation | Headroom (MW) | Thermal | 1.05 | 1.01 | 0.99 | 0.96 | 0.86 | 0.8 | 0.75 | 0.7 | 0.65 | 0.61 | 0.57 | 0.53 | 0.49 | 0.45 | 0.41 | 0.03 | -0.4 | -0.88
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Leading the Way | Headroom (MW) | Thermal | 1.05 | 1.01 | 0.98 | 0.95 | 0.84 | 0.77 | 0.71 | 0.66 | 0.61 | 0.57 | 0.53 | 0.49 | 0.44 | 0.4 | 0.34 | -0.05 | -0.52 | -1.14
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | Steady Progression | Headroom (MW) | N/A | 1.05 | 1.03 | 1.02 | 1.01 | 0.99 | 0.97 | 0.96 | 0.94 | 0.93 | 0.92 | 0.9 | 0.89 | 0.89 | 0.88 | 0.88 | 0.88 | 0.83 | 0.73
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | System Transformation | Headroom (MW) | N/A | 1.05 | 1.02 | 1 | 0.99 | 0.94 | 0.91 | 0.88 | 0.85 | 0.83 | 0.8 | 0.78 | 0.76 | 0.74 | 0.73 | 0.71 | 0.64 | 0.43 | 0.22
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | EASTHOPE 33 11kV S STN | Primary | 11 | -2.6368 | 52.5521 | WPD Best View | Headroom (MW) | N/A | 1.05 | 1.02 | 1 | 0.99 | 0.94 | 0.91 | 0.88 | 0.85 | 0.83 | 0.8 | 0.78 | 0.76 | 0.74 | 0.73 | 0.71 | 0.64 | 0.43 | 0.22
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Consumer Transformation | Headroom (MW) | N/A | 26.42 | 26.25 | 26.16 | 26.12 | 25.87 | 25.78 | 25.65 | 25.26 | 24.88 | 24.6 | 24.38 | 24.2 | 24.05 | 23.89 | 23.71 | 22.33 | 21.17 | 20.13
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Leading the Way | Headroom (MW) | N/A | 26.42 | 26.23 | 26.13 | 26.11 | 25.74 | 25.65 | 25.51 | 25.31 | 25.11 | 24.96 | 24.79 | 24.62 | 24.44 | 24.25 | 24.04 | 22.79 | 25.34 | 16.89
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | Steady Progression | Headroom (MW) | N/A | 26.42 | 26.27 | 26.19 | 26.16 | 26.03 | 25.97 | 25.9 | 25.52 | 25.11 | 24.74 | 24.39 | 24.1 | 23.92 | 23.77 | 23.66 | 23.32 | 22.96 | 22.58
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | System Transformation | Headroom (MW) | N/A | 26.42 | 26.26 | 26.17 | 26.15 | 25.96 | 25.89 | 25.81 | 25.53 | 25.25 | 25.06 | 24.91 | 24.82 | 24.72 | 24.63 | 24.55 | 24.06 | 27.44 | 22.39
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | HALESFIELD 33 11kV S STN | Primary | 11 | -2.433 | 52.641 | WPD Best View | Headroom (MW) | N/A | 26.42 | 26.23 | 26.13 | 26.11 | 25.74 | 25.65 | 25.51 | 25.31 | 25.11 | 24.96 | 24.79 | 24.62 | 24.44 | 24.25 | 24.04 | 22.79 | 25.34 | 16.89
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Consumer Transformation | Headroom (MW) | Thermal | 5.415 | 5.315 | 5.235 | 5.145 | 4.885 | 4.695 | 4.515 | 4.335 | 4.165 | 4.025 | 3.875 | 3.745 | 3.615 | 3.475 | 3.295 | 2.075 | 0.555 | -1.125
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Leading the Way | Headroom (MW) | Thermal | 5.415 | 5.305 | 5.225 | 5.125 | 4.825 | 4.635 | 4.445 | 4.265 | 4.105 | 3.965 | 3.815 | 3.675 | 3.535 | 3.355 | 3.145 | 1.805 | 0.115 | -2.085
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | Steady Progression | Headroom (MW) | N/A | 5.415 | 5.355 | 5.325 | 5.305 | 5.265 | 5.225 | 5.195 | 5.155 | 5.125 | 5.085 | 5.045 | 5.025 | 4.995 | 4.985 | 4.975 | 5.025 | 4.865 | 4.515
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | System Transformation | Headroom (MW) | N/A | 5.415 | 5.335 | 5.285 | 5.235 | 5.125 | 5.045 | 4.945 | 4.855 | 4.765 | 4.685 | 4.615 | 4.545 | 4.495 | 4.455 | 4.415 | 4.155 | 3.435 | 2.725
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | LEEBOTWOOD 33 11kV S STN | Primary | 11 | -2.7663 | 52.5785 | WPD Best View | Headroom (MW) | N/A | 5.415 | 5.335 | 5.285 | 5.235 | 5.125 | 5.045 | 4.945 | 4.855 | 4.765 | 4.685 | 4.615 | 4.545 | 4.495 | 4.455 | 4.415 | 4.155 | 3.435 | 2.725
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Consumer Transformation | Headroom (MW) | Thermal | 13.49 | 13.34 | 13.21 | 12.97 | 12.39 | 11.95 | 11.54 | 11.03 | 10.53 | 10.03 | 9.47 | 8.86 | 8.22 | 7.6 | 6.88 | 3.41 | -1.3 | -6.62
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Leading the Way | Headroom (MW) | Thermal | 13.49 | 13.32 | 13.18 | 12.92 | 12.25 | 11.79 | 11.36 | 10.97 | 10.63 | 10.3 | 9.94 | 9.56 | 8.95 | 8.32 | 7.62 | 3.67 | -1.67 | -7.93
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | Steady Progression | Headroom (MW) | N/A | 13.49 | 13.37 | 13.32 | 13.26 | 13.18 | 13.13 | 13.07 | 12.96 | 12.85 | 12.73 | 12.61 | 12.49 | 12.29 | 12.12 | 11.9 | 11.63 | 10.8 | 9.68
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | System Transformation | Headroom (MW) | N/A | 13.49 | 13.35 | 13.28 | 13.2 | 12.94 | 12.73 | 12.51 | 12.19 | 11.85 | 11.51 | 11.13 | 10.74 | 10.35 | 9.97 | 9.54 | 8.36 | 5.86 | 3.18
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | MADELEY 33 11kV S STN | Primary | 11 | -2.4532 | 52.6509 | WPD Best View | Headroom (MW) | Thermal | 13.49 | 13.32 | 13.18 | 12.92 | 12.25 | 11.79 | 11.36 | 10.97 | 10.63 | 10.3 | 9.94 | 9.56 | 8.95 | 8.32 | 7.62 | 3.67 | -1.67 | -7.93
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Consumer Transformation | Headroom (MW) | Thermal | 13.63 | 13.39 | 13.3 | 13.17 | 13.13 | 12.84 | 12.54 | 11.97 | 11.35 | 10.68 | 9.91 | 9.02 | 8.09 | 7.23 | 6.2 | 2.57 | -1.42 | -6.02
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Leading the Way | Headroom (MW) | Thermal | 13.63 | 13.37 | 13.29 | 13.15 | 13.15 | 12.86 | 12.54 | 12.24 | 11.97 | 11.72 | 11.49 | 11.26 | 10.5 | 9.77 | 8.96 | 5.01 | 0.32 | -3.69
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | Steady Progression | Headroom (MW) | N/A | 13.63 | 13.46 | 13.44 | 13.4 | 13.68 | 13.64 | 13.59 | 13.47 | 13.36 | 13.21 | 13.04 | 12.84 | 12.42 | 11.99 | 11.43 | 10.75 | 9.73 | 8.3
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | System Transformation | Headroom (MW) | N/A | 13.63 | 13.43 | 13.39 | 13.31 | 13.53 | 13.41 | 13.26 | 12.82 | 12.3 | 11.74 | 11.06 | 10.27 | 9.45 | 8.75 | 7.89 | 6.18 | 3.52 | 0.47
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | STAR ALUMINIUM 33 11kV S STN | Primary | 11 | -2.4626 | 52.5213 | WPD Best View | Headroom (MW) | N/A | 13.63 | 13.43 | 13.39 | 13.31 | 13.53 | 13.41 | 13.26 | 12.82 | 12.3 | 11.74 | 11.06 | 10.27 | 9.45 | 8.75 | 7.89 | 6.18 | 3.52 | 0.47
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Consumer Transformation | Headroom (MW) | Thermal | 3.23 | 3.19 | 3.1 | 3.06 | 2.97 | 2.9 | 2.83 | 2.57 | 2.27 | 1.93 | 1.51 | 1.04 | 0.55 | 0.1 | -0.45 | -1.55 | -2.85 | -4.43
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Leading the Way | Headroom (MW) | Thermal | 3.23 | 3.19 | 3.09 | 3.05 | 2.95 | 2.87 | 2.79 | 2.72 | 2.64 | 2.57 | 2.5 | 2.43 | 2.04 | 1.67 | 1.28 | 0.05 | -1.58 | -2.46
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | Steady Progression | Headroom (MW) | N/A | 3.23 | 3.2 | 3.19 | 3.18 | 3.16 | 3.14 | 3.13 | 3.06 | 3 | 2.92 | 2.82 | 2.7 | 2.44 | 2.19 | 1.87 | 1.45 | 0.98 | 0.46
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | System Transformation | Headroom (MW) | Thermal | 3.23 | 3.2 | 3.18 | 3.09 | 3.05 | 3.01 | 2.97 | 2.74 | 2.46 | 2.15 | 1.76 | 1.32 | 0.86 | 0.45 | -0.06 | -0.81 | -1.84 | -3.08
Ironbridge & Shrewsbury 132kV | Ironbridge 132 33 | WORFIELD 33 11kV S STN | Primary | 11 | -2.3364 | 52.5727 | WPD Best View | Headroom (MW) | Thermal | 3.23 | 3.2 | 3.18 | 3.09 | 3.05 | 3.01 | 2.97 | 2.74 | 2.46 | 2.14 | 1.75 | 1.31 | 0.84 | 0.43 | -0.07 | -0.82 | -1.85 | -3.1
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Consumer Transformation | Headroom (MW) | Thermal | 6.44 | 6.31 | 6.21 | 6.09 | 5.83 | 5.64 | 5.35 | 4.96 | 4.65 | 4.38 | 4.09 | 3.83 | 3.58 | 3.3 | 3 | 0.98 | -2.74 | -5.68
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Leading the Way | Headroom (MW) | Thermal | 6.44 | 6.3 | 6.2 | 6.07 | 5.78 | 5.6 | 5.29 | 5.01 | 4.77 | 4.51 | 4.27 | 4.04 | 3.79 | 3.52 | 3.21 | 1.21 | -3.44 | -6.74
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | Steady Progression | Headroom (MW) | N/A | 6.44 | 6.36 | 6.31 | 6.27 | 6.22 | 6.19 | 6.15 | 6.1 | 6.04 | 5.88 | 5.82 | 5.76 | 5.7 | 5.66 | 5.64 | 5.67 | 5.49 | 5.03
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | System Transformation | Headroom (MW) | N/A | 6.44 | 6.33 | 6.27 | 6.2 | 6.08 | 5.99 | 5.9 | 5.8 | 5.6 | 5.48 | 5.35 | 5.24 | 5.15 | 5.08 | 5.02 | 4.67 | 2.63 | 1.57
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DONNINGTON 33 11kV S STN | Primary | 11 | -2.4338 | 52.7265 | WPD Best View | Headroom (MW) | Thermal | 6.44 | 6.3 | 6.2 | 6.08 | 5.79 | 5.62 | 5.44 | 5.26 | 5 | 4.81 | 4.62 | 4.45 | 4.28 | 4.11 | 3.9 | 2.33 | -1.72 | -4.4
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Consumer Transformation | Headroom (MW) | Thermal | 3.09 | 2.99 | 2.89 | 2.77 | 2.5 | 2.28 | 2.11 | 2.01 | 1.9 | 1.78 | 1.67 | 1.57 | 1.43 | 1.28 | 1.12 | -0.99 | -2.68 | -4.78
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Leading the Way | Headroom (MW) | Thermal | 3.09 | 2.98 | 2.87 | 2.75 | 2.45 | 2.22 | 2.07 | 2.02 | 1.94 | 1.81 | 1.69 | 1.56 | 1.39 | 1.21 | 0.99 | -2.16 | -3.13 | -7.87
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | Steady Progression | Headroom (MW) | N/A | 3.09 | 3.04 | 3.01 | 2.99 | 2.96 | 2.92 | 2.89 | 2.91 | 2.92 | 2.91 | 2.9 | 2.9 | 2.91 | 2.93 | 2.96 | 3.18 | 3.05 | 2.63
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | System Transformation | Headroom (MW) | Thermal | 3.09 | 3.02 | 2.96 | 2.9 | 2.79 | 2.69 | 2.61 | 2.61 | 2.58 | 2.52 | 2.47 | 2.43 | 2.41 | 2.4 | 2.4 | 1.4 | 1.48 | -0.66
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | DOTHILL 33 11kV S STN | Primary | 11 | -2.5343 | 52.7167 | WPD Best View | Headroom (MW) | Thermal | 3.09 | 2.98 | 2.87 | 2.75 | 2.46 | 2.22 | 2.06 | 2.01 | 1.93 | 1.8 | 1.68 | 1.55 | 1.39 | 1.21 | 0.99 | -2.21 | -3.39 | -7.51
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Consumer Transformation | Headroom (MW) | N/A | 29.62 | 29.43 | 29.26 | 29.06 | 28.55 | 28.14 | 27.76 | 27.4 | 27.08 | 26.81 | 26.55 | 26.26 | 25.95 | 25.62 | 25.28 | 22.76 | 19.31 | 15.47
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Leading the Way | Headroom (MW) | N/A | 29.62 | 29.42 | 29.24 | 29.02 | 28.46 | 28.05 | 27.66 | 27.31 | 27.01 | 26.76 | 26.48 | 26.15 | 25.8 | 25.43 | 25.01 | 22.12 | 18.3 | 13.24
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | Steady Progression | Headroom (MW) | N/A | 29.62 | 29.52 | 29.47 | 29.43 | 29.37 | 29.3 | 29.23 | 29.15 | 29.09 | 29.02 | 28.97 | 28.92 | 28.88 | 28.86 | 28.85 | 28.79 | 28.28 | 27.55
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | System Transformation | Headroom (MW) | N/A | 29.62 | 29.48 | 29.38 | 29.27 | 29.07 | 28.89 | 28.68 | 28.49 | 28.32 | 28.18 | 28.03 | 27.91 | 27.82 | 27.75 | 27.66 | 26.91 | 25.3 | 23.74
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | Ketley 132/33/11kVDUMMY | Primary | 11 | -2.4835 | 52.6945 | WPD Best View | Headroom (MW) | N/A | 29.62 | 29.42 | 29.24 | 29.02 | 28.46 | 28.05 | 27.66 | 27.31 | 27.01 | 26.76 | 26.48 | 26.15 | 25.8 | 25.43 | 25.01 | 22.12 | 18.3 | 13.24
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Consumer Transformation | Headroom (MW) | N/A | 11.63 | 11.39 | 11.22 | 11.04 | 10.64 | 10.37 | 10.07 | 9.77 | 9.54 | 9.3 | 9.07 | 8.86 | 8.65 | 8.44 | 8.22 | 6.39 | 3.98 | 1.35
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Leading the Way | Headroom (MW) | N/A | 11.63 | 11.37 | 11.2 | 11.01 | 10.57 | 10.32 | 10.02 | 9.74 | 9.55 | 9.33 | 9.09 | 8.87 | 8.65 | 8.4 | 8.11 | 6 | 3.46 | 0.11
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | Steady Progression | Headroom (MW) | N/A | 11.63 | 11.45 | 11.36 | 11.28 | 11.18 | 11.12 | 11.03 | 10.91 | 10.82 | 10.72 | 10.62 | 10.54 | 10.48 | 10.43 | 10.39 | 10.37 | 10.06 | 9.37
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | System Transformation | Headroom (MW) | N/A | 11.63 | 11.42 | 11.3 | 11.17 | 10.97 | 10.85 | 10.67 | 10.48 | 10.35 | 10.2 | 10.05 | 9.93 | 9.83 | 9.75 | 9.68 | 9.26 | 8.04 | 6.81
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | NEWPORT 33 11kV S STN | Primary | 11 | -2.3948 | 52.765 | WPD Best View | Headroom (MW) | N/A | 11.63 | 11.37 | 11.2 | 11.01 | 10.58 | 10.33 | 10.03 | 9.77 | 9.59 | 9.38 | 9.15 | 8.94 | 8.73 | 8.49 | 8.21 | 6.13 | 3.62 | 0.31
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Consumer Transformation | Headroom (MW) | N/A | 8.68 | 8.6 | 8.54 | 8.46 | 8.29 | 8.17 | 8.03 | 7.91 | 7.79 | 7.68 | 7.57 | 7.47 | 7.38 | 7.27 | 7.14 | 6.3 | 5.03 | 3.61
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Leading the Way | Headroom (MW) | N/A | 8.68 | 8.6 | 8.53 | 8.44 | 8.25 | 8.14 | 8.01 | 7.9 | 7.79 | 7.69 | 7.59 | 7.49 | 7.38 | 7.26 | 7.11 | 6.16 | 4.72 | 2.84
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | Steady Progression | Headroom (MW) | N/A | 8.68 | 8.64 | 8.63 | 8.61 | 8.62 | 8.62 | 8.62 | 8.61 | 8.6 | 8.6 | 8.6 | 8.61 | 8.63 | 8.65 | 8.68 | 8.88 | 8.72 | 8.41
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | System Transformation | Headroom (MW) | N/A | 8.68 | 8.62 | 8.59 | 8.55 | 8.5 | 8.46 | 8.4 | 8.35 | 8.31 | 8.27 | 8.23 | 8.2 | 8.18 | 8.17 | 8.16 | 8.08 | 7.49 | 6.89
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SHIFNAL 33 11kV S STN | Primary | 11 | -2.3783 | 52.6656 | WPD Best View | Headroom (MW) | N/A | 8.68 | 8.62 | 8.59 | 8.55 | 8.5 | 8.46 | 8.4 | 8.34 | 8.29 | 8.24 | 8.19 | 8.15 | 8.11 | 8.1 | 8.08 | 7.98 | 7.36 | 6.73
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Consumer Transformation | Headroom (MW) | N/A | 26.721 | 26.6272 | 26.407 | 26.2743 | 25.9526 | 25.6316 | 25.3036 | 24.9659 | 24.6213 | 24.2836 | 23.9154 | 23.536 | 23.1538 | 22.771 | 22.3979 | 20.5261 | 17.44 | 13.88
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Leading the Way | Headroom (MW) | N/A | 29.63 | 29.33 | 29.1 | 28.95 | 28.32 | 27.91 | 27.5 | 27.12 | 26.7 | 26.3 | 25.86 | 25.43 | 24.97 | 24.49 | 23.99 | 20.98 | 15.94 | 11.46
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | Steady Progression | Headroom (MW) | N/A | 15.051 | 15.0379 | 15.0261 | 15.0164 | 15.0055 | 14.9841 | 14.9592 | 14.9308 | 14.9031 | 14.8708 | 14.8362 | 14.8017 | 14.7646 | 14.7263 | 14.6893 | 14.5221 | 14.3942 | 14.2681
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | System Transformation | Headroom (MW) | N/A | 21.5078 | 21.4718 | 21.4317 | 21.3227 | 21.2485 | 21.1591 | 21.0523 | 20.942 | 20.8286 | 20.7174 | 20.5941 | 20.4656 | 20.3348 | 20.2031 | 20.075 | 19.4456 | 18.4902 | 17.8235
Ironbridge & Shrewsbury 132kV | Ketley 132 33 | SNEDSHILL 33 11kV S STN | Primary | 11 | -2.442 | 52.6889 | WPD Best View | Headroom (MW) | N/A | 22.4248 | 22.3585 | 22.2068 | 22.1145 | 21.9002 | 21.6846 | 21.462 | 21.2329 | 20.9991 | 20.7649 | 20.514 | 20.2543 | 19.9806 | 19.6431 | 19.3169 | 17.6815 | 15.0483 | 11.46
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Consumer Transformation | Headroom (MW) | N/A | 14.34 | 14.13 | 13.99 | 13.81 | 13.41 | 13.09 | 12.78 | 12.48 | 12.21 | 11.97 | 11.73 | 11.5 | 11.22 | 10.94 | 10.65 | 8.51 | 5.69 | 2.57
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Leading the Way | Headroom (MW) | N/A | 14.34 | 14.12 | 13.97 | 13.78 | 13.33 | 13 | 12.68 | 12.39 | 12.13 | 11.9 | 11.63 | 11.37 | 11.07 | 10.74 | 10.38 | 7.96 | 4.85 | 0.73
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | Steady Progression | Headroom (MW) | N/A | 14.34 | 14.2 | 14.15 | 14.09 | 14.03 | 13.95 | 13.87 | 13.79 | 13.72 | 13.64 | 13.57 | 13.51 | 13.47 | 13.43 | 13.4 | 13.38 | 12.95 | 12.24
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | System Transformation | Headroom (MW) | N/A | 14.34 | 14.17 | 14.08 | 13.97 | 13.8 | 13.64 | 13.47 | 13.31 | 13.16 | 13.02 | 12.89 | 12.77 | 12.68 | 12.59 | 12.52 | 11.93 | 10.55 | 9.17
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BAYSTON HILL 33 11kV S STN | Primary | 11 | -2.7615 | 52.6764 | WPD Best View | Headroom (MW) | N/A | 14.34 | 14.17 | 14.08 | 13.97 | 13.8 | 13.64 | 13.47 | 13.31 | 13.16 | 13.02 | 12.89 | 12.77 | 12.68 | 12.59 | 12.52 | 11.93 | 10.55 | 9.17
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Consumer Transformation | Headroom (MW) | Thermal | 1.13 | 1.12 | 1.11 | 1.09 | 1.02 | 0.98 | 0.93 | 0.61 | 0.23 | -0.2 | -0.75 | -1.37 | -2.03 | -2.62 | -3.36 | -4.63 | -6.09 | -7.9
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Leading the Way | Headroom (MW) | Thermal | 1.13 | 1.11 | 1.1 | 1.09 | 0.99 | 0.94 | 0.89 | 0.83 | 0.78 | 0.72 | 0.68 | 0.63 | 0.13 | -0.34 | -0.83 | -2.23 | -4.12 | -4.8
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | Steady Progression | Headroom (MW) | Thermal | 1.13 | 1.13 | 1.13 | 1.13 | 1.12 | 1.11 | 1.11 | 1.04 | 0.96 | 0.87 | 0.75 | 0.6 | 0.24 | -0.11 | -0.57 | -1.14 | -1.73 | -2.36
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | System Transformation | Headroom (MW) | Thermal | 1.13 | 1.12 | 1.12 | 1.11 | 1.08 | 1.06 | 1.04 | 0.75 | 0.38 | -0.04 | -0.57 | -1.17 | -1.81 | -2.38 | -3.08 | -4.06 | -5.33 | -6.92
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | BERRINGTON 33 11kV S STN | Primary | 11 | -2.6851 | 52.6659 | WPD Best View | Headroom (MW) | Thermal | 1.13 | 1.12 | 1.12 | 1.11 | 1.08 | 1.06 | 1.04 | 0.75 | 0.38 | -0.04 | -0.57 | -1.17 | -1.81 | -2.38 | -3.08 | -4.06 | -5.33 | -6.92
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Consumer Transformation | Headroom (MW) | Thermal | 9.16 | 9.08 | 9.03 | 8.97 | 8.75 | 8.59 | 7.98 | 6.66 | 5.55 | 4.45 | 3.22 | 1.94 | 0.63 | -0.64 | -2.13 | -7.01 | -12.78 | -19.07
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Leading the Way | Headroom (MW) | Thermal | 9.16 | 9.07 | 9.03 | 8.97 | 8.7 | 8.54 | 7.87 | 7.31 | 6.88 | 6.3 | 5.78 | 5.29 | 4.29 | 3.28 | 2.2 | -2.03 | -7.44 | -11.71
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | Steady Progression | Headroom (MW) | N/A | 9.16 | 9.11 | 9.09 | 9.07 | 9.03 | 8.99 | 8.95 | 8.84 | 8.64 | 8.03 | 7.8 | 7.52 | 6.98 | 6.5 | 5.93 | 5.08 | 4.15 | 3.15
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | System Transformation | Headroom (MW) | Thermal | 9.16 | 9.1 | 9.07 | 9.04 | 8.93 | 8.86 | 8.77 | 8.4 | 7.53 | 6.87 | 6.05 | 5.19 | 4.31 | 3.56 | 2.66 | 0.9 | -1.55 | -4.43
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | HARLESCOTT 33 11kV S STN | Primary | 11 | -2.7285 | 52.7388 | WPD Best View | Headroom (MW) | Thermal | 9.16 | 9.1 | 9.07 | 9.04 | 8.93 | 8.86 | 8.77 | 8.4 | 7.53 | 6.87 | 6.05 | 5.19 | 4.31 | 3.56 | 2.66 | 0.9 | -1.55 | -4.43
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Consumer Transformation | Headroom (MW) | Thermal | 1.805 | 1.385 | 1.145 | 1.095 | 0.955 | 0.845 | 0.735 | 0.215 | -0.395 | -1.095 | -1.985 | -2.995 | -4.075 | -5.035 | -6.225 | -8.405 | -11.325 | -14.465
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Leading the Way | Headroom (MW) | Thermal | 1.805 | 1.375 | 1.145 | 1.085 | 0.915 | 0.795 | 0.665 | 0.525 | 0.395 | 0.255 | 0.145 | 0.045 | -0.785 | -1.555 | -2.355 | -4.755 | -8.725 | -10.125
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | Steady Progression | Headroom (MW) | Thermal | 1.805 | 1.765 | 1.395 | 1.375 | 1.345 | 1.325 | 1.305 | 1.185 | 1.055 | 0.905 | 0.705 | 0.455 | -0.125 | -0.685 | -1.415 | -2.365 | -3.395 | -4.505
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | System Transformation | Headroom (MW) | Thermal | 1.805 | 1.395 | 1.365 | 1.145 | 1.075 | 1.025 | 0.955 | 0.495 | -0.085 | -0.735 | -1.585 | -2.545 | -3.565 | -4.465 | -5.585 | -7.235 | -9.755 | -12.425
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | LEATON 33 11kV S STN | Primary | 11 | -2.5751 | 52.7026 | WPD Best View | Headroom (MW) | Thermal | 1.805 | 1.385 | 1.155 | 1.105 | 0.975 | 0.875 | 0.775 | 0.495 | 0.175 | -0.185 | -0.625 | -1.125 | -2.035 | -2.865 | -3.805 | -5.835 | -8.945 | -10.945
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Consumer Transformation | Headroom (MW) | N/A | 7.56 | 7.47 | 7.4 | 7.32 | 7.13 | 6.98 | 6.84 | 6.7 | 6.58 | 6.46 | 6.36 | 6.26 | 6.16 | 6.04 | 5.91 | 5.01 | 3.85 | 2.57
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Leading the Way | Headroom (MW) | N/A | 7.56 | 7.46 | 7.39 | 7.3 | 7.09 | 6.94 | 6.79 | 6.66 | 6.54 | 6.43 | 6.32 | 6.21 | 6.09 | 5.95 | 5.8 | 4.79 | 3.5 | 1.78
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | Steady Progression | Headroom (MW) | N/A | 7.56 | 7.5 | 7.48 | 5.91 | 5.87 | 5.84 | 5.77 | 5.74 | 5.7 | 5.67 | 5.64 | 5.62 | 5.6 | 5.58 | 5.57 | 5.6 | 5.47 | 5.2
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | System Transformation | Headroom (MW) | N/A | 7.56 | 7.49 | 7.44 | 7.39 | 7.31 | 7.23 | 7.16 | 7.08 | 7.01 | 6.94 | 6.88 | 6.83 | 6.8 | 6.77 | 6.74 | 6.52 | 5.97 | 5.42
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | MALEHURST 33 11kV S STN | Primary | 11 | -2.9104 | 52.6503 | WPD Best View | Headroom (MW) | N/A | 7.56 | 7.49 | 7.44 | 7.39 | 7.31 | 7.23 | 7.16 | 7.08 | 7.01 | 6.94 | 6.88 | 6.83 | 6.8 | 6.77 | 6.74 | 6.52 | 5.97 | 5.42
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Consumer Transformation | Headroom (MW) | N/A | 4.22 | 4.15 | 4.11 | 4.07 | 3.95 | 3.87 | 3.79 | 3.71 | 3.63 | 3.56 | 3.49 | 3.42 | 3.35 | 3.28 | 3.21 | 2.7 | 2.14 | 1.53
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Leading the Way | Headroom (MW) | N/A | 4.22 | 4.15 | 4.11 | 4.06 | 3.92 | 3.84 | 3.75 | 3.67 | 3.6 | 3.52 | 3.44 | 3.37 | 3.3 | 3.23 | 3.15 | 2.62 | 1.99 | 1.22
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | Steady Progression | Headroom (MW) | N/A | 4.22 | 4.17 | 4.14 | 4.11 | 4.07 | 4.04 | 4.01 | 3.98 | 3.95 | 3.92 | 3.89 | 3.86 | 3.84 | 3.82 | 3.8 | 3.73 | 3.62 | 3.44
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | System Transformation | Headroom (MW) | N/A | 4.22 | 4.16 | 4.13 | 4.09 | 4.02 | 3.98 | 3.92 | 3.87 | 3.82 | 3.78 | 3.73 | 3.69 | 3.66 | 3.63 | 3.59 | 3.43 | 3.13 | 2.82
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | PRIESTWESTON 33 11kV S STN | Primary | 11 | -3.0467 | 52.5762 | WPD Best View | Headroom (MW) | N/A | 4.22 | 4.16 | 4.12 | 4.08 | 3.99 | 3.92 | 3.86 | 3.8 | 3.74 | 3.69 | 3.63 | 3.58 | 3.54 | 3.49 | 3.44 | 3.15 | 2.73 | 2.25
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Consumer Transformation | Headroom (MW) | N/A | 13.86 | 13.92 | 14 | 14.07 | 13.97 | 13.88 | 13.64 | 13.39 | 13.17 | 12.98 | 12.77 | 12.57 | 12.37 | 12.12 | 11.86 | 10.1 | 7.9 | 5.5
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Leading the Way | Headroom (MW) | N/A | 13.86 | 13.94 | 14.03 | 14.12 | 13.97 | 13.88 | 13.61 | 13.35 | 13.13 | 12.94 | 12.72 | 12.51 | 12.27 | 11.98 | 11.67 | 9.73 | 7.33 | 4.29
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | Steady Progression | Headroom (MW) | N/A | 12.4462 | 12.4437 | 12.4418 | 12.4397 | 12.4362 | 12.4241 | 12.4098 | 12.3933 | 12.3768 | 12.3556 | 12.3348 | 12.3145 | 12.2943 | 12.2747 | 12.2554 | 12.1567 | 12.0512 | 11.9475
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | System Transformation | Headroom (MW) | N/A | 13.86 | 13.93 | 14.02 | 14.1 | 14.04 | 14.01 | 13.96 | 13.91 | 13.86 | 13.81 | 13.73 | 13.63 | 13.54 | 13.46 | 13.39 | 12.78 | 11.74 | 10.69
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROUSHILL 33 11kV S STN | Primary | 11 | -2.7534 | 52.7096 | WPD Best View | Headroom (MW) | N/A | 13.86 | 13.93 | 14.02 | 14.1 | 14.04 | 14.01 | 13.96 | 13.91 | 13.86 | 13.81 | 13.73 | 13.63 | 13.54 | 13.46 | 13.39 | 12.78 | 11.74 | 10.69
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Consumer Transformation | Headroom (MW) | Thermal | 0.42 | 0.38 | 0.36 | 0.33 | 0.24 | 0.19 | 0.13 | 0.07 | 0.02 | -0.03 | -0.07 | -0.12 | -0.16 | -0.2 | -0.25 | -1.07 | -1.55 | -1.99
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Leading the Way | Headroom (MW) | Thermal | 0.42 | 0.38 | 0.35 | 0.32 | 0.21 | 0.15 | 0.09 | 0.04 | -0.02 | -0.07 | -0.11 | -0.16 | -0.2 | -0.25 | -0.3 | -1.14 | -1.68 | -2.26
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | Steady Progression | Headroom (MW) | Thermal | 0.42 | 0.39 | 0.38 | 0.37 | 0.35 | -0.7 | -0.71 | -0.73 | -0.75 | -0.77 | -0.78 | -0.79 | -0.8 | -0.81 | -0.82 | -0.83 | -0.87 | -0.97
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | System Transformation | Headroom (MW) | Thermal | 0.42 | 0.39 | 0.37 | 0.35 | 0.31 | 0.28 | -0.78 | -0.82 | -0.85 | -0.88 | -0.9 | -0.92 | -0.94 | -0.96 | -0.98 | -1.29 | -1.52 | -1.72
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | ROWTON 33 11kV S STN | Primary | 11 | -2.9411 | 52.7012 | WPD Best View | Headroom (MW) | Thermal | 0.42 | 0.39 | 0.37 | 0.35 | 0.31 | 0.28 | -0.78 | -0.82 | -0.85 | -0.88 | -0.9 | -0.92 | -0.94 | -0.96 | -0.98 | -1.29 | -1.52 | -1.72
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Consumer Transformation | Headroom (MW) | Thermal | 27.42 | 27.07 | 26.79 | 26.3 | 25.5 | 24.9 | 24.1 | 22.83 | 21.62 | 20.42 | 18.99 | 17.52 | 15.96 | 14.4 | 12.62 | 5.71 | -3.37 | -13.55
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Leading the Way | Headroom (MW) | Thermal | 27.42 | 27.04 | 26.76 | 26.27 | 25.33 | 24.71 | 23.86 | 23.12 | 22.46 | 21.78 | 21.09 | 20.43 | 19.09 | 17.71 | 16.22 | 9.11 | -0.66 | -10.5
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | Steady Progression | Headroom (MW) | N/A | 27.42 | 27.2 | 27.15 | 27.08 | 26.99 | 26.88 | 26.76 | 26.56 | 26.34 | 25.91 | 25.62 | 25.31 | 24.72 | 24.2 | 23.55 | 22.82 | 21.19 | 18.86
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | System Transformation | Headroom (MW) | N/A | 27.42 | 27.14 | 27.03 | 26.82 | 26.49 | 26.22 | 25.91 | 25.31 | 24.45 | 23.65 | 22.61 | 21.51 | 20.42 | 19.49 | 18.4 | 15.88 | 11.09 | 5.76
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | SPRING GARDENS 33 11kV S STN | Primary | 11 | -2.7391 | 52.7202 | WPD Best View | Headroom (MW) | N/A | 27.42 | 27.14 | 27.03 | 26.82 | 26.49 | 26.22 | 25.91 | 25.31 | 24.45 | 23.65 | 22.61 | 21.51 | 20.42 | 19.49 | 18.4 | 15.88 | 11.09 | 5.76
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Consumer Transformation | Headroom (MW) | Thermal | 3.77 | 3.74 | 3.72 | 3.66 | 3.53 | 3.39 | 3.28 | 3.16 | 3.06 | 2.98 | 2.88 | 2.78 | 2.69 | 2.59 | 2.48 | 1.63 | 0.33 | -1.15
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Leading the Way | Headroom (MW) | Thermal | 3.77 | 3.74 | 3.72 | 3.65 | 3.51 | 3.39 | 3.28 | 3.18 | 3.1 | 3.02 | 2.93 | 2.84 | 2.75 | 2.65 | 2.51 | 1.48 | 0.01 | -1.95
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | Steady Progression | Headroom (MW) | N/A | 3.77 | 3.75 | 3.74 | 3.74 | 3.76 | 3.78 | 3.78 | 3.79 | 3.8 | 3.8 | 3.81 | 3.82 | 3.84 | 3.86 | 3.87 | 3.87 | 3.74 | 3.46
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | System Transformation | Headroom (MW) | N/A | 3.77 | 3.75 | 3.74 | 3.73 | 3.74 | 3.71 | 3.66 | 3.61 | 3.58 | 3.55 | 3.53 | 3.51 | 3.5 | 3.5 | 3.47 | 3.28 | 2.65 | 2.04
Ironbridge & Shrewsbury 132kV | Shrewsbury 132 33 | WEIR HILL 33 11kV S STN | Primary | 11 | -2.7188 | 52.7046 | WPD Best View | Headroom (MW) | N/A | 3.77 | 3.75 | 3.74 | 3.73 | 3.74 | 3.71 | 3.66 | 3.61 | 3.58 | 3.55 | 3.53 | 3.51 | 3.5 | 3.5 | 3.47 | 3.28 | 2.65 | 2.04
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Consumer Transformation | Headroom (MW) | N/A | 27.08 | 26.88 | 26.75 | 26.6 | 26.37 | 25.98 | 25.36 | 24.77 | 24.22 | 23.74 | 23.25 | 22.77 | 22.22 | 21.63 | 20.99 | 16.39 | 9.94 | 2.74
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Leading the Way | Headroom (MW) | Thermal | 27.08 | 26.87 | 26.72 | 26.56 | 26.28 | 25.84 | 25.19 | 24.59 | 24.03 | 23.53 | 22.97 | 22.43 | 21.78 | 21.04 | 20.21 | 14.89 | 7.75 | -1.6
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | Steady Progression | Headroom (MW) | N/A | 27.08 | 26.92 | 26.84 | 26.76 | 26.66 | 26.56 | 26.46 | 26.36 | 26.26 | 26.17 | 26.06 | 25.96 | 25.85 | 25.75 | 25.65 | 25.15 | 24.53 | 23.76
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | System Transformation | Headroom (MW) | N/A | 27.08 | 26.9 | 26.8 | 26.69 | 26.54 | 26.44 | 26.34 | 26.16 | 25.93 | 25.78 | 25.54 | 25.34 | 25.16 | 25.02 | 24.89 | 23.15 | 20.08 | 17.07
Kitwell 132kV | Bartley Green 132 11 (GT1) | BARTLEY GREEN 132 11kV SUBSTN | Primary | 11 | -1.9864 | 52.4412 | WPD Best View | Headroom (MW) | Thermal | 27.08 | 26.87 | 26.72 | 26.56 | 26.28 | 25.84 | 25.2 | 24.6 | 24.04 | 23.55 | 22.99 | 22.45 | 21.8 | 21.07 | 20.24 | 14.93 | 7.81 | -1.52
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Consumer Transformation | Headroom (MW) | N/A | 50.2172 | 50.0164 | 49.762 | 49.4265 | 48.5963 | 47.7787 | 46.9481 | 46.1054 | 45.2536 | 44.4539 | 43.5959 | 42.7295 | 41.8506 | 40.9627 | 40.0741 | 35.5362 | 30.7511 | 25.9006
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Leading the Way | Headroom (MW) | N/A | 62.4 | 62.1462 | 61.825 | 61.4011 | 60.3644 | 59.3346 | 58.2904 | 57.2231 | 56.1397 | 55.1469 | 54.0695 | 52.9748 | 51.8594 | 50.723 | 49.5833 | 43.696 | 37.5547 | 31.3324
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | Steady Progression | Headroom (MW) | N/A | 31.8303 | 31.8109 | 31.7924 | 31.7739 | 31.7514 | 31.6858 | 31.6083 | 31.5172 | 31.4258 | 31.3214 | 31.2176 | 31.1163 | 31.0154 | 30.9146 | 30.8155 | 30.3099 | 29.7761 | 29.241
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | System Transformation | Headroom (MW) | N/A | 42.1568 | 42.0775 | 41.98 | 41.8646 | 41.6361 | 41.3562 | 41.0163 | 40.6702 | 40.3188 | 39.9954 | 39.6451 | 39.2912 | 38.9298 | 38.563 | 38.1915 | 36.3104 | 34.3569 | 32.3918
Kitwell 132kV | Bournville 132 11 (GT1) | Bournville 132/11kV | Primary | 11 | -1.9259 | 52.4279 | WPD Best View | Headroom (MW) | N/A | 43.4889 | 43.3132 | 43.0906 | 42.797 | 42.0787 | 41.3646 | 40.6415 | 39.9023 | 39.1535 | 38.4678 | 37.7238 | 36.9694 | 36.2006 | 35.4161 | 34.6261 | 30.5434 | 26.2838 | 21.9683
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Consumer Transformation | Headroom (MW) | N/A | 50.1021 | 49.911 | 49.6678 | 49.3343 | 48.4889 | 47.656 | 46.8094 | 45.9549 | 45.0934 | 44.243 | 43.353 | 42.4547 | 41.5383 | 40.6114 | 39.6839 | 34.9438 | 30.0906 | 23.09
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Leading the Way | Headroom (MW) | N/A | 52.49 | 52.09 | 51.85 | 51.59 | 51.03 | 50.75 | 50.48 | 50.18 | 49.87 | 49.56 | 48.86 | 48.2 | 47.49 | 46.5 | 45.42 | 38.58 | 29.58 | 17.3
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | Steady Progression | Headroom (MW) | N/A | 29.1112 | 29.1006 | 29.0906 | 29.0788 | 29.0635 | 29.0172 | 28.9621 | 28.8973 | 28.8326 | 28.7557 | 28.6791 | 28.6035 | 28.5278 | 28.4516 | 28.3766 | 27.999 | 27.6214 | 27.2444
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | System Transformation | Headroom (MW) | N/A | 41.5997 | 41.545 | 41.477 | 41.3907 | 41.2141 | 40.9979 | 40.7346 | 40.4672 | 40.1972 | 39.8784 | 39.5141 | 39.1457 | 38.7673 | 38.383 | 37.9934 | 36.0172 | 34.0527 | 32.0847
Kitwell 132kV | Chad Valley 132 11 (GT1A) | Chad Valley 132/11kVDUMMY | Primary | 11 | -1.953 | 52.4738 | WPD Best View | Headroom (MW) | N/A | 43.3733 | 43.2605 | 43.0981 | 42.8808 | 42.3671 | 41.836 | 41.2695 | 40.6901 | 40.1053 | 39.5385 | 38.9398 | 38.3316 | 37.7088 | 37.0741 | 36.4405 | 33.1875 | 29.9497 | 26.6835
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Consumer Transformation | Headroom (MW) | N/A | 49.95 | 49.43 | 48.98 | 48.53 | 47.23 | 46.26 | 45.36 | 44.34 | 43.35 | 42.41 | 41.47 | 40.48 | 39.35 | 38.22 | 36.97 | 30.22 | 21.64 | 12.02
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Leading the Way | Headroom (MW) | N/A | 49.95 | 49.36 | 48.9 | 48.42 | 46.87 | 45.86 | 44.93 | 44.08 | 43.31 | 42.63 | 41.96 | 41.19 | 40.07 | 38.9 | 37.63 | 30.27 | 20.64 | 9.05
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | Steady Progression | Headroom (MW) | N/A | 37.6919 | 37.6816 | 37.6723 | 37.6602 | 37.6449 | 37.5982 | 37.545 | 37.4672 | 37.3903 | 37.2953 | 37.1926 | 37.0852 | 36.9262 | 36.7702 | 36.5872 | 36.0969 | 35.5132 | 34.8112
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | System Transformation | Headroom (MW) | N/A | 49.95 | 49.53 | 49.28 | 48.95 | 48.36 | 47.96 | 47.49 | 46.86 | 46.22 | 45.58 | 44.92 | 44.26 | 43.63 | 43.11 | 42.53 | 40.33 | 36 | 31.41
Kitwell 132kV | Halesowen 132 11 (GT1) | Halesowen 132/11kVDUMMY | Primary | 11 | -2.0461 | 52.4538 | WPD Best View | Headroom (MW) | N/A | 49.95 | 49.46 | 49.12 | 48.66 | 47.58 | 46.78 | 46.02 | 45.13 | 44.25 | 43.41 | 42.56 | 41.71 | 40.76 | 39.79 | 38.71 | 33.37 | 26 | 17.82
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Consumer Transformation | Headroom (MW) | N/A | 51.16 | 50.81 | 50.59 | 50.35 | 49.96 | 49.74 | 49.49 | 48.83 | 48.07 | 47.42 | 46.75 | 46.12 | 45.41 | 44.58 | 43.66 | 37.34 | 28.68 | 19.01
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Leading the Way | Headroom (MW) | N/A | 51.16 | 50.79 | 50.55 | 50.28 | 49.78 | 49.53 | 49.26 | 48.63 | 47.89 | 47.24 | 46.5 | 45.79 | 45 | 43.96 | 42.85 | 35.63 | 26 | 13.21
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | Steady Progression | Headroom (MW) | N/A | 51.16 | 50.88 | 50.74 | 50.6 | 50.45 | 50.32 | 50.2 | 50.08 | 49.96 | 49.83 | 49.7 | 49.57 | 49.43 | 49.3 | 49.16 | 48.55 | 47.68 | 46.6
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | System Transformation | Headroom (MW) | N/A | 51.16 | 50.85 | 50.67 | 50.49 | 50.24 | 50.1 | 49.94 | 49.79 | 49.64 | 49.48 | 49.3 | 49.13 | 48.95 | 48.78 | 48.6 | 46.91 | 42.99 | 39.25
Kitwell 132kV | Hall Green 132 11 (GT1A) | Hall Green 132/11kV | Primary | 11 | -1.8424 | 52.4407 | WPD Best View | Headroom (MW) | N/A | 51.16 | 50.79 | 50.55 | 50.29 | 49.8 | 49.56 | 49.29 | 48.66 | 47.91 | 47.26 | 46.53 | 45.82 | 45.05 | 44.03 | 42.93 | 35.83 | 26.3 | 13.88
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Consumer Transformation | Headroom (MW) | N/A | 46.15 | 45.93 | 45.78 | 45.61 | 45.3 | 44.86 | 44.25 | 43.69 | 43.15 | 42.68 | 42.14 | 41.61 | 41.04 | 40.39 | 39.72 | 34.85 | 27.95 | 20.04
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Leading the Way | Headroom (MW) | N/A | 46.15 | 45.9 | 45.74 | 45.54 | 45.16 | 44.69 | 44.08 | 43.57 | 43.05 | 42.58 | 41.98 | 41.39 | 40.69 | 39.92 | 39.06 | 33.33 | 25.6 | 14.98
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | Steady Progression | Headroom (MW) | N/A | 35.2974 | 35.2877 | 35.2799 | 35.2721 | 35.264 | 35.2317 | 35.1931 | 35.1464 | 35.1 | 35.044 | 34.9861 | 34.9316 | 34.8774 | 34.8236 | 34.7704 | 34.489 | 34.1683 | 33.7411
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | System Transformation | Headroom (MW) | N/A | 46.15 | 45.95 | 45.84 | 45.72 | 45.54 | 45.43 | 45.36 | 45.28 | 45.17 | 45.05 | 44.85 | 44.68 | 44.55 | 44.4 | 44.08 | 42.34 | 39.23 | 36.39
Kitwell 132kV | Highters Heath 132 11 (GT1A) | Highters Heath 132/11kV | Primary | 11 | -1.8697 | 52.4043 | WPD Best View | Headroom (MW) | N/A | 46.15 | 45.92 | 45.77 | 45.6 | 45.29 | 45.07 | 44.52 | 44.04 | 43.57 | 43.16 | 42.72 | 42.22 | 41.66 | 41.04 | 40.32 | 35.73 | 29.18 | 20.63
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Consumer Transformation | Headroom (MW) | N/A | 48.0198 | 47.7946 | 47.5153 | 47.1457 | 46.2711 | 45.391 | 44.4923 | 43.3341 | 42.1189 | 40.878 | 39.4475 | 37.9314 | 36.3626 | 34.8542 | 33.2131 | 27.2217 | 19.98 | 7.88
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Leading the Way | Headroom (MW) | N/A | 51.11 | 50.87 | 50.77 | 50.64 | 50.1 | 49.81 | 49.21 | 48.29 | 47.44 | 46.7 | 45.9 | 45.06 | 43.62 | 42.12 | 40.47 | 31.36 | 19.2 | 4.95
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | Steady Progression | Headroom (MW) | N/A | 28.1704 | 28.1548 | 28.1424 | 28.1299 | 28.1153 | 28.068 | 28.011 | 27.9158 | 27.8218 | 27.7078 | 27.5802 | 27.442 | 27.216 | 26.9947 | 26.7251 | 26.0876 | 25.4268 | 24.7619
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | System Transformation | Headroom (MW) | N/A | 40.2554 | 40.1873 | 40.1081 | 39.9948 | 39.7587 | 39.4614 | 39.0952 | 38.5152 | 37.8745 | 37.2128 | 36.4262 | 35.5719 | 34.6761 | 33.834 | 32.8774 | 30.0257 | 26.8701 | 23.4578
Kitwell 132kV | Longbridge 132 11 (GT1) | Longbridge 132/11kVDUMMY | Primary | 11 | -1.974 | 52.3967 | WPD Best View | Headroom (MW) | N/A | 41.586 | 41.4012 | 41.1732 | 40.8729 | 40.1805 | 39.467 | 38.7337 | 37.7719 | 36.7457 | 35.7243 | 34.529 | 33.2565 | 31.9341 | 30.652 | 29.2476 | 24.1179 | 18.5134 | 4.71
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Consumer Transformation | Headroom (MW) | N/A | 25.62 | 25.49 | 25.43 | 25.36 | 25.15 | 24.83 | 24.41 | 23.85 | 23.3 | 22.76 | 22.17 | 21.54 | 20.83 | 20.13 | 19.32 | 15.7 | 10.88 | 5.42
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Leading the Way | Headroom (MW) | N/A | 25.62 | 25.48 | 25.42 | 25.35 | 25.06 | 24.72 | 24.28 | 23.86 | 23.49 | 23.18 | 22.82 | 22.48 | 21.87 | 21.23 | 20.47 | 16.3 | 10.79 | 4.54
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | Steady Progression | Headroom (MW) | N/A | 25.62 | 25.52 | 25.49 | 25.47 | 25.38 | 25.32 | 25.26 | 25.19 | 25.13 | 25.05 | 24.98 | 24.9 | 24.81 | 24.72 | 24.57 | 24.24 | 23.37 | 22.1
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | System Transformation | Headroom (MW) | N/A | 25.62 | 25.51 | 25.47 | 25.43 | 25.29 | 25.21 | 25.13 | 24.97 | 24.57 | 24.16 | 23.71 | 23.24 | 22.78 | 22.39 | 21.93 | 20.7 | 18.1 | 15.18
Kitwell 132kV | Rednal 132 11 (GT2) | Rednal 132/11kV | Primary | 11 | -1.9816 | 52.397 | WPD Best View | Headroom (MW) | N/A | 25.62 | 25.51 | 25.48 | 25.44 | 25.27 | 25.18 | 25.07 | 24.75 | 24.32 | 23.9 | 23.42 | 22.91 | 22.4 | 21.94 | 21.37 | 19.38 | 16.07 | 12.2
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Consumer Transformation | Headroom (MW) | N/A | 14.15 | 13.99 | 13.93 | 13.85 | 13.67 | 13.55 | 13.25 | 12.94 | 12.65 | 12.39 | 12.1 | 11.82 | 11.54 | 11.23 | 10.91 | 12.37 | 8.71 | 4.63
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Leading the Way | Headroom (MW) | N/A | 14.15 | 13.99 | 13.93 | 13.85 | 13.61 | 13.49 | 13.18 | 12.88 | 12.61 | 12.35 | 12.02 | 11.71 | 11.39 | 15.12 | 14.7 | 11.67 | 7.61 | 2.24
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | Steady Progression | Headroom (MW) | N/A | 14.1086 | 14.01 | 13.97 | 13.93 | 13.85 | 13.78 | 13.71 | 13.63 | 13.55 | 13.46 | 13.38 | 13.29 | 13.2 | 13.11 | 13.01 | 12.58 | 16.15 | 15.54
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | System Transformation | Headroom (MW) | N/A | 14.15 | 14 | 13.96 | 13.91 | 13.79 | 13.71 | 13.61 | 13.52 | 13.43 | 13.33 | 13.23 | 13.12 | 13.01 | 12.9 | 12.79 | 16.23 | 14.46 | 12.71
Kitwell 132kV | Selly Oak 132 11 (GT1) | Selly Oak 132/11kV | Primary | 11 | -1.9367 | 52.4442 | WPD Best View | Headroom (MW) | N/A | 14.15 | 13.99 | 13.93 | 13.85 | 13.61 | 13.49 | 13.18 | 12.88 | 12.61 | 12.35 | 12.02 | 11.71 | 11.39 | 15.12 | 14.7 | 11.67 | 7.61 | 2.24
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Consumer Transformation | Headroom (MW) | N/A | 37.67 | 37.44 | 37.3 | 37.15 | 36.85 | 36.69 | 36.51 | 35.96 | 35.42 | 34.94 | 34.49 | 34.06 | 33.52 | 32.89 | 32.21 | 27.42 | 20.75 | 13.08
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Leading the Way | Headroom (MW) | N/A | 37.67 | 37.42 | 37.27 | 37.09 | 36.7 | 36.53 | 36.32 | 35.81 | 35.29 | 34.82 | 34.31 | 33.82 | 33.17 | 32.37 | 31.51 | 25.98 | 18.45 | 8.15
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | Steady Progression | Headroom (MW) | N/A | 37.67 | 37.49 | 37.41 | 37.33 | 37.23 | 37.15 | 37.07 | 36.99 | 36.91 | 36.83 | 36.74 | 36.64 | 36.55 | 36.46 | 36.37 | 35.94 | 35.3 | 34.49
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | System Transformation | Headroom (MW) | N/A | 37.67 | 37.47 | 37.36 | 37.25 | 37.08 | 36.98 | 36.87 | 36.77 | 36.66 | 36.55 | 36.42 | 36.29 | 36.17 | 36.04 | 35.92 | 34.69 | 31.8 | 29.06
Lea Marston 132kV | Boughton Road 132 11 (GT1A) | Boughton Road | Primary | 11 | -1.8207 | 52.4643 | WPD Best View | Headroom (MW) | N/A | 37.67 | 37.42 | 37.27 | 37.11 | 36.73 | 36.56 | 36.36 | 35.85 | 35.32 | 34.85 | 34.35 | 33.88 | 33.25 | 32.49 | 31.67 | 26.32 | 18.96 | 9.25
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Consumer Transformation | Headroom (MW) | N/A | 25.26 | 25.11 | 25.02 | 24.93 | 24.68 | 24.42 | 24.19 | 24.05 | 23.87 | 23.71 | 23.57 | 23.45 | 23.31 | 23.15 | 22.92 | 21.17 | 18.62 | 15.71
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Leading the Way | Headroom (MW) | N/A | 25.26 | 25.1 | 25.01 | 24.91 | 24.62 | 24.36 | 24.12 | 24.04 | 23.86 | 23.7 | 23.54 | 23.39 | 23.22 | 23.01 | 22.72 | 20.66 | 17.79 | 13.94
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | Steady Progression | Headroom (MW) | N/A | 25.26 | 25.13 | 25.06 | 24.99 | 24.92 | 24.86 | 24.8 | 24.78 | 24.72 | 24.67 | 24.62 | 24.57 | 24.51 | 24.46 | 24.41 | 24.15 | 23.81 | 23.41
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | System Transformation | Headroom (MW) | N/A | 25.26 | 25.12 | 25.04 | 24.97 | 24.87 | 24.8 | 24.65 | 24.6 | 24.49 | 24.4 | 24.32 | 24.27 | 24.23 | 24.2 | 24.19 | 23.66 | 22.42 | 21.22
Lea Marston 132kV | Chelmsley Wood 132 11 (GT1) | CHELMSLEY WOOD | Primary | 11 | -1.7366 | 52.4796 | WPD Best View | Headroom (MW) | N/A | 25.26 | 25.11 | 25.02 | 24.93 | 24.68 | 24.42 | 24.19 | 24.05 | 23.87 | 23.71 | 23.57 | 23.45 | 23.31 | 23.15 | 22.92 | 21.17 | 18.62 | 15.71
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Consumer Transformation | Headroom (MW) | N/A | 45.69 | 45.5 | 45.38 | 45.25 | 45.01 | 44.57 | 44.16 | 43.43 | 42.63 | 41.76 | 40.6 | 39.36 | 38.04 | 36.82 | 35.38 | 31.01 | 25.67 | 19.49
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Leading the Way | Headroom (MW) | N/A | 45.69 | 45.48 | 45.35 | 45.21 | 44.91 | 44.46 | 44.03 | 43.61 | 43.19 | 42.78 | 42.3 | 41.86 | 40.82 | 39.73 | 38.58 | 33.79 | 27.52 | 21.97
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | Steady Progression | Headroom (MW) | N/A | 45.69 | 45.53 | 45.45 | 45.37 | 45.28 | 45.2 | 45.12 | 45.05 | 44.98 | 44.91 | 44.79 | 44.51 | 43.97 | 43.45 | 42.78 | 41.93 | 40.5 | 38.64
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | System Transformation | Headroom (MW) | N/A | 45.69 | 45.51 | 45.41 | 45.31 | 45.17 | 45.08 | 44.98 | 44.51 | 43.87 | 43.17 | 42.22 | 41.15 | 40.07 | 39.12 | 38 | 35.72 | 32.2 | 28.24
Lea Marston 132kV | Copt Heath 132 11 (GT1A) | Copt Heath 132/11kV | Primary | 11 | -1.749 | 52.4067 | WPD Best View | Headroom (MW) | N/A | 45.69 | 45.5 | 45.38 | 45.25 | 45.01 | 44.57 | 44.16 | 43.43 | 42.63 | 41.76 | 40.6 | 39.36 | 38.04 | 36.82 | 35.38 | 31.01 | 25.67 | 19.49
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Consumer Transformation | Headroom (MW) | N/A | 64.49 | 64.1 | 63.92 | 60.25 | 59.95 | 59.77 | 59.57 | 59.38 | 59.17 | 58.49 | 57.7 | 56.85 | 56 | 55.2 | 54.28 | 51.24 | 57.64 | 54.4
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Leading the Way | Headroom (MW) | N/A | 64.49 | 64.09 | 63.9 | 60.22 | 59.85 | 59.65 | 59.48 | 59.31 | 59.18 | 58.91 | 58.41 | 57.93 | 57.16 | 56.48 | 55.8 | 53.19 | 62.07 | 53.84
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | Steady Progression | Headroom (MW) | N/A | 56.3056 | 56.2784 | 56.2714 | 52.1792 | 52.1665 | 52.1405 | 52.0346 | 51.9389 | 51.8517 | 51.7528 | 51.6347 | 51.5024 | 51.284 | 51.0717 | 50.8145 | 50.3754 | 50.0261 | 49.6803
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | System Transformation | Headroom (MW) | N/A | 64.49 | 64.11 | 63.94 | 60.28 | 60.04 | 59.87 | 59.69 | 59.52 | 59.4 | 59.25 | 58.71 | 58 | 57.29 | 56.66 | 55.92 | 54.17 | 63.8 | 57.75
Lea Marston 132kV | Elmdon 132 11 (GT1) | Elmdon 132/11kVDUMMY | Primary | 11 | -1.7125 | 52.4519 | WPD Best View | Headroom (MW) | N/A | 64.49 | 64.1 | 63.92 | 60.25 | 59.95 | 59.77 | 59.57 | 59.38 | 59.17 | 58.49 | 57.7 | 56.85 | 56 | 55.2 | 54.28 | 51.24 | 57.64 | 54.4
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Consumer Transformation | Headroom (MW) | N/A | 43.96 | 43.91 | 44.01 | 43.97 | 43.59 | 43.12 | 42.63 | 41.64 | 40.56 | 39.39 | 37.97 | 36.4 | 34.75 | 33.25 | 31.46 | 25.94 | 19.42 | 12.05
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Leading the Way | Headroom (MW) | N/A | 43.96 | 43.92 | 44.05 | 44.04 | 43.55 | 43.02 | 42.46 | 41.88 | 41.34 | 40.88 | 40.43 | 40.01 | 38.72 | 37.56 | 36.58 | 29.86 | 21.59 | 14.18
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | Steady Progression | Headroom (MW) | N/A | 43.96 | 43.93 | 44.07 | 44.11 | 44.05 | 43.96 | 43.84 | 43.58 | 43.32 | 43 | 42.62 | 42.18 | 41.32 | 40.49 | 39.44 | 37.91 | 36.11 | 33.85
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | System Transformation | Headroom (MW) | N/A | 43.96 | 43.94 | 44.08 | 44.1 | 43.94 | 43.8 | 43.61 | 42.78 | 41.74 | 40.81 | 39.57 | 38.19 | 36.75 | 35.47 | 33.95 | 30.82 | 26.08 | 19.36
Lea Marston 132kV | Hams Hall South 132 11 (GT3A1A) | Hams Hall South 132/11kVDUMMY | Primary | 11 | -1.7182 | 52.5249 | WPD Best View | Headroom (MW) | N/A | 43.96 | 43.9 | 44 | 43.97 | 43.58 | 43.11 | 42.62 | 41.63 | 40.55 | 39.39 | 37.97 | 36.39 | 34.74 | 33.24 | 31.45 | 25.93 | 19.4 | 12.01
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Consumer Transformation | Headroom (MW) | N/A | 90.55 | 90.18 | 89.95 | 89.69 | 89.22 | 88.95 | 88.09 | 87.17 | 86.31 | 85.55 | 84.88 | 84.17 | 83.36 | 82.43 | 81.4 | 74.06 | 63.6 | 51.78
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Leading the Way | Headroom (MW) | N/A | 90.55 | 90.15 | 89.9 | 89.61 | 89 | 88.7 | 87.8 | 86.89 | 86.05 | 85.3 | 84.53 | 83.74 | 82.77 | 81.61 | 80.32 | 71.84 | 60.15 | 44.45
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | Steady Progression | Headroom (MW) | N/A | 90.55 | 90.26 | 90.12 | 89.98 | 89.79 | 89.65 | 89.51 | 89.37 | 89.23 | 89.09 | 88.95 | 88.8 | 88.66 | 88.51 | 88.37 | 87.69 | 86.75 | 85.57
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | System Transformation | Headroom (MW) | N/A | 90.55 | 90.22 | 90.04 | 89.85 | 89.55 | 89.38 | 89.2 | 89.02 | 88.84 | 88.65 | 88.46 | 88.26 | 88.06 | 87.87 | 87.67 | 85.13 | 80.41 | 76
Lea Marston 132kV | Kitts Green 132 11 (GT1A) | Kitts Green 132/11kVDUMMY | Primary | 11 | -1.7797 | 52.4838 | WPD Best View | Headroom (MW) | N/A | 90.55 | 90.16 | 89.92 | 89.64 | 89.07 | 88.77 | 87.89 | 86.97 | 86.12 | 85.38 | 84.63 | 83.87 | 82.97 | 81.88 | 80.69 | 72.62 | 61.36 | 47.03
Kitwell 132kV | Shirley 132 11 (GT1) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Consumer Transformation | Headroom (MW) | N/A | 51.53 | 51.12 | 50.71 | 50.22 | 49.06 | 48.21 | 47.35 | 45.94 | 44.44 | 42.94 | 41.05 | 39 | 36.76 | 34.7 | 32.3 | 23.91 | 13.7 | 1.96
Kitwell 132kV | Shirley 132 11 (GT1) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Leading the Way | Headroom (MW) | N/A | 51.53 | 51.07 | 50.64 | 50.12 | 48.8 | 47.96 | 47.1 | 46.19 | 45.33 | 44.61 | 43.76 | 42.8 | 40.79 | 38.9 | 36.89 | 27.82 | 15.92 | 4.43
Kitwell 132kV | Shirley 132 11 (GT1) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | Steady Progression | Headroom (MW) | N/A | 33.6793 | 33.6318 | 33.6036 | 33.582 | 33.5551 | 33.4833 | 33.4005 | 33.2251 | 33.0509 | 32.8329 | 32.557 | 32.2443 | 31.6727 | 31.1164 | 30.4237 | 29.1698 | 27.9402 | 26.7176
Kitwell 132kV | Shirley 132 11 (GT1) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | System Transformation | Headroom (MW) | N/A | 44.6057 | 44.4792 | 44.3619 | 44.24 | 44.0053 | 43.7157 | 43.369 | 42.6148 | 41.73 | 40.7513 | 39.4745 | 38.0755 | 36.6281 | 35.3388 | 33.8246 | 30.4228 | 26.7662 | 21.13
Kitwell 132kV | Shirley 132 11 (GT1) | Shirley 132/11kVDUMMY | Primary | 11 | -1.8062 | 52.3951 | WPD Best View | Headroom (MW) | N/A | 46.0153 | 45.7969 | 45.5622 | 45.28 | 44.6256 | 43.9689 | 43.3009 | 42.3818 | 41.4062 | 40.3427 | 38.9953 | 37.573 | 35.9642 | 34.4806 | 32.788 | 27.9092 | 19.7 | 9.58
Lea Marston 132kV | Solihull 132 11 (GT1) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Consumer Transformation | Headroom (MW) | Thermal | 9.8 | 9.49 | 9.29 | 9.08 | 8.76 | 8.57 | 8.3 | 7.52 | 6.78 | 6.17 | 5.5 | 4.86 | 4.26 | 3.61 | 2.89 | -2.11 | -7.08 | -15.12
Lea Marston 132kV | Solihull 132 11 (GT1) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Leading the Way | Headroom (MW) | Thermal | 9.8 | 9.47 | 9.26 | 9.02 | 8.64 | 8.43 | 8.13 | 7.41 | 6.71 | 6.09 | 5.34 | 4.62 | 3.94 | 3.21 | 3.82 | -3.28 | -10.28 | -19.54
Lea Marston 132kV | Solihull 132 11 (GT1) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | Steady Progression | Headroom (MW) | N/A | 9.8 | 9.54 | 9.41 | 9.27 | 9.13 | 9.02 | 8.9 | 8.7 | 8.51 | 8.32 | 8.14 | 7.97 | 7.82 | 7.69 | 7.57 | 6.99 | 6.23 | 5.72
Lea Marston 132kV | Solihull 132 11 (GT1) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | System Transformation | Headroom (MW) | Thermal | 9.8 | 9.51 | 9.35 | 9.18 | 8.98 | 8.84 | 8.7 | 8.51 | 8.33 | 8.18 | 8.04 | 7.89 | 7.66 | 7.42 | 7.7 | 5.24 | 2.19 | -0.85
Lea Marston 132kV | Solihull 132 11 (GT1) | Solihull 132/11kVDUMMY | Primary | 11 | -1.7801 | 52.4146 | WPD Best View | Headroom (MW) | Thermal | 9.8 | 9.49 | 9.29 | 9.07 | 8.76 | 8.57 | 8.3 | 7.52 | 6.78 | 6.17 | 5.5 | 4.86 | 4.26 | 3.61 | 2.88 | -2.13 | -7.12 | -15.19
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Consumer Transformation | Headroom (MW) | N/A | 48.1 | 47.79 | 47.6 | 47.38 | 46.97 | 46.32 | 45.33 | 44.37 | 43.46 | 42.7 | 41.81 | 40.87 | 39.91 | 38.89 | 37.81 | 31.71 | 21.17 | 11.15
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Leading the Way | Headroom (MW) | N/A | 48.1 | 47.76 | 47.55 | 47.3 | 46.78 | 46.08 | 45.06 | 44.09 | 43.17 | 42.82 | 39.62 | 38.6 | 37.53 | 36.37 | 35.1 | 26.8 | 17.83 | 5.3
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | Steady Progression | Headroom (MW) | N/A | 34.6276 | 34.6155 | 34.6039 | 34.5906 | 34.5694 | 34.5118 | 34.4436 | 34.3633 | 34.2815 | 34.1918 | 34.1006 | 34.0094 | 33.9154 | 33.8189 | 33.7208 | 33.4219 | 32.855 | 32.2623
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | System Transformation | Headroom (MW) | N/A | 46.5356 | 46.4493 | 46.3431 | 46.1034 | 45.8277 | 45.4924 | 45.0779 | 44.6489 | 44.2065 | 44.0904 | 41.3551 | 40.9079 | 40.442 | 39.9627 | 39.4692 | 37.0316 | 35.397 | 32.81
Lea Marston 132kV | Sutton Coldfield 132 11 (GT1A) | Sutton Coldfield 132/11kVDUMMY | Primary | 11 | -1.8136 | 52.5622 | WPD Best View | Headroom (MW) | N/A | 48.0061 | 47.77 | 47.4447 | 47.0945 | 46.2437 | 45.3971 | 44.5294 | 43.6149 | 42.674 | 42.4883 | 38.0148 | 37.0779 | 36.114 | 35.1386 | 34.1622 | 26.99 | 18.08 | 5.63
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Consumer Transformation | Headroom (MW) | N/A | 45.78 | 45.62 | 45.57 | 45.51 | 45.3 | 45.18 | 45.06 | 44.94 | 44.7 | 44.43 | 44.14 | 43.85 | 43.55 | 43.24 | 42.93 | 40.72 | 38.67 | 36.41
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Leading the Way | Headroom (MW) | N/A | 45.78 | 45.6 | 45.55 | 45.49 | 45.14 | 45.02 | 44.88 | 44.74 | 44.45 | 44.12 | 43.79 | 43.46 | 43.12 | 42.79 | 42.45 | 40.42 | 38.24 | 35.69
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | Steady Progression | Headroom (MW) | N/A | 34.1764 | 34.1641 | 34.1522 | 34.1398 | 34.1231 | 34.0971 | 34.0667 | 34.0319 | 33.9958 | 33.9637 | 33.9293 | 33.8941 | 33.8567 | 33.817 | 33.777 | 33.6025 | 33.5198 | 33.4431
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | System Transformation | Headroom (MW) | N/A | 45.2641 | 45.2396 | 45.2116 | 45.1789 | 45.1066 | 45.0185 | 44.9065 | 44.7834 | 44.6481 | 44.549 | 44.4387 | 44.3221 | 44.2048 | 44.0812 | 43.9593 | 43.4553 | 42.51 | 41.2
Nechells 132kV | Bordesley 132 11 (GT1A) | Bordesley 132/11kVDUMMY | Primary | 11 | -1.8794 | 52.4746 | WPD Best View | Headroom (MW) | N/A | 45.78 | 45.6 | 45.55 | 45.49 | 45.14 | 45.02 | 44.88 | 44.74 | 44.45 | 44.12 | 43.79 | 43.46 | 43.12 | 42.79 | 42.45 | 40.42 | 38.24 | 35.69
Lea Marston 132kV | Castle Bromwich 132 11 (GT1A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Consumer Transformation | Headroom (MW) | N/A | 27.07 | 26.87 | 26.79 | 26.71 | 26.46 | 26.34 | 26.08 | 25.94 | 25.81 | 25.68 | 25.54 | 25.41 | 25.27 | 25.12 | 24.99 | 29.21 | 14.35 | 11.42
Lea Marston 132kV | Castle Bromwich 132 11 (GT1A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Leading the Way | Headroom (MW) | N/A | 27.07 | 26.86 | 26.78 | 26.69 | 26.36 | 26.22 | 26.06 | 25.92 | 25.77 | 25.62 | 25.46 | 25.29 | 30.19 | 11.73 | 11.55 | 9.64 | 9.1 | 10.12
Lea Marston 132kV | Castle Bromwich 132 11 (GT1A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | Steady Progression | Headroom (MW) | N/A | 27.07 | 26.89 | 26.83 | 26.76 | 26.64 | 26.55 | 26.24 | 26.14 | 26.05 | 25.95 | 25.85 | 25.75 | 25.65 | 25.55 | 25.45 | 25.01 | 24.66 | 24.15
Lea Marston 132kV | Castle Bromwich 132 11 (GT1A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | System Transformation | Headroom (MW) | N/A | 27.07 | 26.89 | 26.82 | 26.75 | 26.57 | 26.47 | 26.23 | 26.12 | 26.01 | 25.9 | 25.78 | 25.67 | 27.21 | 14.91 | 14.81 | 14.27 | 14.06 | 13.72
Lea Marston 132kV | Castle Bromwich 132 11 (GT1A) | Castle Bromwich 132/11kVDUMMY | Primary | 11 | -1.7816 | 52.5261 | WPD Best View | Headroom (MW) | N/A | 27.07 | 26.86 | 26.78 | 26.69 | 26.36 | 26.22 | 26.06 | 25.91 | 25.77 | 25.62 | 25.46 | 25.29 | 30.18 | 11.72 | 11.55 | 9.64 | 9.1 | 10.12
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Consumer Transformation | Headroom (MW) | N/A | 20.5784 | 20.509 | 20.4221 | 20.3115 | 20.0192 | 19.7123 | 19.381 | 19.0284 | 18.6526 | 18.3259 | 17.9648 | 17.5895 | 17.2137 | 16.8227 | 16.4362 | 14.5928 | 13.2673 | 11.9904
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Leading the Way | Headroom (MW) | N/A | 28.1631 | 28.0596 | 27.9291 | 27.7631 | 27.3584 | 26.9229 | 26.4588 | 25.9452 | 25.3962 | 24.9267 | 24.4232 | 23.8988 | 23.3714 | 22.854 | 22.3559 | 19.8763 | 18.0608 | 16.2785
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | Steady Progression | Headroom (MW) | N/A | 11.3523 | 11.3364 | 11.3212 | 11.3053 | 11.2875 | 11.2577 | 11.2231 | 11.1836 | 11.1434 | 11.103 | 11.0588 | 11.013 | 10.9635 | 10.91 | 10.8558 | 10.6152 | 10.4972 | 10.3855
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | System Transformation | Headroom (MW) | N/A | 16.2224 | 16.185 | 16.1419 | 16.0911 | 15.9991 | 15.8852 | 15.7446 | 15.593 | 15.4293 | 15.2896 | 15.133 | 14.9671 | 14.799 | 14.621 | 14.4427 | 13.6264 | 13.1309 | 12.6638
Nechells 132kV | Cheapside 132 11 (GT1A) | Cheapside 132/11kVDUMMY | Primary | 11 | -1.8877 | 52.4727 | WPD Best View | Headroom (MW) | N/A | 16.914 | 16.8519 | 16.7735 | 16.6738 | 16.4307 | 16.1692 | 15.8904 | 15.582 | 15.2523 | 14.9703 | 14.6679 | 14.353 | 14.0363 | 13.7255 | 13.4264 | 11.9372 | 10.8468 | 9.7764
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Consumer Transformation | Headroom (MW) | N/A | 48.62 | 42.26 | 42.17 | 42.09 | 41.78 | 41.56 | 41.26 | 40.86 | 40.52 | 40.22 | 40 | 39.78 | 39.55 | 39.31 | 39.63 | 37.53 | 36.56 | 26.66
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Leading the Way | Headroom (MW) | N/A | 48.62 | 42.23 | 42.15 | 42.06 | 41.63 | 41.36 | 41.09 | 40.71 | 40.4 | 40.15 | 39.9 | 39.66 | 39.39 | 39.11 | 39.38 | 41.05 | 28.17 | 23.55
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | Steady Progression | Headroom (MW) | N/A | 41.1409 | 33.932 | 33.9298 | 33.9276 | 33.9196 | 33.8998 | 33.7463 | 33.7186 | 33.7068 | 33.6928 | 33.6773 | 33.6626 | 33.6487 | 33.6339 | 33.6222 | 33.5488 | 33.502 | 33.3505
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | System Transformation | Headroom (MW) | N/A | 48.62 | 42.27 | 42.2 | 42.12 | 41.89 | 41.78 | 41.6 | 41.42 | 41.2 | 41.11 | 41 | 40.88 | 40.77 | 40.66 | 40.74 | 42.6 | 35.48 | 33.5
Nechells 132kV | Chester Street 132 11 (GT1) | Chester Street 132/11kVDUMMY | Primary | 11 | -1.8813 | 52.4963 | WPD Best View | Headroom (MW) | N/A | 48.62 | 42.23 | 42.15 | 42.06 | 41.63 | 41.36 | 41.09 | 40.71 | 40.4 | 40.15 | 39.9 | 39.66 | 39.39 | 39.11 | 39.38 | 41.05 | 28.17 | 23.55
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Consumer Transformation | Headroom (MW) | N/A | 49.19 | 48.91 | 48.76 | 48.59 | 48.28 | 48.12 | 47.96 | 47.89 | 47.84 | 47.67 | 47.51 | 47.24 | 46.86 | 46.45 | 46 | 42.32 | 36.97 | 31.06
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Leading the Way | Headroom (MW) | N/A | 49.19 | 48.89 | 48.72 | 48.54 | 48.13 | 47.96 | 47.78 | 47.75 | 47.73 | 47.54 | 47.33 | 47.11 | 46.71 | 46.2 | 45.62 | 41.37 | 35.45 | 27.76
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | Steady Progression | Headroom (MW) | N/A | 37.4437 | 37.4349 | 37.4266 | 37.4182 | 37.4081 | 37.3733 | 37.3323 | 37.2835 | 37.2348 | 37.1771 | 37.1173 | 37.0596 | 37.0024 | 36.9451 | 36.8892 | 36.5972 | 36.2761 | 35.9542
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | System Transformation | Headroom (MW) | N/A | 49.19 | 48.93 | 48.8 | 48.67 | 48.46 | 48.35 | 48.23 | 48.2 | 48.19 | 48.09 | 47.98 | 47.88 | 47.7631 | 47.5463 | 47.3264 | 46.1826 | 44.9501 | 42.95
Nechells 132kV | Erdington 132 11 (GT1A) | ERDINGTON 11kV S STN | Primary | 11 | -1.8275 | 52.5131 | WPD Best View | Headroom (MW) | N/A | 49.19 | 48.89 | 48.72 | 48.54 | 48.13 | 47.96 | 47.78 | 47.75 | 47.73 | 47.54 | 47.33 | 47.11 | 46.71 | 46.2 | 45.62 | 41.37 | 35.45 | 27.76
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Consumer Transformation | Headroom (MW) | N/A | 52.34 | 52.08 | 52.01 | 51.94 | 51.56 | 51.45 | 51.32 | 51.2 | 51.08 | 50.92 | 50.77 | 50.6 | 50.41 | 50.15 | 49.87 | 47.33 | 44.62 | 41.72
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Leading the Way | Headroom (MW) | N/A | 52.34 | 52.05 | 51.99 | 51.93 | 51.35 | 51.23 | 51.09 | 50.96 | 50.83 | 50.64 | 50.46 | 50.27 | 50.08 | 49.88 | 49.56 | 47.11 | 44.06 | 40.35
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | Steady Progression | Headroom (MW) | N/A | 52.34 | 52.11 | 52.05 | 51.97 | 51.81 | 51.73 | 51.63 | 51.53 | 51.43 | 51.31 | 51.2 | 51.08 | 50.96 | 50.84 | 50.72 | 50.09 | 49.39 | 48.67
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | System Transformation | Headroom (MW) | N/A | 52.34 | 52.1 | 52.04 | 51.98 | 51.72 | 51.62 | 51.52 | 51.41 | 51.31 | 51.18 | 51.05 | 50.91 | 50.77 | 50.64 | 50.5 | 49.78 | 48.9 | 48.13
Nechells 132kV | Hockley 132 11 (GT1A) | Hockley 132/11kv | Primary | 11 | -1.901 | 52.489 | WPD Best View | Headroom (MW) | N/A | 52.34 | 52.05 | 51.99 | 51.93 | 51.35 | 51.23 | 51.09 | 50.96 | 50.83 | 50.64 | 50.46 | 50.27 | 50.08 | 49.88 | 49.56 | 47.11 | 44.06 | 40.35
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Consumer Transformation | Headroom (MW) | N/A | 74.52 | 74.09 | 73.89 | 73.67 | 73.02 | 72.18 | 71.55 | 69.83 | 68.25 | 67.02 | 66.07 | 65.33 | 64.84 | 64.31 | 64.83 | 69.44 | 58.39 | 42.13
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Leading the Way | Headroom (MW) | N/A | 74.52 | 74.04 | 73.82 | 73.59 | 72.68 | 71.79 | 71.12 | 70.51 | 69.8 | 69.14 | 68.6 | 69.15 | 54.36 | 53.74 | 66.43 | 49.5 | 42.43 | 32.64
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | Steady Progression | Headroom (MW) | N/A | 74.52 | 66.99 | 66.82 | 66.65 | 66.43 | 66.27 | 66.13 | 64.6 | 63.04 | 61.57 | 60.25 | 59.13 | 58.51 | 58.02 | 57.69 | 56.95 | 56.06 | 54.92
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | System Transformation | Headroom (MW) | N/A | 74.52 | 74.13 | 73.95 | 73.76 | 73.39 | 73.25 | 73.17 | 71.8 | 70.4 | 69.51 | 68.87 | 68.46 | 58.76 | 58.56 | 61.06 | 52.17 | 49.38 | 45.38
Nechells 132kV | Nechells West 132 11 (GT1B1) | Nechells West 132/25/11kVDUMMY | Primary | 11 | -1.8579 | 52.5064 | WPD Best View | Headroom (MW) | N/A | 74.52 | 74.04 | 73.82 | 73.59 | 72.68 | 71.79 | 71.12 | 70.51 | 69.8 | 69.14 | 68.6 | 69.15 | 54.36 | 53.74 | 66.43 | 49.5 | 42.43 | 32.64
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Consumer Transformation | Headroom (MW) | N/A | 50.7528 | 50.6485 | 50.5165 | 50.3414 | 49.6758 | 49.0025 | 48.3348 | 47.6726 | 47.016 | 46.3692 | 45.6493 | 44.9267 | 44.1958 | 43.4621 | 42.7214 | 38.8992 | 34.7713 | 28.99
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Leading the Way | Headroom (MW) | N/A | 54.38 | 53.92 | 53.74 | 53.55 | 52.57 | 52.3 | 52.01 | 51.72 | 51.43 | 51.1 | 50.77 | 50.44 | 49.82 | 49.09 | 48.27 | 42.6 | 35 | 25.26
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | Steady Progression | Headroom (MW) | N/A | 30.1773 | 30.171 | 30.1651 | 30.1592 | 30.1499 | 30.1156 | 30.0752 | 30.0282 | 29.9815 | 29.923 | 29.8635 | 29.805 | 29.7471 | 29.6898 | 29.6335 | 29.3452 | 29.0433 | 28.746
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | System Transformation | Headroom (MW) | N/A | 42.6064 | 42.5662 | 42.5172 | 42.4583 | 42.2839 | 42.0616 | 41.7956 | 41.5326 | 41.2718 | 41.0158 | 40.7288 | 40.4407 | 40.1484 | 39.8545 | 39.5564 | 38.0142 | 36.3781 | 34.7361
Nechells 132kV | Sparkbrook 132 11 (GT1A1) | Sparkbrook 132/11kVDUMMY | Primary | 11 | -1.859 | 52.4611 | WPD Best View | Headroom (MW) | N/A | 43.9528 | 43.8613 | 43.7452 | 43.5917 | 43.0147 | 42.4292 | 41.8474 | 41.2709 | 40.6993 | 40.1391 | 39.5079 | 38.8712 | 38.2256 | 37.5649 | 36.8928 | 33.4419 | 29.7816 | 25.26
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Consumer Transformation | Headroom (MW) | N/A | 55.237 | 55.1856 | 55.1217 | 55.0404 | 54.8813 | 54.7208 | 54.5665 | 54.1537 | 53.7691 | 53.4508 | 53.1844 | 52.9621 | 52.7759 | 52.5841 | 52.4034 | 54.6293 | 49.2277 | 48.5982
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Leading the Way | Headroom (MW) | N/A | 65.4 | 65.21 | 65.14 | 65.07 | 64.97 | 64.95 | 64.91 | 64.87 | 64.84 | 64.79 | 58.239 | 58.0016 | 57.7728 | 57.5371 | 57.2994 | 56.0743 | 58.1807 | 60.2519
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | Steady Progression | Headroom (MW) | N/A | 35.0121 | 34.9949 | 34.9786 | 34.9615 | 34.9527 | 34.9359 | 34.917 | 34.6477 | 34.3881 | 34.1403 | 33.9144 | 33.7237 | 33.6145 | 33.5259 | 33.465 | 33.3281 | 33.2567 | 33.1929
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | System Transformation | Headroom (MW) | N/A | 46.3709 | 46.3377 | 46.3003 | 46.256 | 46.207 | 46.1475 | 46.0822 | 45.8009 | 45.5434 | 45.3445 | 41.2161 | 41.103 | 41.0179 | 40.9286 | 40.8458 | 40.4054 | 40.5027 | 40.5523
Nechells 132kV | Summer Lane 132 11 (GT1A) | Summer Lane 132/11kVDUMMY | Primary | 11 | -1.8988 | 52.4872 | WPD Best View | Headroom (MW) | N/A | 47.8362 | 47.7863 | 47.7237 | 47.6443 | 47.5119 | 47.3789 | 47.2447 | 47.1172 | 46.9878 | 46.9024 | 40.5889 | 40.4235 | 40.264 | 40.0997 | 39.9341 | 39.0803 | 40.5483 | 41.9918
Ocker Hill 132kV | Black Lake 132 11 (GT1B) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Consumer Transformation | Headroom (MW) | N/A | 68.66 | 67.7 | 67.21 | 66.76 | 65.88 | 65.38 | 64.88 | 64.37 | 63.74 | 62.11 | 60.81 | 59.74 | 58.76 | 57.72 | 56.67 | 51.63 | 58.25 | 30.64
Ocker Hill 132kV | Black Lake 132 11 (GT1B) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Leading the Way | Headroom (MW) | N/A | 68.66 | 67.64 | 67.14 | 66.68 | 65.53 | 65 | 64.46 | 63.91 | 63.24 | 62.13 | 61.05 | 60.02 | 58.96 | 57.86 | 77.09 | 39.56 | 30.81 | 19.29
Ocker Hill 132kV | Black Lake 132 11 (GT1B) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | Steady Progression | Headroom (MW) | N/A | 68.66 | 67.78 | 67.34 | 66.94 | 66.42 | 66.01 | 65.59 | 63.67 | 61.78 | 61.38 | 60.24 | 58.84 | 57.95 | 57.21 | 56.63 | 54.71 | 52.71 | 50.66
Ocker Hill 132kV | Black Lake 132 11 (GT1B) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | System Transformation | Headroom (MW) | N/A | 68.66 | 67.74 | 67.28 | 66.86 | 66.19 | 65.75 | 65.3 | 64.85 | 64.4 | 63.39 | 62.65 | 62.11 | 61.68 | 61.26 | 63.81 | 41.28 | 36.71 | 32.15
Ocker Hill 132kV | Black Lake 132 11 (GT1B) | Black Lake 132/11kVDUMMY | Primary | 11 | -2.0062 | 52.5306 | WPD Best View | Headroom (MW) | N/A | 68.66 | 67.74 | 67.28 | 66.86 | 66.19 | 65.75 | 65.3 | 64.85 | 64.4 | 63.39 | 62.65 | 62.11 | 61.68 | 61.26 | 63.81 | 41.28 | 36.71 | 32.15
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Consumer Transformation | Headroom (MW) | N/A | 47.0124 | 46.9144 | 46.7602 | 46.5253 | 45.9742 | 45.4169 | 44.8357 | 44.237 | 43.6633 | 43.0645 | 42.4338 | 41.7934 | 41.1474 | 40.4938 | 39.8726 | 36.8029 | 33.14 | 26.37
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Leading the Way | Headroom (MW) | N/A | 49.19 | 48.72 | 48.51 | 48.52 | 47.68 | 47.42 | 47.2 | 46.93 | 46.63 | 46.28 | 45.66 | 45.05 | 44.42 | 43.76 | 43.03 | 38.16 | 31.58 | 22.96
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | Steady Progression | Headroom (MW) | N/A | 28.1987 | 28.1941 | 28.1832 | 28.167 | 28.1505 | 28.1175 | 28.0789 | 28.031 | 27.9855 | 27.9338 | 27.8781 | 27.8264 | 27.7745 | 27.7222 | 27.6724 | 27.4464 | 27.1952 | 26.9458
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | System Transformation | Headroom (MW) | N/A | 39.4664 | 39.4308 | 39.3679 | 39.2734 | 39.1064 | 38.9068 | 38.6629 | 38.4096 | 38.1708 | 37.9174 | 37.6524 | 37.3875 | 37.1196 | 36.8454 | 36.58 | 35.3067 | 33.936 | 32.5492
Ocker Hill 132kV | Ocker Hill 132 11 (GT1) | Ocker Hill B 132/33/11kVDUMMY | Primary | 11 | -2.0372 | 52.5412 | WPD Best View | Headroom (MW) | N/A | 40.7136 | 40.669 | 40.5932 | 40.4813 | 40.2638 | 40.018 | 39.7323 | 39.4311 | 39.1467 | 38.852 | 38.537 | 38.2176 | 37.8946 | 37.5667 | 37.2568 | 35.7592 | 34.1304 | 32.4777
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Consumer Transformation | Headroom (MW) | N/A | 50.16 | 49.77 | 49.56 | 49.32 | 48.8 | 48.55 | 47.81 | 46.96 | 46.17 | 45.45 | 44.81 | 44.18 | 43.54 | 42.83 | 41.99 | 35.72 | 28.52 | 17.8
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Leading the Way | Headroom (MW) | N/A | 50.16 | 49.72 | 49.49 | 49.23 | 48.49 | 48.21 | 47.42 | 46.55 | 45.75 | 45 | 44.28 | 43.57 | 42.83 | 42 | 42.6 | 33.4 | 24.25 | 12.2
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | Steady Progression | Headroom (MW) | N/A | 37.2439 | 37.2078 | 37.191 | 37.1717 | 37.1514 | 37.0937 | 37.009 | 36.925 | 36.8423 | 36.7436 | 36.6442 | 36.5469 | 36.4491 | 36.3513 | 36.2575 | 35.7859 | 35.3044 | 34.8043
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | System Transformation | Headroom (MW) | N/A | 49.3267 | 49.2317 | 49.1448 | 48.9645 | 48.7588 | 48.5017 | 48.1772 | 47.8456 | 47.5187 | 47.1877 | 46.8451 | 46.4987 | 46.1448 | 45.7857 | 45.9761 | 41.7601 | 39.8195 | 36.58
Oldbury 132kV | Birchfield Lane 132 11 (GT1) | Birchfield Lane 132/11kVDUMMY | Primary | 11 | -2.0221 | 52.4929 | WPD Best View | Headroom (MW) | N/A | 50.16 | 49.81 | 49.62 | 49.43 | 49.06 | 48.88 | 48.68 | 48.49 | 48.29 | 48.02 | 47.62 | 47.2498 | 46.8028 | 46.3491 | 46.4667 | 41.7144 | 37.62 | 32.58
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Consumer Transformation | Headroom (MW) | N/A | 24.09 | 23.9 | 23.71 | 15.38 | 14.97 | 14.71 | 14.46 | 13.78 | 13.17 | 12.73 | 12.43 | 12.23 | 12.08 | 11.93 | 11.76 | 10.13 | 16.04 | 5.61
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Leading the Way | Headroom (MW) | N/A | 24.09 | 23.87 | 23.68 | 15.34 | 14.84 | 14.57 | 14.31 | 14.07 | 13.85 | 13.65 | 13.48 | 13.32 | 13.16 | 12.97 | 12.74 | 19.27 | 4.34 | 1.49
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | Steady Progression | Headroom (MW) | N/A | 24.09 | 23.94 | 23.87 | 15.6 | 15.49 | 15.42 | 15.33 | 14.57 | 13.84 | 13.15 | 12.55 | 12.04 | 11.77 | 11.58 | 11.46 | 11.38 | 11.14 | 10.65
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | System Transformation | Headroom (MW) | N/A | 24.09 | 23.92 | 23.83 | 15.46 | 15.24 | 15.1 | 14.95 | 14.36 | 13.83 | 13.45 | 13.2 | 13.06 | 12.99 | 12.93 | 12.88 | 18.06 | 8.67 | 7.6
Oldbury 132kV | Oldbury 132 11 (GT1) | Oldbury B 11kV | Primary | 11 | -2.0223 | 52.4987 | WPD Best View | Headroom (MW) | N/A | 24.09 | 23.92 | 23.83 | 15.46 | 15.24 | 15.09 | 14.94 | 14.35 | 13.81 | 13.43 | 13.18 | 13.04 | 12.96 | 12.9 | 12.85 | 18.02 | 8.6 | 7.52
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Consumer Transformation | Headroom (MW) | N/A | 9.2446 | 9.1865 | 9.1024 | 8.9664 | 8.6544 | 8.3305 | 8.0224 | 7.7115 | 7.4051 | 7.0914 | 6.763 | 6.4301 | 6.0944 | 5.7541 | 5.4325 | 3.909 | 2.298 | 0.6696
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Leading the Way | Headroom (MW) | N/A | 12.6519 | 12.5716 | 12.4519 | 12.2535 | 11.8125 | 11.3438 | 10.916 | 10.482 | 10.0557 | 9.6178 | 9.1692 | 8.7128 | 8.261 | 7.8216 | 7.4039 | 5.2926 | 3.0261 | 0.73646
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | Steady Progression | Headroom (MW) | N/A | 5.0999 | 5.0952 | 5.0877 | 5.075 | 5.0597 | 5.0317 | 5.0049 | 4.9744 | 4.9446 | 4.91 | 4.8742 | 4.8393 | 4.8042 | 4.7687 | 4.7341 | 4.5754 | 4.4253 | 4.2794
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | System Transformation | Headroom (MW) | N/A | 7.2877 | 7.2664 | 7.2339 | 7.181 | 7.0862 | 6.9701 | 6.8473 | 6.7232 | 6.6014 | 6.475 | 6.3438 | 6.2117 | 6.0774 | 5.9408 | 5.8105 | 5.2189 | 4.6117 | 4.001
Oldbury 132kV | Tividale 132 11 (GT1A) | Tividale 132/11kVDUMMY | Primary | 11 | -2.0541 | 52.52 | WPD Best View | Headroom (MW) | N/A | 7.5984 | 7.5701 | 7.5289 | 7.4635 | 7.3308 | 7.1796 | 7.0215 | 6.8605 | 6.7043 | 6.5429 | 6.3736 | 6.2015 | 6.0267 | 5.849 | 5.6835 | 4.915 | 4.1145 | 3.3075
Penn 132kV | Coseley 132 11 (GT2) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Consumer Transformation | Headroom (MW) | N/A | 48.9 | 48.48 | 48.27 | 48.02 | 47.41 | 47.18 | 46.89 | 46.13 | 45.25 | 44.46 | 43.7 | 42.98 | 42.25 | 41.46 | 40.63 | 33.68 | 24.35 | 14.05
Penn 132kV | Coseley 132 11 (GT2) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Leading the Way | Headroom (MW) | N/A | 48.9 | 48.43 | 48.2 | 47.93 | 47.09 | 46.84 | 46.51 | 45.74 | 44.88 | 44.1 | 43.27 | 42.48 | 41.64 | 40.71 | 39.64 | 31.94 | 21.67 | 8.2
Penn 132kV | Coseley 132 11 (GT2) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | Steady Progression | Headroom (MW) | N/A | 41.3535 | 41.3257 | 41.2883 | 41.257 | 41.2271 | 41.1579 | 41.08 | 40.9874 | 40.8975 | 40.7878 | 40.6724 | 40.5636 | 40.4553 | 40.3469 | 40.2452 | 39.733 | 39.1605 | 38.5848
Penn 132kV | Coseley 132 11 (GT2) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | System Transformation | Headroom (MW) | N/A | 48.9 | 48.53 | 48.35 | 48.16 | 47.76 | 47.6 | 47.41 | 47.21 | 47.01 | 46.84 | 46.63 | 46.43 | 46.22 | 46.02 | 45.81 | 44.23 | 39.95 | 35.59
Penn 132kV | Coseley 132 11 (GT2) | Coseley 132/11kV | Primary | 11 | -2.0917 | 52.5519 | WPD Best View | Headroom (MW) | N/A | 48.9 | 48.48 | 48.27 | 48.02 | 47.41 | 47.18 | 46.89 | 46.13 | 45.25 | 44.46 | 43.71 | 42.98 | 42.25 | 41.46 | 40.63 | 33.68 | 24.36 | 14.05
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Consumer Transformation | Headroom (MW) | N/A | 45.6 | 45.14 | 44.88 | 44.6 | 43.85 | 43.57 | 43.03 | 42.13 | 41.15 | 40.25 | 39.4 | 38.59 | 37.78 | 36.88 | 35.83 | 27.77 | 17.08 | 5.25
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Leading the Way | Headroom (MW) | N/A | 45.6 | 45.07 | 44.79 | 44.47 | 43.42 | 43.11 | 42.51 | 41.72 | 40.75 | 39.84 | 38.89 | 37.99 | 37.04 | 35.97 | 34.67 | 25.78 | 21.58 | 6.11
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | Steady Progression | Headroom (MW) | N/A | 45.6 | 45.25 | 45.08 | 44.91 | 44.61 | 44.47 | 44.31 | 44.2 | 44.05 | 43.9 | 43.74 | 43.58 | 43.43 | 43.27 | 43.12 | 42.38 | 41.31 | 39.99
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | System Transformation | Headroom (MW) | N/A | 45.6 | 45.19 | 44.98 | 44.77 | 44.28 | 44.09 | 43.89 | 43.78 | 43.59 | 43.39 | 43.18 | 42.97 | 42.77 | 42.56 | 42.35 | 40.18 | 35.38 | 30.53
Penn 132kV | Dudley 132 11 (GT1) | Dudley 132/11kVDUMMY | Primary | 11 | -2.0997 | 52.5069 | WPD Best View | Headroom (MW) | N/A | 45.6 | 45.14 | 44.89 | 44.61 | 43.87 | 43.59 | 43.15 | 42.27 | 41.3 | 40.42 | 39.58 | 38.79 | 37.99 | 37.14 | 36.14 | 28.39 | 18 | 6.54
Penn 132kV | Hinksford 132 33 | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Consumer Transformation | Headroom (MW) | Thermal | 22.68 | 22.33 | 21.7 | 21.23 | 20 | 19 | 18.04 | 16.96 | 15.89 | 14.86 | 13.74 | 12.5 | 11.22 | 9.96 | 8.56 | 1.36 | -7.82 | -18.16
Penn 132kV | Hinksford 132 33 | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Leading the Way | Headroom (MW) | Thermal | 22.68 | 22.28 | 21.64 | 21.14 | 19.71 | 18.65 | 17.63 | 16.7 | 15.85 | 15.05 | 14.13 | 13.23 | 11.96 | 10.65 | 9.25 | 1.33 | -9 | -21.2
Penn 132kV | Hinksford 132 33 | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | Steady Progression | Headroom (MW) | N/A | 22.68 | 22.51 | 22.41 | 22.31 | 22.14 | 21.99 | 21.83 | 21.63 | 21.42 | 21.2 | 20.96 | 20.74 | 20.39 | 20.07 | 19.71 | 19.12 | 17.6 | 15.55
Penn 132kV | Hinksford 132 33 | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | System Transformation | Headroom (MW) | N/A | 22.68 | 22.43 | 22.22 | 21.72 | 21.19 | 20.78 | 20.32 | 19.65 | 18.91 | 18.25 | 17.49 | 16.74 | 16.02 | 15.4 | 14.6 | 12.21 | 7.46 | 2.34
Penn 132kV | Hinksford 132 33 | Hinksford 132/33/11kVDUMMY | Primary | 11 | -2.1938 | 52.506 | WPD Best View | Headroom (MW) | Thermal | 22.68 | 22.32 | 21.69 | 21.22 | 19.94 | 18.92 | 17.94 | 17.02 | 16.16 | 15.37 | 14.56 | 13.73 | 12.54 | 11.33 | 10.07 | 2.76 | -6.87 | -16.99
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Consumer Transformation | Headroom (MW) | Thermal | 47.19 | 46.69 | 46.4 | 46.08 | 45.06 | 43.68 | 42.37 | 41.1 | 39.9 | 38.83 | 37.77 | 36.59 | 35.42 | 34.19 | 32.91 | 23.33 | 10.9 | -2.85
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Leading the Way | Headroom (MW) | Thermal | 47.19 | 46.61 | 46.3 | 45.93 | 44.57 | 43.14 | 41.78 | 40.55 | 39.37 | 38.28 | 37.13 | 35.87 | 34.55 | 33.12 | 31.5 | 20.95 | 7.3 | -10.79
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | Steady Progression | Headroom (MW) | N/A | 47.19 | 46.82 | 46.65 | 46.48 | 46.18 | 46 | 45.83 | 45.64 | 45.45 | 45.26 | 45.07 | 44.88 | 44.69 | 44.5 | 44.31 | 43.45 | 42.29 | 40.36
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | System Transformation | Headroom (MW) | N/A | 47.19 | 46.75 | 46.53 | 46.3 | 45.78 | 45.55 | 45.31 | 44.83 | 44.2 | 43.62 | 43.09 | 42.64 | 42.26 | 41.94 | 41.68 | 38.59 | 33.02 | 27.44
Penn 132kV | Lye 132 11 (GT1) | Lye 11kV DUMMY | Primary | 11 | -2.1224 | 52.4594 | WPD Best View | Headroom (MW) | Thermal | 47.19 | 46.69 | 46.41 | 46.1 | 45.22 | 43.9 | 42.64 | 41.43 | 40.28 | 39.24 | 38.24 | 37.16 | 36.05 | 34.89 | 33.68 | 24.68 | 12.77 | -0.37
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Consumer Transformation | Headroom (MW) | N/A | 2.15 | 2.13 | 2.1 | 2.08 | 2.01 | 1.95 | 1.89 | 1.83 | 1.78 | 1.72 | 1.67 | 1.62 | 1.57 | 1.51 | 1.45 | 1.1 | 0.68 | 0.2
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Leading the Way | Headroom (MW) | Thermal | 2.15 | 2.12 | 2.1 | 2.07 | 1.99 | 1.94 | 1.88 | 1.82 | 1.77 | 1.71 | 1.65 | 1.59 | 1.53 | 1.47 | 1.41 | 1.02 | 0.53 | -0.1
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | Steady Progression | Headroom (MW) | N/A | 2.15 | 2.14 | 2.13 | 2.12 | 2.11 | 2.1 | 2.09 | 2.08 | 2.06 | 2.05 | 2.04 | 2.03 | 2.03 | 2.02 | 2.02 | 2.02 | 1.98 | 1.88
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | System Transformation | Headroom (MW) | N/A | 2.15 | 2.13 | 2.12 | 2.1 | 2.07 | 2.05 | 2.02 | 1.98 | 1.95 | 1.93 | 1.9 | 1.88 | 1.86 | 1.84 | 1.82 | 1.74 | 1.55 | 1.36
Penn 132kV | Wolverhampton West 132 33 | PATTINGHAM 33 11kV S STN | Primary | 11 | -2.2589 | 52.5899 | WPD Best View | Headroom (MW) | N/A | 2.15 | 2.13 | 2.1 | 2.08 | 2.01 | 1.97 | 1.92 | 1.87 | 1.82 | 1.78 | 1.73 | 1.69 | 1.64 | 1.6 | 1.54 | 1.23 | 0.82 | 0.27
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Consumer Transformation | Headroom (MW) | Thermal | 29.6202 | 29.3826 | 29.0755 | 28.6655 | 27.7373 | 26.814 | 25.8575 | 24.7235 | 23.5382 | 22.2982 | 20.9123 | 19.4671 | 17.9734 | 16.5122 | 15.2612 | 9.1928 | 2.7962 | -6.89
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Leading the Way | Headroom (MW) | Thermal | 36.8062 | 36.9793 | 36.5942 | 36.0788 | 34.9204 | 33.7586 | 32.5499 | 31.3311 | 30.099 | 28.8512 | 27.4954 | 26.1308 | 24.3529 | 22.5729 | 20.7635 | 12.8685 | 4.07 | -11.56
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | Steady Progression | Headroom (MW) | N/A | 16.7577 | 16.7447 | 16.731 | 16.717 | 16.7011 | 16.6503 | 16.5887 | 16.4966 | 16.4044 | 16.2917 | 16.1679 | 16.0381 | 15.8454 | 15.6543 | 15.4286 | 15.0697 | 14.4642 | 13.8563
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | System Transformation | Headroom (MW) | N/A | 23.9467 | 23.8782 | 23.7915 | 23.6865 | 23.4939 | 23.2537 | 22.953 | 22.5384 | 22.0874 | 21.6097 | 21.0599 | 20.3518 | 19.5569 | 18.7918 | 18.2282 | 15.4402 | 12.5134 | 9.4129
Penn 132kV | Wolverhampton West 132 33 | Wolverhampton West 132/33/11kVDUMMY | Primary | 11 | -2.1856 | 52.5738 | WPD Best View | Headroom (MW) | Thermal | 24.9677 | 24.8086 | 24.6032 | 24.3291 | 23.7081 | 23.0857 | 22.3862 | 21.5477 | 20.7015 | 19.8487 | 18.9333 | 18.0176 | 16.8196 | 15.6341 | 14.7072 | 9.485 | 3.7448 | -5.54
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Consumer Transformation | Headroom (MW) | N/A | 51.91 | 51.59 | 51.43 | 51.29 | 50.72 | 50.27 | 49.57 | 48.88 | 48.22 | 47.61 | 47.02 | 46.46 | 45.92 | 45.32 | 44.71 | 40.3 | 35.1 | 29.46
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Leading the Way | Headroom (MW) | N/A | 51.91 | 51.54 | 51.38 | 51.22 | 50.38 | 49.87 | 49.12 | 48.41 | 47.72 | 47.1 | 46.47 | 45.87 | 45.26 | 44.63 | 43.95 | 39.68 | 34.06 | 26.99
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | Steady Progression | Headroom (MW) | N/A | 51.91 | 51.65 | 51.53 | 51.43 | 51.19 | 51.08 | 50.97 | 50.85 | 50.71 | 50.59 | 50.46 | 50.33 | 50.2 | 50.06 | 49.93 | 49.25 | 48.47 | 47.6
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | System Transformation | Headroom (MW) | N/A | 51.91 | 51.62 | 51.49 | 51.37 | 50.98 | 50.85 | 50.7 | 50.55 | 50.2 | 49.85 | 49.51 | 49.2 | 48.91 | 48.65 | 48.4 | 47.15 | 44.72 | 42.12
Penn 132kV | Woodside 132 11 (GT1A) | Woodside 132/11kVDUMMY | Primary | 11 | -2.1174 | 52.4897 | WPD Best View | Headroom (MW) | N/A | 51.91 | 51.59 | 51.44 | 51.3 | 50.76 | 50.38 | 49.7 | 49.04 | 48.4 | 47.82 | 47.25 | 46.71 | 46.18 | 45.62 | 45.05 | 41.02 | 36.08 | 30.73
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Consumer Transformation | Headroom (MW) | N/A | 19.36 | 14.56 | 14.48 | 14.39 | 14.3 | 14.21 | 13.99 | 13.87 | 13.74 | 13.59 | 13.41 | 13.22 | 13.02 | 12.79 | 12.54 | 10.5 | 8.5 | 5.79
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Leading the Way | Headroom (MW) | N/A | 19.36 | 14.55 | 14.47 | 14.37 | 14.32 | 14.33 | 14.17 | 14.11 | 13.99 | 13.83 | 13.6 | 13.37 | 13.11 | 12.82 | 12.49 | 10.22 | 10.75 | 1.88
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | Steady Progression | Headroom (MW) | N/A | 19.36 | 14.58 | 14.53 | 14.47 | 14.57 | 14.64 | 14.59 | 14.62 | 14.64 | 14.65 | 14.64 | 14.64 | 14.64 | 14.63 | 14.61 | 14.51 | 14.14 | 13.68
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | System Transformation | Headroom (MW) | N/A | 19.36 | 14.57 | 14.51 | 14.44 | 14.54 | 14.63 | 14.61 | 14.6 | 14.57 | 14.52 | 14.45 | 14.36 | 14.28 | 14.22 | 14.15 | 13.67 | 15.16 | 10.38
Port Ham 132kV | Castle Meads 132 33 | BROCKWORTH 33 11kV S STN | Primary | 11 | -2.167 | 51.8451 | WPD Best View | Headroom (MW) | N/A | 19.36 | 14.58 | 14.53 | 14.47 | 14.57 | 14.64 | 14.59 | 14.62 | 14.64 | 14.65 | 14.64 | 14.64 | 14.64 | 14.63 | 14.61 | 14.51 | 14.14 | 13.68
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Consumer Transformation | Headroom (MW) | N/A | 31.6 | 31.31 | 31.36 | 31.22 | 30.86 | 30.62 | 30.38 | 29.29 | 28.13 | 27.03 | 25.77 | 24.41 | 23.01 | 21.63 | 19.98 | 14 | 11.96 | 4.17
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Leading the Way | Headroom (MW) | Thermal | 31.6 | 31.29 | 31.36 | 31.2 | 30.72 | 30.42 | 30.13 | 29.53 | 28.91 | 28.28 | 27.61 | 26.97 | 25.71 | 24.45 | 23.13 | 10.3 | 6.3 | -1.72
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | Steady Progression | Headroom (MW) | N/A | 31.6 | 31.36 | 31.42 | 31.32 | 31.16 | 31.04 | 30.94 | 30.63 | 30.32 | 30 | 29.7 | 29.44 | 29.23 | 28.76 | 28.04 | 26.94 | 25.37 | 28.27
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | System Transformation | Headroom (MW) | N/A | 31.6 | 31.34 | 31.41 | 31.29 | 31.05 | 30.92 | 30.82 | 30.51 | 29.91 | 29.07 | 28.07 | 26.99 | 25.88 | 24.86 | 23.68 | 21.05 | 24.04 | 11.17
Port Ham 132kV | Castle Meads 132 33 | COMMERCIAL RD 33 11kV S STN | Primary | 11 | -2.2501 | 51.8645 | WPD Best View | Headroom (MW) | N/A | 31.6 | 31.36 | 31.42 | 31.32 | 31.16 | 31.04 | 30.94 | 30.63 | 30.32 | 30 | 29.7 | 29.44 | 29.23 | 28.76 | 28.04 | 26.94 | 25.37 | 28.27
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Consumer Transformation | Headroom (MW) | Thermal | 23.26 | 23.95 | 24.49 | 24.7 | 24.68 | 24.69 | 24.65 | 24.03 | 23.31 | 22.48 | 21.43 | 20.25 | 19.02 | 17.84 | 16.56 | 12.06 | 6.28 | -0.14
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Leading the Way | Headroom (MW) | N/A | 23.26 | 24.04 | 24.64 | 24.87 | 24.74 | 24.7 | 24.6 | 24.17 | 23.76 | 23.27 | 22.73 | 22.15 | 21.05 | 19.99 | 19.06 | 14.05 | 7.38 | 1.14
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | Steady Progression | Headroom (MW) | N/A | 23.26 | 23.88 | 24.38 | 24.61 | 24.68 | 24.82 | 24.91 | 24.99 | 25.03 | 25.01 | 24.99 | 24.97 | 24.93 | 24.78 | 24.29 | 23.45 | 22.12 | 20.34
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | System Transformation | Headroom (MW) | N/A | 23.26 | 23.97 | 24.52 | 24.76 | 24.8 | 24.93 | 25.01 | 25.01 | 24.8 | 24.24 | 23.46 | 22.61 | 21.71 | 20.84 | 19.88 | 17.79 | 14.2 | 10.2
Port Ham 132kV | Castle Meads 132 33 | ROTOL 33 11kV S STN | Primary | 11 | -2.1785 | 51.8975 | WPD Best View | Headroom (MW) | N/A | 23.26 | 23.88 | 24.38 | 24.61 | 24.68 | 24.82 | 24.91 | 24.99 | 25.03 | 25.01 | 24.99 | 24.97 | 24.93 | 24.78 | 24.29 | 23.45 | 22.12 | 20.34
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Consumer Transformation | Headroom (MW) | Thermal | 20.45 | 20.33 | 20.35 | 20.28 | 19.99 | 19.5 | 19.03 | 18.34 | 17.61 | 16.86 | 15.98 | 14.97 | 13.89 | 12.86 | 11.67 | 7.05 | 1.13 | -5.64
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Leading the Way | Headroom (MW) | Thermal | 20.45 | 20.32 | 20.33 | 20.27 | 19.86 | 19.33 | 18.84 | 18.36 | 17.92 | 17.49 | 17.06 | 16.65 | 15.76 | 14.8 | 13.76 | 8.65 | 1.82 | -5.18
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | Steady Progression | Headroom (MW) | N/A | 20.45 | 20.37 | 20.41 | 20.38 | 20.3 | 20.26 | 20.2 | 20.14 | 20.07 | 19.99 | 19.9 | 19.81 | 19.43 | 19.03 | 18.54 | 17.94 | 16.66 | 14.88
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | System Transformation | Headroom (MW) | N/A | 20.45 | 20.36 | 20.39 | 20.35 | 20.2 | 20.14 | 20.05 | 19.68 | 19.13 | 18.56 | 17.85 | 17.07 | 16.27 | 15.57 | 14.73 | 12.78 | 9.24 | 5.32
Port Ham 132kV | Castle Meads 132 33 | TUFFLEY 33 11kV S STN | Primary | 11 | -2.2621 | 51.8372 | WPD Best View | Headroom (MW) | N/A | 20.45 | 20.37 | 20.41 | 20.38 | 20.3 | 20.26 | 20.2 | 20.14 | 20.07 | 19.99 | 19.9 | 19.81 | 19.43 | 19.03 | 18.54 | 17.94 | 16.66 | 14.88
Port Ham 132kV | Cheltenham 132 11 (GT3) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Consumer Transformation | Headroom (MW) | N/A | 41.88 | 41.6 | 41.84 | 42.01 | 42.05 | 42.25 | 42.5 | 42.52 | 41.98 | 41.4 | 40.5 | 39.5 | 38.35 | 37.19 | 35.98 | 30.91 | 24.73 | 17.87
Port Ham 132kV | Cheltenham 132 11 (GT3) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Leading the Way | Headroom (MW) | N/A | 41.88 | 41.58 | 41.85 | 42.1 | 42.12 | 42.45 | 42.78 | 43.02 | 42.67 | 42.29 | 41.59 | 40.85 | 39.72 | 38.54 | 37.4 | 31.88 | 24.94 | 17.34
Port Ham 132kV | Cheltenham 132 11 (GT3) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | Steady Progression | Headroom (MW) | N/A | 41.88 | 41.65 | 41.87 | 42.05 | 42.21 | 42.41 | 42.59 | 42.75 | 42.9 | 43.04 | 43.12 | 43.2 | 43.26 | 43.3 | 43.33 | 43.3 | 42.52 | 40.72
Port Ham 132kV | Cheltenham 132 11 (GT3) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | System Transformation | Headroom (MW) | N/A | 41.88 | 41.63 | 41.88 | 42.08 | 42.22 | 42.47 | 42.76 | 42.98 | 43.16 | 43.33 | 43.01 | 42.36 | 41.63 | 40.99 | 40.31 | 38.27 | 34.61 | 30.71
Port Ham 132kV | Cheltenham 132 11 (GT3) | Cheltenham 132/66/11kVDUMMY | Primary | 11 | -2.1206 | 51.9096 | WPD Best View | Headroom (MW) | N/A | 41.88 | 41.65 | 41.87 | 42.05 | 42.21 | 42.41 | 42.59 | 42.75 | 42.9 | 43.04 | 43.12 | 43.2 | 43.26 | 43.3 | 43.33 | 43.3 | 42.52 | 40.72
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Consumer Transformation | Headroom (MW) | Thermal | 7.29 | 7.13 | 1.74 | 1.62 | 1.35 | 1.13 | 0.93 | 0.54 | 0.08 | -0.4 | -1.04 | -1.74 | -2.49 | -3.16 | -3.98 | -6.09 | -9.54 | -12.69
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Leading the Way | Headroom (MW) | Thermal | 7.29 | 7.13 | 1.73 | 1.61 | 1.3 | 1.06 | 0.85 | 0.71 | 0.52 | 0.39 | 0.22 | 0.05 | -0.55 | -1.13 | -1.75 | -4.13 | -8.91 | -11.33
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | Steady Progression | Headroom (MW) | N/A | 7.29 | 7.17 | 7.11 | 7.06 | 6.99 | 6.92 | 6.86 | 6.76 | 6.64 | 6.53 | 6.36 | 6.19 | 5.81 | 5.46 | 5 | 4.41 | 3.62 | 2.61
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | System Transformation | Headroom (MW) | Thermal | 7.29 | 7.15 | 7.08 | 6.84 | 6.7 | 6.58 | 6.46 | 6.14 | 5.74 | 5.33 | 4.75 | 4.11 | 3.44 | 2.86 | 2.14 | 0.99 | -1.67 | -3.91
Port Ham 132kV | Cheltenham 132 66 | ALDERTON 66 11kV S STN | Primary | 11 | -1.9982 | 51.9913 | WPD Best View | Headroom (MW) | N/A | 7.29 | 7.17 | 7.11 | 7.06 | 6.99 | 6.92 | 6.86 | 6.76 | 6.64 | 6.53 | 6.36 | 6.19 | 5.81 | 5.46 | 5 | 4.41 | 3.62 | 2.61
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Consumer Transformation | Headroom (MW) | Thermal | 2.45 | 2.34 | 2.06 | 1.93 | 1.61 | 1.34 | 1.08 | 0.61 | 0.1 | -0.48 | -1.27 | -2.15 | -3.08 | -3.92 | -4.96 | -7.71 | -11.91 | -16.19
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Leading the Way | Headroom (MW) | Thermal | 2.45 | 2.33 | 2.05 | 1.9 | 1.56 | 1.28 | 1.02 | 0.86 | 0.74 | 0.57 | 0.36 | 0.16 | -0.6 | -1.33 | -2.13 | -5.27 | -7.31 | -13.48
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | Steady Progression | Headroom (MW) | Thermal | 2.45 | 2.4 | 2.39 | 2.37 | 2.34 | 2.3 | 2.23 | 2.16 | 2.1 | 2 | 1.85 | 1.67 | 1.25 | 0.85 | 0.31 | -0.22 | -1.07 | -2.27
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | System Transformation | Headroom (MW) | Thermal | 2.45 | 2.37 | 2.32 | 2.08 | 1.96 | 1.85 | 1.7 | 1.35 | 0.94 | 0.45 | -0.24 | -1.01 | -1.81 | -2.51 | -3.37 | -4.76 | -6.5 | -11.38
Port Ham 132kV | Cheltenham 132 66 | BISHOPS CLEEVE 66 11kV S STN | Primary | 11 | -2.0789 | 51.9472 | WPD Best View | Headroom (MW) | Thermal | 2.45 | 2.4 | 2.39 | 2.37 | 2.34 | 2.3 | 2.23 | 2.16 | 2.1 | 2 | 1.85 | 1.67 | 1.25 | 0.85 | 0.31 | -0.22 | -1.07 | -2.27
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Consumer Transformation | Headroom (MW) | N/A | 49.06 | 48.69 | 48.49 | 48.26 | 48.04 | 47.94 | 47.74 | 47.51 | 47.21 | 46.68 | 46.18 | 45.67 | 45.16 | 44.61 | 44.02 | 39.4 | 32.86 | 25.64
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Leading the Way | Headroom (MW) | N/A | 49.06 | 48.67 | 48.46 | 48.21 | 47.94 | 47.88 | 47.65 | 47.39 | 47.12 | 46.61 | 46.04 | 45.48 | 44.88 | 44.2 | 43.44 | 38.14 | 30.93 | 21.46
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | Steady Progression | Headroom (MW) | N/A | 44.8978 | 44.8897 | 44.8816 | 44.8732 | 44.8638 | 44.834 | 44.7988 | 44.7583 | 44.7197 | 44.6709 | 44.6217 | 44.5734 | 44.5252 | 44.4772 | 44.4306 | 44.1871 | 43.916 | 43.6411
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | System Transformation | Headroom (MW) | N/A | 49.06 | 48.72 | 48.55 | 48.37 | 48.26 | 48.21 | 48.06 | 47.9 | 47.75 | 47.59 | 47.44 | 47.27 | 47.1 | 46.92 | 46.75 | 45.87 | 43.21 | 40.02
Port Ham 132kV | Eastern Avenue 132 11 (GT1A) | Eastern Avenue 132/11kVDUMMY | Primary | 11 | -2.2256 | 51.8548 | WPD Best View | Headroom (MW) | N/A | 49.06 | 48.74 | 48.6 | 48.45 | 48.39 | 48.34 | 48.21 | 48.08 | 47.95 | 47.82 | 47.68 | 47.55 | 47.42 | 47.27 | 47.13 | 46.46 | 45.59 | 44.58
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Consumer Transformation | Headroom (MW) | N/A | 40.54 | 40.17 | 39.89 | 39.57 | 38.77 | 38.14 | 37.44 | 36.58 | 35.82 | 35.06 | 34.32 | 33.64 | 32.97 | 32.27 | 31.4 | 26.56 | 20.72 | 14.3
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Leading the Way | Headroom (MW) | N/A | 40.54 | 40.14 | 39.85 | 39.51 | 38.6 | 37.95 | 37.23 | 36.45 | 35.77 | 34.99 | 34.22 | 33.5 | 32.78 | 32 | 31.16 | 25.89 | 19.38 | 11.28
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | Steady Progression | Headroom (MW) | N/A | 40.54 | 40.28 | 40.16 | 40.05 | 39.88 | 39.77 | 39.66 | 39.57 | 39.45 | 39.23 | 39.07 | 38.95 | 38.84 | 38.75 | 38.68 | 38.57 | 37.83 | 36.53
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | System Transformation | Headroom (MW) | N/A | 40.54 | 40.23 | 40.05 | 39.85 | 39.46 | 39.23 | 38.99 | 38.6 | 38.12 | 37.74 | 37.36 | 37.05 | 36.8 | 36.57 | 36.29 | 35.18 | 32.33 | 29.38
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD NORTH 66 11kV S STN | Primary | 11 | -2.7146 | 52.0744 | WPD Best View | Headroom (MW) | N/A | 40.54 | 40.17 | 39.89 | 39.57 | 38.77 | 38.14 | 37.44 | 36.58 | 35.82 | 35.06 | 34.32 | 33.64 | 32.97 | 32.27 | 31.4 | 26.56 | 20.72 | 14.3
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Consumer Transformation | Headroom (MW) | Thermal | 10.84 | 10.56 | 10.33 | 10.09 | 9.29 | 8.32 | 7.33 | 5.84 | 4.28 | 2.71 | 0.93 | -0.93 | -2.89 | -4.79 | -6.99 | -15.43 | -25.4 | -36.5
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Leading the Way | Headroom (MW) | Thermal | 10.84 | 10.53 | 10.29 | 10.04 | 9.17 | 8.07 | 6.94 | 5.8 | 4.74 | 3.65 | 2.51 | 1.39 | -0.54 | -2.42 | -4.4 | -13.48 | -25.05 | -36.15
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | Steady Progression | Headroom (MW) | N/A | 10.84 | 10.68 | 10.63 | 10.58 | 10.44 | 10.26 | 10.07 | 9.76 | 9.46 | 9.12 | 8.75 | 8.36 | 7.65 | 6.96 | 6.2 | 4.95 | 3.18 | 0.84
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | System Transformation | Headroom (MW) | Thermal | 10.84 | 10.62 | 10.52 | 10.36 | 9.99 | 9.73 | 9.41 | 8.29 | 6.85 | 5.85 | 4.55 | 3.18 | 1.8 | 0.57 | -0.92 | -4.37 | -10.69 | -17.52
Port Ham 132kV | Hereford (Walham) 132 66 | HEREFORD SOUTH 66 11kV S STN | Primary | 11 | -2.7064 | 52.0293 | WPD Best View | Headroom (MW) | Thermal | 10.84 | 10.56 | 10.33 | 10.09 | 9.29 | 8.32 | 7.33 | 5.84 | 4.28 | 2.71 | 0.93 | -0.93 | -2.89 | -4.79 | -6.99 | -15.43 | -25.4 | -36.5
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Consumer Transformation | Headroom (MW) | N/A | 25.02 | 24.86 | 24.78 | 24.7 | 24.48 | 24.23 | 23.95 | 23.69 | 23.43 | 23.22 | 23 | 22.8 | 22.59 | 22.37 | 22.14 | 20.4 | 18.25 | 15.88
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Leading the Way | Headroom (MW) | N/A | 25.02 | 24.84 | 24.76 | 24.67 | 24.36 | 24.09 | 23.8 | 23.53 | 23.28 | 23.06 | 22.83 | 22.62 | 22.39 | 22.15 | 21.89 | 20.12 | 17.79 | 14.82
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | Steady Progression | Headroom (MW) | N/A | 25.02 | 24.88 | 24.81 | 24.75 | 24.64 | 24.58 | 24.51 | 24.44 | 24.38 | 24.31 | 24.24 | 24.18 | 24.11 | 24.05 | 23.99 | 23.67 | 23.33 | 22.96
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | System Transformation | Headroom (MW) | N/A | 25.02 | 24.87 | 24.8 | 24.72 | 24.57 | 24.49 | 24.41 | 24.31 | 24.16 | 24.03 | 23.9 | 23.79 | 23.7 | 23.61 | 23.53 | 23.07 | 22.06 | 20.95
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford Central 66/11kv | Primary | 11 | -2.7161 | 52.0596 | WPD Best View | Headroom (MW) | N/A | 25.02 | 24.86 | 24.78 | 24.7 | 24.48 | 24.23 | 23.95 | 23.69 | 23.43 | 23.22 | 23 | 22.8 | 22.59 | 22.37 | 22.14 | 20.4 | 18.25 | 15.88
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Consumer Transformation | Headroom (MW) | N/A | 13.94 | 13.75 | 13.54 | 13.38 | 12.93 | 12.65 | 12.37 | 12.12 | 11.9 | 11.75 | 11.65 | 11.56 | 11.49 | 11.41 | 11.29 | 10.14 | 7.65 | 4.79
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Leading the Way | Headroom (MW) | N/A | 13.94 | 13.73 | 13.52 | 13.35 | 12.82 | 12.54 | 12.27 | 12.04 | 11.85 | 11.75 | 11.67 | 11.63 | 11.58 | 11.47 | 11.34 | 10.21 | 7.42 | 3.71
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | Steady Progression | Headroom (MW) | N/A | 13.94 | 13.81 | 13.74 | 13.68 | 13.59 | 13.53 | 13.48 | 13.43 | 13.39 | 13.38 | 13.39 | 13.41 | 13.49 | 13.59 | 13.7 | 14.47 | 14.18 | 13.47
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | System Transformation | Headroom (MW) | N/A | 13.94 | 13.78 | 13.68 | 13.52 | 13.3 | 13.18 | 13.04 | 12.92 | 12.82 | 12.77 | 12.75 | 12.76 | 12.8 | 12.86 | 12.94 | 13.26 | 12.07 | 10.79
Port Ham 132kV | Lydney 132 33 | BILSON 33 11kV S STN | Primary | 11 | -2.51 | 51.8225 | WPD Best View | Headroom (MW) | N/A | 13.94 | 13.81 | 13.74 | 13.68 | 13.58 | 13.53 | 13.48 | 13.42 | 13.38 | 13.37 | 13.37 | 13.39 | 13.47 | 13.56 | 13.67 | 14.44 | 14.15 | 13.44
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Consumer Transformation | Headroom (MW) | Thermal | 3.44 | 3.19 | 3.09 | 2.98 | 2.65 | 2.43 | 2.21 | 2 | 1.8 | 1.63 | 1.47 | 1.32 | 1.17 | 0.99 | 0.79 | -1.75 | -3.66 | -5.77
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Leading the Way | Headroom (MW) | Thermal | 3.44 | 3.18 | 3.08 | 2.95 | 2.58 | 2.36 | 2.12 | 1.92 | 1.72 | 1.55 | 1.38 | 1.22 | 1.04 | 0.82 | 0.57 | -3.19 | -5.29 | -8.04
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | Steady Progression | Headroom (MW) | N/A | 3.44 | 3.24 | 3.21 | 3.19 | 3.15 | 3.12 | 3.08 | 3.04 | 3.01 | 2.97 | 2.94 | 2.91 | 2.89 | 2.88 | 2.87 | 2.95 | 2.77 | 2.35
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | System Transformation | Headroom (MW) | Thermal | 3.44 | 3.22 | 3.16 | 3.1 | 2.97 | 2.88 | 2.76 | 2.66 | 2.55 | 2.47 | 2.38 | 2.31 | 2.25 | 2.21 | 2.18 | 0.81 | -0.08 | -0.97
Port Ham 132kV | Lydney 132 33 | BIXHEAD 33 11kV S STN | Primary | 11 | -2.5919 | 51.7958 | WPD Best View | Headroom (MW) | N/A | 3.44 | 3.24 | 3.21 | 3.19 | 3.14 | 3.12 | 3.07 | 3.03 | 2.99 | 2.96 | 2.92 | 2.89 | 2.86 | 2.85 | 2.84 | 2.92 | 2.74 | 2.32
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Consumer Transformation | Headroom (MW) | Thermal | 4.175 | 4.105 | 4.055 | 3.985 | 3.825 | 3.705 | 3.585 | 2.705 | 1.645 | 0.405 | -1.015 | -2.645 | -4.375 | -5.925 | -7.845 | -11.485 | -15.325 | -20.045
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Leading the Way | Headroom (MW) | Thermal | 4.175 | 4.095 | 4.045 | 3.975 | 3.785 | 3.665 | 3.515 | 3.395 | 3.265 | 3.155 | 3.055 | 2.965 | 1.655 | 0.445 | -0.845 | -5.185 | -10.095 | -12.015
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | Steady Progression | Headroom (MW) | Thermal | 4.175 | 4.135 | 4.115 | 4.095 | 4.065 | 4.045 | 4.015 | 3.795 | 3.575 | 3.295 | 2.975 | 2.565 | 1.615 | 0.695 | -0.535 | -2.075 | -3.635 | -5.295
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | System Transformation | Headroom (MW) | Thermal | 4.175 | 4.125 | 4.085 | 4.055 | 3.975 | 3.915 | 3.845 | 3.015 | 1.965 | 0.765 | -0.625 | -2.215 | -3.905 | -5.385 | -7.225 | -10.155 | -13.455 | -17.555
Port Ham 132kV | Lydney 132 33 | ELTON 33 11kV S STN | Primary | 11 | -2.4428 | 51.8211 | WPD Best View | Headroom (MW) | Thermal | 4.175 | 4.135 | 4.115 | 4.095 | 4.065 | 4.045 | 4.015 | 3.795 | 3.575 | 3.295 | 2.975 | 2.565 | 1.615 | 0.695 | -0.535 | -2.075 | -3.635 | -5.295
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Consumer Transformation | Headroom (MW) | Thermal | 5.69 | 5.61 | 5.54 | 5.45 | 5.23 | 5.04 | 4.93 | 4.7 | 4.48 | 4.28 | 4.02 | 3.68 | 3.29 | 2.91 | 2.45 | 1.19 | -0.72 | -2.95
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Leading the Way | Headroom (MW) | Thermal | 5.69 | 5.6 | 5.53 | 5.44 | 5.19 | 4.99 | 4.91 | 4.87 | 4.9 | 4.99 | 5.03 | 5.01 | 4.67 | 4.34 | 3.99 | 2.47 | 0.19 | -1.9
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | Steady Progression | Headroom (MW) | N/A | 5.69 | 5.64 | 5.62 | 5.6 | 5.57 | 5.54 | 5.55 | 5.55 | 5.57 | 5.61 | 5.61 | 5.6 | 5.46 | 5.33 | 5.14 | 5.13 | 4.7 | 4.05
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | System Transformation | Headroom (MW) | N/A | 5.69 | 5.62 | 5.58 | 5.54 | 5.45 | 5.37 | 5.35 | 5.19 | 5.04 | 4.92 | 4.72 | 4.45 | 4.13 | 3.85 | 3.52 | 3.05 | 1.85 | 0.44
Port Ham 132kV | Lydney 132 33 | Lydney 33/11kVDUMMY | Primary | 11 | -2.5366 | 51.7368 | WPD Best View | Headroom (MW) | N/A | 5.69 | 5.64 | 5.62 | 5.6 | 5.57 | 5.54 | 5.55 | 5.55 | 5.57 | 5.61 | 5.61 | 5.6 | 5.46 | 5.33 | 5.14 | 5.13 | 4.7 | 4.05
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Consumer Transformation | Headroom (MW) | N/A | 19.56 | 19.39 | 19.3 | 19.21 | 19.02 | 19.04 | 19 | 18.97 | 18.95 | 18.94 | 18.91 | 18.85 | 18.79 | 18.73 | 18.67 | 16.79 | 15.92 | 14.98
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Leading the Way | Headroom (MW) | N/A | 19.56 | 19.39 | 19.3 | 19.2 | 18.98 | 19.07 | 19.06 | 19.06 | 19.08 | 19.1 | 19.07 | 19.01 | 18.92 | 18.83 | 18.74 | 15.93 | 14.97 | 13.85
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | Steady Progression | Headroom (MW) | N/A | 19.56 | 19.41 | 19.34 | 19.27 | 19.18 | 19.23 | 19.21 | 19.21 | 19.22 | 19.23 | 19.23 | 19.21 | 19.2 | 19.19 | 19.18 | 19.14 | 18.83 | 18.41
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | System Transformation | Headroom (MW) | N/A | 19.56 | 19.4 | 19.32 | 19.24 | 19.12 | 19.18 | 19.17 | 19.18 | 19.19 | 19.21 | 19.2 | 19.17 | 19.15 | 19.12 | 19.1 | 17.88 | 17.34 | 16.76
Port Ham 132kV | Lydney 132 33 | MEAD LA 33 11kV S STN | Primary | 11 | -2.5377 | 51.7143 | WPD Best View | Headroom (MW) | N/A | 19.56 | 19.41 | 19.34 | 19.27 | 19.18 | 19.23 | 19.21 | 19.21 | 19.22 | 19.23 | 19.23 | 19.21 | 19.2 | 19.19 | 19.18 | 19.14 | 18.83 | 18.41
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Consumer Transformation | Headroom (MW) | N/A | 9.23 | 9.16 | 9.11 | 9.06 | 8.89 | 8.82 | 8.74 | 8.67 | 8.61 | 8.57 | 8.5 | 8.43 | 8.37 | 8.3 | 8.22 | 7.57 | 6.68 | 5.71
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Leading the Way | Headroom (MW) | N/A | 9.23 | 9.15 | 9.1 | 9.05 | 8.85 | 8.8 | 8.73 | 8.68 | 8.64 | 8.62 | 8.55 | 8.47 | 8.4 | 8.3 | 8.2 | 7.46 | 6.49 | 5.26
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | Steady Progression | Headroom (MW) | N/A | 9.23 | 9.18 | 9.16 | 9.14 | 9.1 | 9.11 | 9.1 | 9.1 | 9.11 | 9.11 | 9.11 | 9.1 | 9.1 | 9.1 | 9.1 | 9.13 | 9.01 | 8.78
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | System Transformation | Headroom (MW) | N/A | 9.23 | 9.17 | 9.14 | 9.11 | 9.03 | 9.01 | 8.99 | 8.97 | 8.96 | 8.96 | 8.93 | 8.91 | 8.89 | 8.88 | 8.87 | 8.75 | 8.31 | 7.87
Port Ham 132kV | Lydney 132 33 | MITCHELDEAN 33 11kV S STN | Primary | 11 | -2.4988 | 51.8582 | WPD Best View | Headroom (MW) | N/A | 9.23 | 9.18 | 9.16 | 9.14 | 9.1 | 9.11 | 9.1 | 9.1 | 9.1 | 9.1 | 9.09 | 9.08 | 9.07 | 9.07 | 9.07 | 9.1 | 8.98 | 8.75
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Consumer Transformation | Headroom (MW) | N/A | 8.64 | 8.52 | 8.43 | 8.32 | 8.05 | 7.91 | 7.79 | 7.7 | 7.62 | 7.57 | 7.5 | 7.45 | 7.41 | 7.32 | 7.21 | 6.14 | 4.48 | 2.62
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Leading the Way | Headroom (MW) | N/A | 8.64 | 8.51 | 8.41 | 8.3 | 7.99 | 7.87 | 7.78 | 7.73 | 7.69 | 7.68 | 7.63 | 7.59 | 7.54 | 7.4 | 7.25 | 5.96 | 4.11 | 1.68
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | Steady Progression | Headroom (MW) | N/A | 8.64 | 8.56 | 8.53 | 8.5 | 8.45 | 8.44 | 8.44 | 8.45 | 8.47 | 8.5 | 8.52 | 8.56 | 8.62 | 8.65 | 8.69 | 8.89 | 8.72 | 8.31
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | System Transformation | Headroom (MW) | N/A | 8.64 | 8.54 | 8.48 | 8.42 | 8.3 | 8.26 | 8.23 | 8.22 | 8.22 | 8.24 | 8.25 | 8.26 | 8.3 | 8.3 | 8.32 | 8.25 | 7.45 | 6.64
Port Ham 132kV | Lydney 132 33 | PRINCESS ROYAL 33 11kV S STN | Primary | 11 | -2.5617 | 51.7544 | WPD Best View | Headroom (MW) | N/A | 8.64 | 8.56 | 8.53 | 8.5 | 8.45 | 8.44 | 8.44 | 8.45 | 8.47 | 8.5 | 8.52 | 8.56 | 8.62 | 8.65 | 8.69 | 8.89 | 8.72 | 8.31
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Consumer Transformation | Headroom (MW) | Thermal | 3.13 | 3.1 | 3.07 | 3.05 | 2.17 | 2.12 | 1.98 | 1.74 | 1.56 | 1.39 | 1.23 | 1.08 | 0.94 | 0.79 | 0.62 | -0.3 | -1.37 | -2.52
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Leading the Way | Headroom (MW) | Thermal | 3.13 | 3.09 | 3.07 | 2.25 | 2.15 | 2.14 | 2.01 | 1.87 | 1.76 | 1.62 | 1.5 | 1.39 | 1.28 | 1.15 | 1.01 | 0.24 | -0.71 | -1.81
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | Steady Progression | Headroom (MW) | N/A | 3.13 | 3.11 | 3.1 | 3.09 | 3.07 | 3.09 | 3.09 | 2.29 | 2.27 | 2.17 | 2.16 | 2.14 | 2.12 | 2.11 | 2.11 | 2.13 | 2.07 | 1.95
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | System Transformation | Headroom (MW) | N/A | 3.13 | 3.1 | 3.09 | 3.08 | 2.24 | 2.24 | 2.23 | 2.2 | 2.09 | 2.03 | 1.97 | 1.92 | 1.88 | 1.85 | 1.82 | 1.67 | 1.33 | 0.96
Port Ham 132kV | Lydney 132 33 | STOWFIELD 33 11kV S STN | Primary | 11 | -2.5989 | 51.8545 | WPD Best View | Headroom (MW) | Thermal | 3.13 | 3.1 | 3.08 | 3.06 | 2.19 | 2.16 | 2.04 | 1.82 | 1.66 | 1.52 | 1.38 | 1.26 | 1.14 | 1.01 | 0.87 | 0.1 | -0.84 | -1.85
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Consumer Transformation | Headroom (MW) | N/A | 49.71 | 49.37 | 49.16 | 48.92 | 48.45 | 47.74 | 46.86 | 46.03 | 45.29 | 44.83 | 44.26 | 43.51 | 42.75 | 41.96 | 41.13 | 35.11 | 26.98 | 17.88
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Leading the Way | Headroom (MW) | N/A | 49.71 | 49.33 | 49.11 | 48.84 | 48.21 | 47.48 | 46.57 | 45.76 | 45.05 | 44.7 | 44.15 | 43.34 | 42.5 | 41.55 | 40.48 | 33.69 | 24.82 | 12.95
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | Steady Progression | Headroom (MW) | N/A | 49.71 | 49.45 | 49.32 | 49.19 | 49.01 | 48.89 | 48.76 | 48.63 | 48.51 | 48.45 | 48.39 | 48.29 | 48.19 | 48.08 | 47.98 | 47.64 | 46.82 | 45.74
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | System Transformation | Headroom (MW) | N/A | 49.71 | 49.41 | 49.24 | 49.06 | 48.77 | 48.62 | 48.46 | 48.28 | 48.11 | 47.96 | 47.75 | 47.49 | 47.26 | 47.08 | 46.93 | 45.07 | 41.47 | 37.72
Port Ham 132kV | Montpellier 132 11 (GT1A) | Montpellier 132/11kVDUMMY | Primary | 11 | -2.0844 | 51.8927 | WPD Best View | Headroom (MW) | N/A | 49.71 | 49.45 | 49.32 | 49.19 | 49.01 | 48.89 | 48.76 | 48.63 | 48.51 | 48.45 | 48.39 | 48.29 | 48.19 | 48.08 | 47.98 | 47.64 | 46.82 | 45.74
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Consumer Transformation | Headroom (MW) | Thermal | 8.61 | 8.66 | 8.53 | 8.75 | 8.96 | 9.05 | 8.91 | 8.61 | 8.09 | 7.54 | 6.88 | 6.12 | 5.33 | 4.58 | 3.69 | 3.45 | -1.38 | -6.81
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Leading the Way | Headroom (MW) | Thermal | 8.61 | 8.71 | 8.58 | 8.87 | 9.15 | 9.42 | 9.31 | 9.24 | 8.92 | 8.61 | 8.28 | 7.96 | 7.21 | 6.46 | 5.66 | 4.98 | -5.63 | -11.06
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | Steady Progression | Headroom (MW) | N/A | 8.61 | 8.93 | 8.95 | 8.97 | 9.54 | 9.87 | 10.01 | 10.11 | 10.09 | 10.05 | 9.98 | 9.91 | 9.65 | 9.36 | 8.99 | 11.98 | 10.9 | 9.41
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | System Transformation | Headroom (MW) | Thermal | 8.61 | 8.96 | 8.7 | 8.91 | 9.43 | 9.73 | 9.77 | 9.64 | 9.28 | 8.9 | 8.38 | 7.78 | 7.16 | 6.62 | 5.98 | 8.04 | 1.66 | -1.64
Port Ham 132kV | Tewkesbury 132 11 (GT1) | Tewkesbury Grid 132/11kVDUMMY | Primary | 11 | -2.1629 | 51.9861 | WPD Best View | Headroom (MW) | N/A | 8.61 | 8.93 | 8.95 | 8.97 | 9.54 | 9.87 | 10.01 | 10.11 | 10.09 | 10.05 | 9.98 | 9.91 | 9.65 | 9.36 | 8.99 | 11.98 | 10.9 | 9.41
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Consumer Transformation | Headroom (MW) | N/A | 30.95 | 30.71 | 30.6 | 30.46 | 30.15 | 30.02 | 29.87 | 29.46 | 28.96 | 28.46 | 27.91 | 27.36 | 26.78 | 26.14 | 25.47 | 21.12 | 17.25 | 12.64
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Leading the Way | Headroom (MW) | N/A | 30.95 | 30.69 | 30.57 | 30.42 | 30 | 29.85 | 29.68 | 29.22 | 28.71 | 28.18 | 27.57 | 26.94 | 26.27 | 25.54 | 24.75 | 20.67 | 16.27 | 10.53
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | Steady Progression | Headroom (MW) | N/A | 30.95 | 30.76 | 30.67 | 30.58 | 30.44 | 30.35 | 30.27 | 30.18 | 30.11 | 30.03 | 29.96 | 29.88 | 29.81 | 29.75 | 29.69 | 29.51 | 28.98 | 28.73
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | System Transformation | Headroom (MW) | N/A | 30.95 | 30.73 | 30.64 | 30.53 | 30.32 | 30.21 | 30.11 | 30.02 | 29.93 | 29.84 | 29.74 | 29.55 | 29.25 | 28.94 | 28.63 | 27.21 | 25.49 | 23.34
Port ham 132kV | Cheltenham 132 66 | Marle Hill 132/66/11kVDUMMY | Primary | 11 | -2.0825 | 51.9105 | WPD Best View | Headroom (MW) | N/A | 30.95 | 30.76 | 30.67 | 30.58 | 30.44 | 30.35 | 30.27 | 30.18 | 30.11 | 30.03 | 29.96 | 29.88 | 29.81 | 29.75 | 29.69 | 29.51 | 28.98 | 28.73
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Consumer Transformation | Headroom (MW) | N/A | 94.1 | 93.64 | 93.36 | 93.08 | 92.37 | 92.04 | 91.21 | 90.17 | 89.17 | 88.26 | 87.26 | 86.26 | 85.23 | 84.13 | 82.84 | 74.73 | 63.99 | 52.01
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Leading the Way | Headroom (MW) | N/A | 94.1 | 93.58 | 93.28 | 92.97 | 91.99 | 91.61 | 90.75 | 89.74 | 88.79 | 87.91 | 87 | 86.11 | 85 | 83.81 | 82.44 | 73.42 | 61.47 | 46.61
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | Steady Progression | Headroom (MW) | N/A | 94.1 | 93.74 | 93.55 | 93.39 | 93.09 | 92.91 | 92.74 | 92.55 | 92.37 | 92.2 | 92.01 | 91.83 | 91.64 | 91.46 | 91.27 | 90.38 | 89.24 | 87.75
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | System Transformation | Headroom (MW) | N/A | 94.1 | 93.69 | 93.46 | 93.24 | 92.78 | 92.55 | 92.34 | 92.11 | 91.88 | 91.63 | 91.33 | 90.74 | 90.19 | 89.72 | 89.23 | 86.86 | 81.4 | 75.84
Rugeley 132kV | Burntwood 132 11 (GT1A) | Burntwood 132/11kVDUMMY | Primary | 11 | -1.9479 | 52.6802 | WPD Best View | Headroom (MW) | N/A | 94.1 | 93.71 | 93.52 | 93.33 | 92.92 | 92.71 | 92.51 | 92.31 | 92.1 | 91.89 | 91.67 | 91.45 | 91.22 | 90.98 | 90.74 | 89.59 | 87.25 | 83.27
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Consumer Transformation | Headroom (MW) | Thermal | 52.91 | 52.44 | 52.26 | 52.06 | 50.25 | 48.81 | 47.4 | 45.77 | 44.18 | 42.6 | 41.04 | 39.08 | 37.23 | 35.39 | 33.37 | 22.32 | 8.04 | -7.92
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Leading the Way | Headroom (MW) | Thermal | 52.91 | 52.37 | 52.17 | 51.97 | 49.77 | 48.27 | 46.81 | 45.45 | 44.21 | 43.09 | 41.9 | 40.25 | 38.43 | 36.52 | 34.46 | 22.36 | 6.41 | -12.84
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | Steady Progression | Headroom (MW) | N/A | 52.91 | 52.57 | 52.49 | 52.42 | 52.15 | 52.02 | 51.87 | 51.72 | 51.56 | 51.39 | 51.12 | 50.78 | 50.3 | 49.86 | 49.36 | 48.86 | 46.45 | 42.81
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | System Transformation | Headroom (MW) | N/A | 52.91 | 52.51 | 52.39 | 52.28 | 51.78 | 51.44 | 50.7 | 49.72 | 48.7 | 47.7 | 46.7 | 45.48 | 44.46 | 43.6 | 42.54 | 39.01 | 31.59 | 23.86
Rugeley 132kV | Cannock 132 11 (GT1A) | Cannock 132/11kV | Primary | 11 | -2.0186 | 52.6826 | WPD Best View | Headroom (MW) | Thermal | 52.91 | 52.37 | 52.17 | 51.97 | 49.77 | 48.28 | 46.82 | 45.46 | 44.23 | 43.11 | 41.93 | 40.29 | 38.48 | 36.58 | 34.52 | 22.42 | 6.47 | -12.78
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Consumer Transformation | Headroom (MW) | Thermal | 42.92 | 42.44 | 42.07 | 41.81 | 40.67 | 39.8 | 38.94 | 37.05 | 34.95 | 32.72 | 29.86 | 26.71 | 23.41 | 20.38 | 16.73 | 6.18 | -7.73 | -23.63
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Leading the Way | Headroom (MW) | Thermal | 42.92 | 42.4 | 42.04 | 41.81 | 40.56 | 39.71 | 38.81 | 37.96 | 37.17 | 36.42 | 35.63 | 34.83 | 32.2 | 29.62 | 28.35 | 14.65 | -1.95 | -15.22
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | Steady Progression | Headroom (MW) | N/A | 42.92 | 42.64 | 42.55 | 42.62 | 42.55 | 42.44 | 42.32 | 41.92 | 41.52 | 40.97 | 40.35 | 39.64 | 38.1 | 36.59 | 34.63 | 32.57 | 31.72 | 27.13
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | System Transformation | Headroom (MW) | Thermal | 42.92 | 42.56 | 42.36 | 42.31 | 41.89 | 41.53 | 41.15 | 39.79 | 38.08 | 36.19 | 33.67 | 30.88 | 27.98 | 25.47 | 22.43 | 18.68 | 9.48 | -0.9
Rugeley 132kV | Lichfield 132 11 (GT1A) | Lichfield 132/11kVDUMMY | Primary | 11 | -1.8174 | 52.6982 | WPD Best View | Headroom (MW) | N/A | 42.92 | 42.64 | 42.54 | 42.6 | 42.52 | 42.4 | 42.27 | 41.75 | 41.19 | 40.46 | 39.62 | 38.66 | 36.91 | 35.28 | 33.19 | 30.88 | 29.61 | 24.46
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Consumer Transformation | Headroom (MW) | Thermal | 25.52 | 25.12 | 24.87 | 24.54 | 23.7 | 22.81 | 21.95 | 20.33 | 18.5 | 16.53 | 14.14 | 11.53 | 8.81 | 6.3 | 3.23 | -6.31 | -17.4 | -30.28
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Leading the Way | Headroom (MW) | Thermal | 25.52 | 25.09 | 24.82 | 24.48 | 23.5 | 22.52 | 21.57 | 20.64 | 19.78 | 18.95 | 18.09 | 17.25 | 15 | 12.66 | 10.22 | -0.15 | -13.15 | -23.88
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | Steady Progression | Headroom (MW) | N/A | 25.52 | 25.27 | 25.2 | 25.11 | 25 | 24.84 | 24.68 | 24.32 | 23.97 | 23.56 | 23.05 | 22.46 | 21.24 | 20.02 | 18.45 | 16.5 | 13.84 | 10.46
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | System Transformation | Headroom (MW) | Thermal | 25.52 | 25.2 | 25.05 | 24.88 | 24.52 | 24.21 | 23.87 | 22.6 | 20.99 | 19.43 | 17.4 | 15.14 | 12.82 | 10.77 | 8.31 | 3.62 | -3.93 | -12.64
Rugeley 132kV | Rugeley Town 132 11 (GT1) | RUGELEY TOWN 132 11kV S STN | Primary | 11 | -1.935 | 52.7543 | WPD Best View | Headroom (MW) | Thermal | 25.52 | 25.15 | 24.96 | 24.73 | 24.06 | 23.45 | 22.86 | 21.8 | 20.67 | 19.43 | 17.93 | 16.31 | 14.29 | 12.37 | 9.99 | 3.77 | -4.03 | -13.77
Bustleholm 132kV | Bentley 132 11 (GT1A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Consumer Transformation | Headroom (MW) | N/A | 53.36 | 52.95 | 52.74 | 52.52 | 51.91 | 51.67 | 51.5 | 51.36 | 51.23 | 51.04 | 50.83 | 50.61 | 50.39 | 49.92 | 49.39 | 44.96 | 39.1 | 32.42
Bustleholm 132kV | Bentley 132 11 (GT1A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Leading the Way | Headroom (MW) | N/A | 53.36 | 52.89 | 52.68 | 52.44 | 51.56 | 51.28 | 51.11 | 51 | 50.87 | 50.66 | 50.39 | 50.11 | 49.83 | 49.35 | 48.67 | 43.92 | 37.52 | 29.03
Bustleholm 132kV | Bentley 132 11 (GT1A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | Steady Progression | Headroom (MW) | N/A | 53.36 | 53.02 | 52.86 | 52.69 | 52.41 | 52.25 | 52.12 | 52.03 | 51.93 | 51.82 | 51.7 | 51.57 | 51.45 | 51.33 | 51.21 | 50.61 | 49.78 | 48.81
Bustleholm 132kV | Bentley 132 11 (GT1A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | System Transformation | Headroom (MW) | N/A | 53.36 | 52.98 | 52.8 | 52.62 | 52.19 | 52 | 51.88 | 51.79 | 51.71 | 51.58 | 51.43 | 51.29 | 51.14 | 51 | 50.85 | 50.05 | 48.66 | 45.6
Bustleholm 132kV | Bentley 132 11 (GT1A) | Bentley 132/11kVDUMMY | Primary | 11 | -2.0181 | 52.5804 | WPD Best View | Headroom (MW) | N/A | 53.36 | 53.02 | 52.86 | 52.69 | 52.41 | 52.24 | 52.12 | 52.02 | 51.93 | 51.82 | 51.69 | 51.57 | 51.45 | 51.33 | 51.2 | 50.6 | 49.76 | 48.79
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Consumer Transformation | Headroom (MW) | N/A | 45.5 | 45.15 | 44.99 | 44.81 | 44.19 | 43.54 | 42.89 | 42.12 | 41.43 | 40.88 | 40.33 | 39.82 | 39.39 | 38.95 | 38.91 | 34.79 | 29.6 | 23.17
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Leading the Way | Headroom (MW) | N/A | 45.5 | 45.09 | 44.92 | 44.73 | 43.81 | 43.14 | 42.43 | 41.85 | 41.23 | 40.76 | 40.24 | 39.78 | 39.3 | 38.77 | 38.64 | 35.43 | 25.15 | 17.15
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | Steady Progression | Headroom (MW) | N/A | 38.9452 | 38.9346 | 38.9214 | 38.9091 | 38.8972 | 38.8624 | 38.8214 | 38.5205 | 38.2276 | 37.9446 | 37.6821 | 37.4582 | 37.3205 | 37.2056 | 37.1205 | 36.9235 | 36.6964 | 36.3855
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | System Transformation | Headroom (MW) | N/A | 45.5 | 45.18 | 45.04 | 44.9 | 44.48 | 44.36 | 44.2 | 43.74 | 43.25 | 42.95 | 42.63 | 42.37 | 42.19 | 42.04 | 42.05 | 42.39 | 37.24 | 34.25
Willenhall 132kV | Willenhall 132 11 (GT1) | Willenhall 132/25/11kVDUMMY | Primary | 11 | -2.0598 | 52.5768 | WPD Best View | Headroom (MW) | N/A | 45.5 | 45.19 | 45.05 | 44.9 | 44.5 | 44.3 | 43.96 | 43.39 | 42.88 | 42.47 | 42.08 | 41.73 | 41.47 | 41.21 | 41.38 | 39.47 | 36.69 | 32.55
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Consumer Transformation | Headroom (MW) | N/A | 45.96 | 40.98 | 40.84 | 40.7 | 40.16 | 39.97 | 39.67 | 39.15 | 38.69 | 38.21 | 37.76 | 37.33 | 36.91 | 36.48 | 36.06 | 32.88 | 30.31 | 26.9
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Leading the Way | Headroom (MW) | N/A | 45.96 | 40.93 | 40.79 | 40.65 | 39.85 | 39.63 | 39.3 | 38.8 | 38.33 | 37.82 | 37.36 | 36.92 | 36.49 | 36.05 | 35.57 | 32.89 | 34.3 | 22.87
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | Steady Progression | Headroom (MW) | N/A | 29.5842 | 23.9735 | 23.9498 | 23.9286 | 23.9131 | 23.89 | 23.8272 | 23.7369 | 23.6603 | 23.5828 | 23.5081 | 23.4452 | 23.4041 | 23.3649 | 23.3316 | 23.1872 | 23.0459 | 22.9198
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | System Transformation | Headroom (MW) | N/A | 42.2757 | 34.2477 | 34.1846 | 34.1201 | 34.0258 | 33.9252 | 33.7887 | 33.617 | 33.4996 | 33.3692 | 33.2264 | 33.0921 | 32.9693 | 32.8448 | 32.7322 | 32.1847 | 38.6891 | 30.4913
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132/33/11kV DUMMY | Primary | 11 | -2.1136 | 52.5814 | WPD Best View | Headroom (MW) | N/A | 43.9732 | 35.693 | 35.5933 | 35.4811 | 35.2232 | 34.9797 | 34.7149 | 34.413 | 34.1695 | 33.907 | 33.6204 | 33.3477 | 33.0926 | 32.8352 | 32.5585 | 31.009 | 30.31 | 26.9
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Consumer Transformation | Headroom (MW) | Thermal | 88.17 | 83.65 | 84.18 | 84.09 | 83.33 | 82.52 | 81.55 | 79.03 | 76.29 | 73.46 | 70.09 | 66.35 | 62.44 | 58.62 | 54.25 | 37.11 | 21.37 | -2.32
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Leading the Way | Headroom (MW) | Thermal | 88.17 | 83.7 | 84.3 | 84.21 | 83.14 | 82.28 | 81.24 | 79.67 | 78.08 | 76.37 | 74.5 | 72.64 | 69.13 | 65.56 | 61.94 | 36.72 | 19.75 | -10.38
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | Steady Progression | Headroom (MW) | N/A | 88.17 | 83.69 | 84.24 | 84.28 | 84.21 | 84.26 | 84.14 | 83.88 | 83.56 | 83.15 | 82.73 | 82.36 | 81.73 | 80.7 | 78.98 | 76.34 | 71.79 | 70.67
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | System Transformation | Headroom (MW) | N/A | 88.17 | 83.74 | 84.33 | 84.34 | 84.09 | 84.12 | 83.99 | 83.3 | 81.91 | 79.89 | 77.33 | 74.53 | 71.64 | 68.99 | 65.94 | 58.79 | 56.14 | 30.57
Port Ham 132kV | Castle Meads 132 33 | Castle Meads 132 33 | Bulk Supply Point | 33 | -2.2572 | 51.868 | WPD Best View | Headroom (MW) | N/A | 88.17 | 83.69 | 84.24 | 84.28 | 84.21 | 84.26 | 84.14 | 83.88 | 83.56 | 83.15 | 82.73 | 82.36 | 81.73 | 80.7 | 78.98 | 76.34 | 71.79 | 70.67
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Consumer Transformation | Headroom (MW) | Thermal | 25.94 | 25.43 | 19.65 | 19.26 | 18.36 | 17.74 | 17.13 | 15.86 | 14.39 | 12.83 | 10.85 | 8.72 | 6.46 | 4.31 | 1.78 | -7.43 | -18.95 | -30.99
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Leading the Way | Headroom (MW) | Thermal | 25.94 | 25.4 | 19.6 | 19.18 | 18.11 | 17.44 | 16.8 | 16.04 | 15.22 | 14.39 | 13.4 | 12.4 | 10.37 | 8.33 | 6.12 | -3.48 | -14.7 | -29.03
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | Steady Progression | Headroom (MW) | N/A | 25.94 | 25.58 | 25.42 | 25.26 | 25.02 | 24.82 | 24.61 | 24.35 | 24.1 | 23.81 | 23.42 | 22.99 | 22.12 | 21.31 | 20.25 | 18.95 | 16.78 | 14.32
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | System Transformation | Headroom (MW) | Thermal | 25.94 | 25.5 | 25.29 | 24.7 | 24.23 | 23.89 | 23.52 | 22.76 | 21.86 | 20.87 | 19.5 | 17.9 | 16.13 | 14.54 | 12.65 | 8.69 | 2.57 | -6.7
Port Ham 132kV | Cheltenham 132 66 | Cheltenham 132 66 | Bulk Supply Point | 66 | -2.1206 | 51.9096 | WPD Best View | Headroom (MW) | N/A | 25.94 | 25.58 | 25.42 | 25.26 | 25.02 | 24.82 | 24.61 | 24.35 | 24.1 | 23.81 | 23.42 | 22.99 | 22.12 | 21.31 | 20.25 | 18.95 | 16.78 | 14.32
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Consumer Transformation | Headroom (MW) | Thermal | 57.4 | 56.59 | 56 | 55.36 | 53.54 | 51.69 | 49.72 | 47.11 | 44.53 | 41.99 | 39.25 | 36.51 | 33.67 | 30.85 | 27.55 | 12.53 | -5.43 | -25.32
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Leading the Way | Headroom (MW) | Thermal | 57.4 | 56.51 | 55.9 | 55.22 | 53.13 | 51.11 | 48.97 | 46.78 | 44.79 | 42.7 | 40.56 | 38.51 | 35.63 | 32.73 | 29.65 | 13.53 | -6.88 | -29.05
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | Steady Progression | Headroom (MW) | N/A | 57.4 | 56.84 | 56.6 | 56.38 | 55.96 | 55.61 | 55.24 | 54.77 | 54.29 | 53.66 | 53.06 | 52.49 | 51.6 | 50.76 | 49.87 | 48.19 | 45.34 | 41.33
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | System Transformation | Headroom (MW) | N/A | 57.4 | 56.72 | 56.37 | 55.93 | 55.02 | 54.45 | 53.81 | 52.2 | 50.13 | 48.62 | 46.81 | 45.02 | 43.3 | 41.75 | 39.9 | 34.88 | 24.7 | 13.81
Port Ham 132kV | Hereford (Walham) 132 66 | Hereford (Walham) 132 66 | Bulk Supply Point | 66 | -2.62 | 52.0548 | WPD Best View | Headroom (MW) | Thermal | 57.4 | 56.59 | 56 | 55.36 | 53.54 | 51.69 | 49.72 | 47.11 | 44.53 | 41.99 | 39.25 | 36.51 | 33.67 | 30.85 | 27.55 | 12.53 | -5.43 | -25.32
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Consumer Transformation | Headroom (MW) | Thermal | 11.18 | 10.83 | 10.2 | 9.73 | 8.5 | 7.5 | 6.54 | 5.46 | 4.39 | 3.36 | 2.24 | 1 | -0.28 | -1.54 | -2.94 | -10.14 | -19.32 | -29.66
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Leading the Way | Headroom (MW) | Thermal | 11.18 | 10.78 | 10.14 | 9.64 | 8.21 | 7.15 | 6.13 | 5.2 | 4.35 | 3.55 | 2.63 | 1.73 | 0.46 | -0.85 | -2.25 | -10.17 | -20.5 | -32.7
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | Steady Progression | Headroom (MW) | N/A | 11.18 | 11.01 | 10.91 | 10.81 | 10.64 | 10.49 | 10.33 | 10.13 | 9.92 | 9.7 | 9.46 | 9.24 | 8.89 | 8.57 | 8.21 | 7.62 | 6.1 | 4.05
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | System Transformation | Headroom (MW) | Thermal | 11.18 | 10.93 | 10.72 | 10.22 | 9.69 | 9.28 | 8.82 | 8.15 | 7.41 | 6.75 | 5.99 | 5.24 | 4.52 | 3.9 | 3.1 | 0.71 | -4.04 | -9.16
Penn 132kV | Hinksford 132 33 | Hinksford 132 33 | Bulk Supply Point | 33 | -2.1938 | 52.506 | WPD Best View | Headroom (MW) | Thermal | 11.18 | 10.82 | 10.19 | 9.72 | 8.44 | 7.42 | 6.44 | 5.52 | 4.66 | 3.87 | 3.06 | 2.23 | 1.04 | -0.17 | -1.43 | -8.74 | -18.37 | -28.49
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Consumer Transformation | Headroom (MW) | Thermal | 17.41 | 17.22 | 17.09 | 16.93 | 16.58 | 16.19 | 15.74 | 14.82 | 13.82 | 12.71 | 11.34 | 9.79 | 8.16 | 6.62 | 4.78 | -0.68 | -7.06 | -14.52
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Leading the Way | Headroom (MW) | Thermal | 17.41 | 17.21 | 17.06 | 16.89 | 16.46 | 16.07 | 15.59 | 15.16 | 14.75 | 14.38 | 14 | 13.64 | 12.26 | 10.92 | 9.5 | 3.42 | -4.2 | -10.42
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | Steady Progression | Headroom (MW) | N/A | 17.41 | 17.28 | 17.23 | 17.17 | 17.1 | 17.05 | 16.99 | 16.85 | 16.71 | 16.54 | 16.32 | 16.05 | 15.29 | 14.57 | 13.63 | 12.47 | 10.82 | 8.73
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | System Transformation | Headroom (MW) | Thermal | 17.41 | 17.25 | 17.16 | 17.07 | 16.9 | 16.79 | 16.65 | 16.06 | 15.21 | 14.29 | 13.09 | 11.74 | 10.33 | 9.11 | 7.59 | 4.72 | 0.46 | -4.45
Cellarhead 132kV | Newcastle 132 33 | Newcastle 132 33 | Bulk Supply Point | 33 | -2.2423 | 53.029 | WPD Best View | Headroom (MW) | N/A | 17.41 | 17.28 | 17.23 | 17.17 | 17.1 | 17.05 | 16.99 | 16.85 | 16.71 | 16.54 | 16.32 | 16.05 | 15.29 | 14.57 | 13.63 | 12.47 | 10.82 | 8.73
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Consumer Transformation | Headroom (MW) | Thermal | -6.44 | -7.18 | -7.87 | -8.4 | -9.59 | -10.75 | -12.47 | -15.47 | -18.54 | -21.83 | -25.74 | -30.05 | -34.59 | -38.85 | -43.85 | -58.87 | -45.41 | -68.43
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Leading the Way | Headroom (MW) | Thermal | -6.44 | -7.26 | -7.97 | -8.53 | -10.01 | -11.26 | -12.98 | -14.66 | -16.15 | -17.65 | -19.26 | -20.81 | -24.58 | -28.37 | -31.38 | -15.7 | -35.53 | -54.79
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | Steady Progression | Headroom (MW) | Thermal | -6.44 | -7.01 | -7.28 | -13.17 | -13.54 | -13.79 | -14.15 | -14.9 | -15.86 | -16.6 | -17.46 | -18.59 | -20.33 | -21.93 | -24.2 | -27.1 | -29.2 | -2.32
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | System Transformation | Headroom (MW) | Thermal | -6.44 | -7.1 | -7.45 | -8.03 | -8.67 | -9.11 | -9.62 | -11.02 | -13.43 | -16 | -19.15 | -22.57 | -26.1 | -29.2 | -33.02 | -39.16 | -16.93 | -30.49
Bishops Wood 132kV | Stourport 132 33 | Stourport 132 33 | Bulk Supply Point | 33 | -2.2691 | 52.3381 | WPD Best View | Headroom (MW) | Thermal | -6.44 | -7.03 | -7.33 | -13.28 | -13.78 | -14.22 | -14.89 | -16.04 | -17.26 | -18.11 | -19.25 | -20.57 | -22.86 | -25.03 | -27.69 | -33.79 | -8.52 | -16.95
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Consumer Transformation | Headroom (MW) | Thermal | 47.87 | 46.76 | 46.03 | 40.27 | 37.54 | 35.28 | 32.71 | 28.13 | 23.5 | 18.9 | 13.46 | 7.74 | 1.88 | -3.55 | -9.26 | -31.22 | -57.82 | -90.01
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Leading the Way | Headroom (MW) | Thermal | 47.87 | 46.63 | 45.88 | 40.05 | 36.8 | 34.4 | 31.63 | 29.16 | 26.7 | 24.42 | 22.05 | 18.33 | 13.4 | 8.51 | 4.63 | -18.67 | -50.04 | -78.95
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | Steady Progression | Headroom (MW) | N/A | 47.87 | 47.09 | 46.73 | 41.5 | 40.94 | 40.5 | 40.03 | 38.86 | 37.64 | 36.06 | 34.59 | 33.05 | 30.41 | 27.94 | 24.91 | 21.1 | 15.4 | 7.57
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | System Transformation | Headroom (MW) | Thermal | 47.87 | 46.93 | 46.41 | 41 | 39.79 | 38.92 | 37.93 | 35.07 | 31.23 | 27.89 | 23.61 | 19.07 | 14.55 | 10.6 | 6.37 | -2.61 | -18.48 | -37.91
Bishops Wood 132kV | Stourport 132 66 & Upton Warren 132 66 | Stourport 132 66 & Upton Warren 132 66 | Bulk Supply Point | 66 | -2.2691 | 52.3381 | WPD Best View | Headroom (MW) | Thermal | 47.87 | 47.02 | 46.59 | 41.26 | 40.41 | 39.78 | 39.11 | 37.46 | 35.59 | 33.41 | 31.1 | 28.68 | 25.45 | 22.54 | 19.05 | 13.12 | 4.4 | -6.27
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Consumer Transformation | Headroom (MW) | Thermal | 18.46 | 13.48 | 13.34 | 13.2 | 12.66 | 12.47 | 12.17 | 11.65 | 11.19 | 10.71 | 10.26 | 9.83 | 9.41 | 8.98 | 8.56 | 5.38 | 2.81 | -0.6
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Leading the Way | Headroom (MW) | Thermal | 18.46 | 13.43 | 13.29 | 13.15 | 12.35 | 12.13 | 11.8 | 11.3 | 10.83 | 10.32 | 9.86 | 9.42 | 8.99 | 8.55 | 8.07 | 5.39 | 6.8 | -4.63
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | Steady Progression | Headroom (MW) | N/A | 18.46 | 13.53 | 13.41 | 13.29 | 13.03 | 12.88 | 12.7 | 12.51 | 12.32 | 12.15 | 11.98 | 11.83 | 11.69 | 11.55 | 11.41 | 10.72 | 10.01 | 9.29
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | System Transformation | Headroom (MW) | N/A | 18.46 | 13.5 | 13.38 | 13.25 | 12.86 | 12.7 | 12.51 | 12.31 | 12.15 | 11.99 | 11.84 | 11.58 | 11.34 | 11.11 | 10.9 | 9.77 | 12.29 | 5.83
Willenhall 132kV | Wolverhampton 132 33 | Wolverhampton 132 33 | Bulk Supply Point | 33 | -2.1136 | 52.5814 | WPD Best View | Headroom (MW) | Thermal | 18.46 | 13.48 | 13.34 | 13.2 | 12.66 | 12.47 | 12.17 | 11.65 | 11.19 | 10.71 | 10.26 | 9.83 | 9.41 | 8.98 | 8.56 | 5.38 | 2.81 | -0.6